## RoomData
Standard Components - Items in room
02.05.2025
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
1BR-BA | 1 Bed Room - Bariatric | 18 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room - Bariatric will accommodate one patient, typically weighing up to 250kg, for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door - the arrangement of the medical services panel reflects this assumption; bariatric sized equipment (bed, chair) and the movement of equipment around all sides of the bed; a ceiling mounted hoist that extends from the bed to the Ensuite. Natural light and outlook is essential and patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing is recommended. This room should be planned with direct access to an Ensuite - Bariatric. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-CCU | 1 Bed Room - CCU | 20 | 24 Hours | 1 patient; 1-2 visitors, 1-4 staff intermittently |  | Acoustic privacy is required | A 1 Bed Room - CCU will accommodate one patient and support the delivery of a range of clinical care, minor procedures and diagnostic tests, with clinical staff requiring access to both sides of the bed. Additional Considerations: The 1 Bed Room - CCU may vary in configuration to suit different Ensuite options including inboard, outboard and stacked (also known as 'back-to-back' or 'nested') configurations. In each configuration, sufficient clearance is required for equipment and staff to access both sides of the bed. Glazed doors and observation windows may be provided for visibility of high acuity patients and monitoring equipment. The provision of observation windows and the use of interstitial blinds or privacy curtains is to be supported by operational models for observation as well as support for patient privacy. The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring and diagnostic equipment. Natural light and outlook is essential and the patient will need to have an external outlook from either the chair or the bed, preferably both.
1BR-IC | 1 Bed Room - Intensive Care | 25 | 24 Hours | 1 patient, 1 visitor, up to 6-8 staff |  | Acoustic privacy is required | An acuity adaptable, enclosed bed room for a patient requiring intensive medical treatment, nursing care and monitoring for potentially life threatening conditions. Visual access to a main Staff Station or Sub Staff Station is required. Natural light is required to patient beds. Dialysis facilities may be required, assumed to be provided via mobile reverse osmosis water dialysis units. As mobile Imaging may be required, shielding requirements must be confirmed with Radiation Consultant.
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | 15 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room - Isolation (Negative Pressure) will accommodate one patient requiring respiratory isolation to prevent the transmittion of infection. The room will be capable of delivering a range of clinical care and treatment. The room will have an attached Anteroom which will be used by staff and visitors so they can don PPE. The patients will be transferred in and out of the room via the patient doors, rather than the Anteroom. This arrangement also makes the room easier to use when not needed for negative pressure isolation. The spatial allowance will accommodate: staff working at either side of the bed however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption - the movement of equipment around all sides of the bed (e.g. a mobile hoist) and a ceiling mounted hoist. While the ceiling mounted hoist is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will requirement outlook from either the bed or chair, preferably both. Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | 16.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room - Isolation (Negative Pressure) will accommodate one patient requiring respiratory isolation to prevent the transmittion of infection. The room will be capable of delivering a range of clinical care and treatment. The room will have an attached Anteroom which will be used by staff and visitors so they can don PPE. The patients will be transferred in and out of the room via the patient doors, rather than the Anteroom. This arrangement also makes the room easier to use when not needed for negative pressure isolation. The spatial allowance will accommodate: staff working at either side of the bed however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption the movement of equipment around all sides of the bed (e.g. a mobile hoist) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will requirement outlook from either the bed or chair, preferably both. Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | 15 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | Single bed room for general mental health patients. Natural light and outlook is essential. The room is to be internally lockable with a master keyed lock from the outside. All fittings and fixtures used in consumer areas of the building must be of a type manufactured and marketed as anti-ligature; and installed in accordance with the manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. Selected fixtures are to have a breaking strain of not more than 15kg (e.g. clothes hooks). All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a minimum thickness of 14.28mm, or equivalent approved. The 1 Bed Room - Mental Health may vary in configuration to suit different Ensuite options, including inboard and back to back. Staff to staff nurse call has not been provided on the assumption that a portable call and duress device is provided to staff. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | 15 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | Single bed room for general mental health patients. Natural light and outlook is essential. The room is to be internally lockable with a master keyed lock from the outside. All fittings and fixtures used in consumer areas of the building must be of a type manufactured and marketed as anti-ligature; and installed in accordance with the manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. Selected fixtures are to have a breaking strain of not more than 15kg (e.g. clothes hooks). All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a minimum thickness of 14.28mm, or equivalent approved. The 1 Bed Room - Mental Health may vary in configuration to suit different Ensuite options, including inboard and back to back. Staff to staff nurse call has not been provided on the assumption that a portable call and duress device is provided to staff. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | 18 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room - Special will accommodate one patient for the delivery of a range of clinical care and treatment. It will typically be provided in maternity, paediatric and palliative care inpatient units.The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While the ceiling hoist is shown, inclusion will be dependent on jurisdictional policies; (d) room for a carer to stay overnight to support models such as 'care by parent'. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both.The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing is recommended. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | 18 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room - Special will accommodate one patient for the delivery of a range of clinical care and treatment. It will typically be provided in maternity, paediatric and palliative care inpatient units.The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While the ceiling hoist is shown, inclusion will be dependent on jurisdictional policies; (d) room for a carer to stay overnight to support models such as 'care by parent'. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both.The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing is recommended. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | 16 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | 16.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | 16.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | 16.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | 17.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | 17.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | 17.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | 27 | 24 Hours | 2 patient; 2-3 staff; 2-4 visitors |  | Acoustic privacy is required | A 2 Bed Room will accommodate two patients for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur in the space in between the beds. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist). Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed. Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite. The 2 Bed Room may vary in configuration to suit different Ensuite options including: inboard and outboard. Each 2 Bed Room will need direct access to the Ensuite. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | 29 | 24 Hours | 2 patient; 2-3 staff; 2-4 visitors |  | Acoustic privacy is required | A 2 Bed Room will accommodate two patients for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur in the space in between the beds. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist). Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed. Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite. The 2 Bed Room may vary in configuration to suit different Ensuite options including: inboard and outboard. Each 2 Bed Room will need direct access to the Ensuite. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
2BR-ST-B | 2 Bed Room - Outboard Ensuite | 28 | 24 Hours | 2 patient; 2-3 staff; 2-4 visitors |  | Acoustic privacy is required | A 2 Bed Room will accommodate two patients for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur in the space in between the beds. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist). Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed. Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite. The 2 Bed Room may vary in configuration to suit different Ensuite options including: inboard and outboard. Each 2 Bed Room will need direct access to the Ensuite. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
4BR-ST | 4 Bed Room - Inboard Ensuite | 58 | 24 Hours | 4 patient; 2-4 staff; 4-6 visitors |  | Acoustic privacy is required | A 4 Bed Room will accommodate four patients for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur in the space in between the beds. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist). Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed. An inboard Ensuite is shown and each 4 Bed Room will need direct access to an Ensuite. Ideally, each 4 Bed Room will have direct access to an additional patient toilet or Ensuite. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.
ADLB | ADL Bathroom | 12 | up to 24 hours | 1 patient, 1 - 2 staff |  | Sound attenuation level medium, Acoustic privacy is required. | The ADL Bathroom provides a toilet, basin with vanity, shower and bath for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The room is to provide domestic facilities with grab rails and other assistive devices to be included to reflect reasonable home modifications and equipment utilised by patients. The entrance of the room is to be flush with the adjoining corridor. The door is to be fitted with escape hardware for the door to open outwards if required. Additional Considerations: An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. The shower area may include a fixed raised hob to simulate a domestic scenario depending on service requirements.
ADLD | ADL Dining | 12 | up to 24 hours | up to 4 patients, 1-2 staff |  | sound attenuation level-high; acoustic privacy is required. | The ADL Dining provides a flexible space for the training and assessment of patients in Activities of Daily Living (ADL) tasks. Typically collocated with the ADL Kitchen, the Dining room supports small group discussions and demonstrations between both rooms and provides a space for debriefing after training and assessment of ADL tasks in the Kitchen. Additional Considerations: An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. External outlook and access to natural light is desirable.
ADLK | ADL Kitchen | 12 | up to 24 hours | up to 2 patients, 1-2 staff |  | Acoustics: sound attenuation level high. | The ADL Kitchen provides an accessible space for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The space is to be functional for a range of patients including wheelchair users. The kitchen can include a combination of fittings and appliances such as a sink, cooktop, oven/grill, microwave and refrigerator to support common ADL training and assessment tasks as per service requirements. Room exhaust to be provided to range hood over cooktop. Additional Considerations: An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. The room may be enclosed with a lockable door depending on security requirements. External outlook and access to natural light is desirable.
ADLL | ADL Laundry | 8 | up to 24 Hours | 1 patient, 1 staff |  |  | The ADL Laundry provides domestic facilities for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The room will include a domestic washing machine and dryer which, if front loading models are selected, may be placed on plinths to raise machines to an accessible height to support common ADL training and assessment tasks as per service requirements. A laundry tub and storage for ironing equipment are also provided. Additional Considerations: An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. The space may be provided as an open bay that is collocated with other ADL rooms. If open, the impact of noise on adjacent areas must be considered.
AHBF | After Hours Blood Fridge | 8 | Available 24 Hours | 1-2 staff, intermittently |  |  | The After Hours Blood Fridge is a discreet area for refrigerated storage of blood and blood products for access by authorised personnel after hours where a 24 hour pathology service is not available. This room is typically located on the periphery of a Pathology unit and may have direct, secure access to the Pathology laboratory with ready access to the transfusion service area. Additional Considerations: Refrigerator temperature monitoring is required and is to be connected to the building management system (BMS). The alarm is to provide alerts where 24-hour monitoring is undertaken, within the unit and/or remotely. Temperature monitoring is to meet ANZSBT guidelines. Additional fridges/freezers or lockable sections within the after hours fridge may be provided to support Pathology laboratory workflows. Provision of smart fridges for blood product tracking and other ICT requirements will be based on local policies and service requirements. Door width to allow for installation of fridge, including considerations for future proofing as equipment is replaced.
AHDR | After Hours Drug Store | 5 | 24 Hours | 1 - 2 staff intermittently |  |  | The After Hours Drug Store is a secure room for the storage of medications that may be required after hours. Stock is replenished by pharmacy personnel and, depending on the location of the room, there may be direct access from within the pharmacy. Secure access to the room for authorised personnel is required. A duress alarm may be required if room accessed from a public or patient care area. Refrigerated storage will be required for some medications. Refer to project specific requirements for automated medication management systems.
AIRLE-12 | Airlock - Entry, 12m2 | 12 | Up to 24 Hours |  |  |  | The Airlock is a transitional space associated with an entry area to provide wind/weather protection and to support efficient temperature regulation. Flooring in the Airlock typically supports the capture of dirt and moisture at the building entry to reduce cleaning requirements. Configuration will be dependent on site, internal layout and access requirements. The Airlock may be used by a wide range of people including fully ambulant people, persons using a wide range of walking aids and persons in wheelchairs. The Airlock may need to support the movement of beds/trolleys (e.g. at an ambulance or transit lounge entry) requiring a configuration that provides a relatively straight path of travel. Additional area to accommodate door movement and circulation will be required if entry from multiple directions provided. Additional Considerations: Entry doors may be glazed and automatic depending on access requirements. Access control may require the provision of swipe card readers, keypads, intercoms, push to open buttons (e.g. to exit after hours), door release buttons from nearby security or reception, etc. Provision of these items will depend on security requirements and operational policies (e.g. for after hours access). Lockdown and emergency egress requirements must also be considered. A hold open function to the internal door will typically be required for cleaning. Depending on layout and alignment of openings when the doors are open, an air curtain may be required to prevent the entry of draughts, insects, odours, etc. Wall materials shown are indicative and will be dependent on facade design and internal layout. Floor finishes are to be specified/detailed to reduce the risk of trips, slips and falls, (e.g. minimise changes in finished height at transitions). Drainage requirements to floor matting must be considered. Where allocated to an Ambulance entry floor finish is to provide a flat smooth surface suitable for transporting spinal and other patients. At public/patient entries, the provision of culturally appropriate artwork (e.g. with film on glazing) may be considered to create a welcoming atmosphere. Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby upon entry in line with local infection control policies. A small amount of concise signage may be required within the airlock however it is recommended that extensive wayfinding information is made readily accessible upon entry to keep airlock clear.
AIRLE-6 | Airlock - Entry, 6m2 | 6 | Up to 24 Hours |  |  |  | The Airlock is a transitional space associated with an entry area to provide wind/weather protection and to support efficient temperature regulation. Flooring in the Airlock typically supports the capture of dirt and moisture at the building entry to reduce cleaning requirements. Configuration will be dependent on site, internal layout and access requirements. The Airlock may be used by a wide range of people including fully ambulant people, persons using a wide range of walking aids and persons in wheelchairs. Additional area and a layout with a relatively straight path of travel is required if the movement of beds/trolleys is to be supported. Additional Considerations: Entry doors may be glazed and automatic depending on access requirements. Access control may require the provision of swipe card readers, keypads, intercoms, push to open buttons (e.g. to exit after hours), door release buttons from nearby security or reception, etc. Provision of these items will depend on security requirements and operational policies (e.g. for after hours access). Lockdown and emergency egress requirements must also be considered. A hold open function to the internal door will typically be required for cleaning. Depending on layout and alignment of openings when the doors are open, an air curtain may be required to prevent the entry of draughts, insects, odours, etc. Wall materials shown are indicative and will be dependent on facade design and internal layout. Floor finishes are to be specified/detailed to reduce the risk of trips, slips and falls, (e.g. minimise changes in finished height at transitions). Drainage requirements to floor matting must be considered. At public/patient entries, the provision of culturally appropriate artwork (e.g. with film on glazing) may be considered to create a welcoming atmosphere. Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby upon entry in line with local infection control policies. A small amount of concise signage may be required within the airlock however it is recommended that extensive wayfinding information is made readily accessible upon entry to keep airlock clear.
ANRM | Anteroom | 6 | 24 Hours | 1 - 2 |  |  | Anteroom associated with an Isolation room for maintenance of air pressurisation and for staff and visitors to change and dispose of protective gear used on entering or exit; a staff handwashing basin will be located within the room; glazing is recommended for patient and staff visibility. Pressurisation - negative or positive depending on type of Isolation room Body Protected electrical area
AUD-CR | Audiology Control Room | 9 | 8am to 6pm, daily | 1 staff |  | Acoustic privacy is required | The Audiology Control Room may be provided adjacent to the Audiology Testing Room to support the administering of tests that require discrete observation, result verification by a second clinician and/or remote control of equipment. The room will require a workspace and visibility of the Testing Room via an observation window. Additional Consideration: The floor of the Control Room should be flush with the floor of the Treatment Room and the adjacent corridor for access by patients in wheelchairs. Portable equipment may be shared between the Control Room and the Treatment Room.
AUD-TR | Audiology Testing Room | 14 | 8am to 6pm, daily | 1 patient, 1 visitor/carer, 1-2 staff |  | Acoustic isolation is required | The Audiology Testing Room provides an acoustically treated, soundproof space for clinical assessments to be carried out under controlled conditions. Testing Rooms may be modular proprietary items or constructed in situ and are generally designed as rooms within rooms in order to isolate the Testing Room from the rest of the building as much as possible. All designs should be reviewed and confirmed by an acoustic design expert. Additional Consideration: The Audiology Testing Room currently indicates a layout (with an adjacent control room) that is suitable for paediatric testing. Layouts will vary to suit service requirements and the provided layout will need to be altered to suit services for older children and adults. The audiometric booth is to be ventilated and connected to air-conditioning, power and data. Noise from mechanical services is to be minimised with air-conditioning to be designed for low noise operation to meet ambient noise requirements for testing. The floor of the Treatment Room should be flush with the floor of the Control Room, or the adjacent corridor where a Control Room is not provided, for access by patients in wheelchairs.
BATH | Bathroom | 15 | 24 Hours | 1 patient; 1-2 staff assisting |  | Sound attenuation level medium, Acoustic privacy is required. | The Bathroom provides facilities for assisted bathing, dressing and grooming of patients. The layout should allow for maneuvering of a patient on a lifting device, commode chair, wheelchair or shower trolley. Placement of the toilet should allow assistance from both sides. A height adjustable bath may be provided instead of a shower trolley depending on service requirements. Bariatric capability may be considered; refer to project specific requirements. Signage with braille tactiles to nominate 'Bathroom' to be provided.
BBEV | Bay - Beverage | 4 | Up to 24 Hours | 1-2 intermittently |  |  | The Beverage Bay is an area for preparation (including heating as required) of refreshments, snacks and small meals, washing some utensils, storing small mounts of food and drink and disposing of food waste (in accordance with food hygiene requirements). Beverage bays may allocated to patient care areas, staff areas and meeting/education facilities. Additional Considerations: Ready access to a handwashing basin is recommended. If an instantaneous boiling water tap/unit is provided, it should be hardwired and access restricted to the unit e.g. within cupboard. If system is located within a joinery unit, ensure appropriate ventilation is provided. A side approach to the sink for wheelchair access has been shown; front access may be required depending on local/jurisdictional policies and service requirements. The Beverage Bay should be adequately recessed to avoid encroachment into the corridor. If the space is to be enclosed and/or access is restricted, an increase in area is required. The door will require an observation panel. Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. Fridge dimensions will vary depending on selection and service requirements; clear area provided for the fridge is to allow for adequate ventilation and full opening of door Provision and type of ice machine will be dependent on service requirements and local infection prevention and control policies.
BBLD | Bay - Blood Fridge | 2 | Available 24 Hours | accessed by staff intermittently |  |  | The Bay - Blood Fridge is an area provided within a secure, staff only area for the storage of blood products. This bay is typically provided in critical care and operating theatre units where the pathology department is not located nearby. A pass-through layout may be developed depending on service requirements and location (e.g. in relation to limiting access to the clean area of operating theatres). Additional Considerations: Refrigerator temperature monitoring is required and is to be connected to the building management system (BMS). The alarm is to provide alerts where 24-hour monitoring is undertaken, within the unit and/or remotely. Temperature monitoring is to meet ANZSBT guidelines. Requirements for accurate record keeping are to be supported through operational policies and service workflows. Provision of smart fridges to support blood product tracking and other ICT requirements will be based on local policies and service requirements.
BBW | Bay - Blanket / Fluid Warmer | 1 | up to 24 Hours | accessed intermittently |  |  | The Bay - Blanket / Fluid Warmer provides clear area and services for a single warming cabinet. The warming cabinet may be for fluids only, blankets only or a combination of fluids and blankets. Additional Considerations: Collocation of blanket warming cabinets with linen bays is common and supports efficient workflows. Locating the bay with ready access to patient areas or operating/procedure areas is recommended. The capacity of warming cabinets varies and must be considered in relation to the area/number of patients to be served. The throughput of patients must also be considered as a higher turnover will require higher capacity/additional cabinets. Warming cabinet sizes vary and the clear area of the bay is to suit the dimensions of the equipment selected as well as ensuring adequate space for ventilation as per manufactures specifications. The bay should deep enough to ensure that the warming cabinet itself does not impede adjacent corridor circulation. Clearance to be provided in adjacent circulation space to allow for opening of the door for intermittent use and restocking. Where fluids are kept, processes for labelling fluids need to be accommodated without impeding circulation. Various cabinet configurations, including benchtop, under bench, freestanding, mobile and built-in cabinets may be selected. See manufacturer's specifications for installation requirements. Temperatures for fluids need to be monitored. A data outlet, or alternative connection to suit project/equipment requirements, may be required for connection the Building Management System (BMS) depending on provision of fluid warming.
BES | Bay - Emergency Shower | 1 | Available 24 Hours | 1 |  |  | An unobstructed and accessible area with an emergency shower and eye wash equipment for staff who have been contaminated with toxic and/or corrosive substances.
BHW | Bay - Height/ Weight | 2 | Available 24 hours | 1 patient and 1 staff, intermittently |  | Sound attenuation level medium, Acoustic privacy is required. | An open bay for measuring and recording the height and weight of patients. Standing scales and a stadiometer are typically provided. Chair scales may be used here or may be stored here to be used elsewhere in the department as required. The type of scales and provision for bariatric patients will be dependent on service requirements. Additional Design Considerations: The bay should deep enough to ensure that equipment does not impede adjacent corridor circulation. Design and location of bay should allow for intermittent use without significant disruption to circulation in adjacent corridor. Grab rails for patient stability may be provided and may be either integral to the scales or wall mounted.
BHWS-A | Bay - Handwashing, Type A | 1 | 24 Hours | 1 |  |  | The Bay - Handwashing, Type A provides handwashing facilities for staff use in areas requiring clinical handwashing prior to undertaking selected procedures and where handwashing up to the elbow may be necessary. The basin is to be a large, wall-mounted, 'scrub' type, with hands-free taps that may be wall-mounted elbow operated, foot/knee operated or operated with electronic sensor taps. Warm and cold water are to be delivered by a common spout.
BHWS-B | Bay - Handwashing, Type B | 1 | 24 Hours | 1 |  |  | The Bay - Handwashing, Type B provides handwashing facilities for staff use before and after every patient contact and visitor use as required. The basin is to be a medium, wall-mounted type, with hands-free taps that may be either wall-mounted or basin-mounted elbow operated taps. Warm and cold water are to be delivered by a common spout.
BIRM-A | Birthing Room, Without Pool | 34 | 24 Hours | 1 mother; 1-2 support persons; up to 4 staff |  | Sound attenuation level high, Acoustic privacy is required. | The Birthing Room - Without Pool provides area and amenities for the entire birthing process including mother's preparation, active birthing exercises, relaxation and analgesia during labour, birthing, infant resuscitation, postnatal recovery and observation. The room includes an active birthing/bed zone, an area to accommodate a support person, a staff observation and write up area, an infant resuscitation area, an equipment store, and a hand hygiene area with type A handwashing basin. Additional Considerations: The room will have direct access to an Ensuite - Birthing. Air should not be recirculated to other areas from the Birthing Room. Negative pressure air conditioning is required for clearance of anaesthetic gases. Clinical items such as medical gases and services as well as neonatal resuscitation equipment may be concealed to support the provision of a calm environment. Even while concealed, items are to be within easy reach of the active birthing zone. The availability of proprietary items for in-room infant resuscitation may change and this can inform the use of built in or mobile equipment. Overall dimensions and configuration of storage for the resuscitaire equipment are to be evaluated based on the selection of equipment and it is recommended that a test-fit is conducted, ensuring appropriate clearances are provided for emergency procedures to be undertaken, in order to confirm room layout requirements. Equipment storage to be configured to suit service requirements including models for sharing equipment between multiple rooms. Storage requirements within the room will vary between facilities depending on models of centralising or decanting and restocking consumables. Configuration and extent of storage to be determined based on service requirements. Various supportive fixtures for active birthing are to be considered, for example, a wall mounted ladder, bench or mantlepiece for support and leaning, or ceiling mounted hooks for supportive fabrics to be hung. Consider mounting heights and providing support for various postures at multiple heights. A mother's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. A fixed workstation for staff write-up and observation has been shown. Sufficient space for dual monitors may be provided as required to suit operational, EMR and ICT requirements. A workstation on wheels is also acceptable. An examination light is required for suturing and small procedures. It is preferred that the light be as unobtrusive as possible and be able to be pushed away so that it is not dominating the area. Lighting options to be provided, including dimmable room lighting, reading lights and night lights to provide flexible lighting across the space. Coloured lighting and calming light artworks may be considered by projects. Systems, including portable items, to facilitate the selection and control of music by the mother are to be considered. Acoustics treatment may be required to support this without disruption to adjacent rooms. Provision of a telephone for patient use will be dependent on the operational model for transferring calls. Natural light and outlook essential. Window sill to be low enough to see view while laying in bed. Treatment, to windows to allow blinds to be kept open as desired but privacy to be maintained, may need to be considered depending on overlook from nearby buildings.
BIRM-B | Birthing Room, With Pool | 40.5 | 24 Hours | 1 mother; 1-2 support persons; up to 4 staff |  | Sound attenuation level high, Acoustic privacy is required. | The Birthing Room - With Pool provides area and amenities for the entire birthing process including mother's preparation, active birthing exercises, water immersion during labour, relaxation and analgesia during labour, birthing, infant resuscitation, postnatal recovery and observation. The room includes an active birthing/bed zone, birthing pool an area to accommodate a support person, a staff observation and write up area, an infant resuscitation area, an equipment store, and a hand hygiene area with type A handwashing basin. Birthing Pool: The use of birthing pools should be based on local policies and protocols for water immersion during labour and birth. Birthing pools can vary significantly in shape and the pool shown on the RLS is indicative only. Final selection may have implications for required area and clearances. The birthing pool must be deep and wide enough for effective water immersion for pain relief during labour and birth. Ergonomic assessment of birthing pool options should be undertaken prior to selection, including the height of the pool for mothers getting into and out of the pool, as well as access for staff assisting the mother from the side of the pool. The location of grabrails and supports, including those integral with the bath design are to be considered to support transfers without impeding access to the mother by staff. Pools may be installed with steps built around them to provide easy access into the pool from a seated position. Provision of stairs is to be assessed to ensure they do not limit access with floatation transfer devices in the event of an emergency. Handrails to be provided to stairs to reduce risk of slips in wet area around the pool. A ceiling mounted hoist has not been included as there are better and more timely ways to remove a mother from the birthing pool should her condition deteriorate. Consideration for ready access to floatation devices for transfer from the pool is required. The tapware and drain for the birthing pool are to be carefully considered. Taps need to allow the bath to be filled rapidly. Water also needs to be able to be drained quickly, preferably without needing to reach into the bath after birthing. Additional Considerations: The room will have direct access to an Ensuite - Birthing. Air should not be recirculated to other areas from the Birthing Room. Negative pressure air conditioning is required for clearance of anaesthetic gases. Clinical items such as medical gases and services as well as neonatal resuscitation equipment may be concealed to support the provision of a calm environment. Even while concealed, items are to be within easy reach of the active birthing zone. The availability of proprietary items for in-room infant resuscitation may change and this can inform the use of built in or mobile equipment. Overall dimensions and configuration of storage for the resuscitaire equipment are to be evaluated based on the selection of equipment and it is recommended that a test-fit is conducted, ensuring appropriate clearances are provided for emergency procedures to be undertaken, in order to confirm room layout requirements. Equipment storage to be configured to suit service requirements including models for sharing equipment between multiple rooms. Storage requirements within the room will vary between facilities depending on models of centralising or decanting and restocking consumables. Configuration and extent of storage to be determined based on service requirements. Various supportive fixtures for active birthing are to be considered, for example, a wall mounted ladder, bench or mantlepiece for support and leaning, or ceiling mounted hooks for supportive fabrics to be hung. Consider mounting heights and providing support for various postures at multiple heights. A mother's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. A fixed workstation for staff write-up and observation has been shown. Sufficient space for dual monitors may be provided as required to suit operational, EMR and ICT requirements. A workstation on wheels is also acceptable. An examination light is required for suturing and small procedures. It is preferred that the light be as unobtrusive as possible and be able to be pushed away so that it is not dominating the area. Lighting options to be provided, including dimmable room lighting, reading lights and night lights to provide flexible lighting across the space. Coloured lighting and calming light artworks may be considered by projects. Systems, including portable items, to facilitate the selection and control of music by the mother are to be considered. Acoustics treatment may be required to support this without disruption to adjacent rooms. Provision of a telephone for patient use will be dependent on the operational model for transferring calls. Natural light and outlook essential. Window sill to be low enough to see view while laying in bed. Treatment, to windows to allow blinds to be kept open as desired but privacy to be maintained, may need to be considered depending on overlook from nearby buildings.
BLIN | Bay - Linen | 2 | Up to 24 Hours | accessed intermittently |  |  | The Bay - Linen is a recessed bay to accommodate a clean linen supply or exchange trolley. Additional Considerations: The bay may be enclosed with hinged doors, sliding doors or a roller shutter where items need to be secured or enclosed. An open bay is acceptable if a covered trolley is supplied (as required by local infection control policies). Where lockable, hinged doors are provided, hold open hardware may be required to support easy movement of the trolley in and out of the bay. Door protection to suit movement of beds and equipment in adjacent area. Where a roller shutter is provided, the weight of the shutter, manual handling requirements and minimising the noise of the shutter when opening are to be considered. If bay is enclosed, a light switch or sensor may be required to provide adequate lighting when linen stock is accessed. Storage for additional items such as pillows, shower curtains, privacy curtains, etc. may be provided as either joinery, a modular shelving system, a wall mounted panel with wire baskets or a mobile trolley. The storage solution will be dependent on items to be stored and if items need to be secured or covered due to infection control requirements. Inclusion of storage should consider size and manoeuvrability of the linen trolley to be used to ensure adequate clearance. Linen trolleys can vary in height and often require a cover that is lifted from the top. In this instance, shelving above the trolley is not recommended. If the trolley is of a suitable height and a shelf is provided, it is to be mounted no higher than 1800AFFL and the reach over trolley is to be considered. Hooks may be provided for clean linen bags and may be differentiated for clinical, general and patient's personal linen. Linen bags on hooks should be able to be accessed without moving the trolley. Bay - Linen may sometimes be combined with Bay - Blanket / Fluid Warmer (see Standard Component BBW for additional space, FF&E and services requirements).
BMEQ | Bay - Mobile Equipment | 4 | Available 24 hours | accessed intermittently |  |  | An open bay for storage and recharging frequently used mobile equipment. Equipment may include wheelchairs, mobile scales, commode chairs, patient lifting devices or observation/diagnostic equipment. Additional Design Considerations: The bay should deep enough to ensure that equipment does not impede adjacent corridor circulation; a depth range from 800mm to 1500mm is recommended. Consider the manoeuverability of equipment to be stored as some items may have large turning circles and will need to be parked perpendicular, requiring a deeper bay. Power outlets may be located on the sides of deeper bays to be accessible when equipment is parked. If portable imaging equipment is to be stored additional area may be required. Data outlets may be required depending on equipment. Equipment may be recharged while stored in this space; provision of appropriately located power outlets is required. Items may be hung in this bay, e.g. a patient slide, and appropriate in-wall supports are required for mounting hooks.
BMFD-3 | Bay - Multifunction Device, 3m2 | 3 | Available 24 Hours | 1 staff intermittently |  |  | An open bay for the provision of printing, scanning and photocopying facilities and storage of stationery. Additional Considerations: Adequate ventilation to be provided over multifunction device. Adequate clearance is required around the multifunction device to allow access to easily open panels (e.g. for clearing paper jams, changing ink, restocking paper, etc.). Clearance requirements will be dependent on device specifications. Clearance to be provided in adjacent circulation space to allow for intermittent use and restocking.
BMFD-7 | Bay - Multifunction Device, 7m2 | 7 | Available 24 Hours | 1-2 staff intermittently |  |  | An open bay for the provision of printing, scanning and photocopying facilities and storage of stationery. Additional Considerations: Adequate ventilation to be provided over multifunction device. Adequate clearance is required around the multifunction device to allow access to easily open panels (e.g. for clearing paper jams, changing ink, restocking paper, etc.). Clearance requirements will be dependent on device specifications. Clearance to be provided in adjacent circulation space to allow for intermittent use and restocking.
BMT | Bay - Meal Trolley | 4 | Up to 24 Hours | accessed intermittently |  |  | The Bay - Meal Trolley is a recessed bay to accommodate meal trolleys during meal delivery and collection times. Additional Considerations: The size and type of meal trolleys to be accommodated will be dependent on service requirements and food service models (re-thermalisation, cook fresh, cook chill, mid-meals, etc.) and will need to be confirmed to inform spatial and services requirements. Consider manoeuvrability of the meal trolley to be used to ensure adequate clearance. Most meal trolleys have 2 x fixed and 2 x swivel wheels which limit movement to position in the bay. Bay may be designed without one end wall to improve trolley access and reduce WHS risks from push/pull movements with certain types of trolleys. The Bay should be deep enough to ensure trolleys do not impede corridor circulation; minimum recommended depth is 1200mm, however, the depth may need to increase to 1500mm depending on the trolley selected. Special power may be required for re-thermalisation trolleys.
BPATH | Bay - Pathology Point of Care Testing (POCT) | 3 | Available 24 Hours | 1-2 staff, intermittently |  |  | The Bay - Pathology Point of Care Testing (POCT) provides the area and facilities for the preparation and testing of specimens close to patient care areas allowing for rapid results to improve clinical decision making and patient care. Two benchtop POCT devices have been indicated, with additional devices requiring added space and services. The devices shown are placeholders as there are many POCT devices available and various combinations of devices may be provided depending on the service requirements of the unit in which this bay is located. Additional Considerations: Ready access to handwashing bay is recommended. Ready access may be required to a pneumatic tube bay that is in a staff supervised area. If providing wall mounted joinery over the bench consider clearance heights for benchtop machines, including for futureproofing. Weight requirements for machines should be considered to ensure adequate support is provided to the bench. POCT devices should not to be located in direct sunlight as they can overheat. Refrigerator temperature monitoring may be required and is to be connected to the building management system (BMS). The alarm is to provide alerts where 24-hour monitoring is undertaken, within the unit and/or remotely. Type and extent of storage to suit testing requirements, including ambient temperature storage for cartridges. Ensure adequate lighting over workspace. Power requirements (type/quantity) to be considered to suit equipment and service requirements.
BPROP | Bay - Property, Staff | 2 | Available 24 Hours | Up to 4 staff, intermittently |  | Sound attenuation level medium, Acoustic privacy is required. | A bay containing lockers for the secure storage of property including clothing, bags and personal effects. The number of lockers provided will be dependent on staff complement per shift. Additional Design Considerations: Approximately 1m2 will be required for each additional 3 x tiers of lockers. Each tier may provide up to 4 lockers. Lockers may be provided as freestanding items or built-in joinery. A proportion (minimum 2%) of lockers may be required to be accessible with locking devices located between 900mm to 1100mm AFFL.
BPTS | Bay - Pneumatic Tube Station | 1 | Available 24 Hours | accessed by staff intermittently |  |  | The Bay - Pneumatic Tube Station (PTS) provides an area for dispatching and receiving of items via the pneumatic tube system. This Standard Component represents a department based bay and additional area, FFE and services will be required for a central receiving and processing area in a pathology or pharmacy department. Additional Considerations: To be collocated or located with clear oversite from a staff station or within a staff only area. Arrival notification alarms must be programmable for different times and scenarios depending on service requirements. Security requirements are to be considered. If the station is to receive deliveries from Pharmacy or is in an area accessed by the public then secure access to a lockable receiving basket may be required depending on location of the bay. Station may be a pass through or end station and receive/dispatch through the floor or ceiling depending on location and system configuration. Radio frequency identification (RFID) technology may be considered by projects to reduce errors, improve traceability and to enable dynamic/intuitive routing to reduce "traffic jams". This technology involves embedded RFID tags in cannisters that are read by receivers at tube stations on dispatch/arrival and at interchange points in the system. Where multiple services send/receive products via the pneumatic tube system, e.g. pathology and pharmacy, colour coding the cannisters for the different streams is recommended. Colour coding to differentiate between cannisters from high priority areas, e.g. emergency and intensive care vs general wards may also be considered.
BRES | Bay - Resuscitation Trolley | 1.5 | Available 24 hours | accessed intermittently |  |  | A open bay to provide supervised holding of the resuscitation trolley and associated equipment. The bay should be located close to a Staff Station. Rapid access to the trolley and from this bay to patient areas is essential. Additional Design Considerations: Requirements for specialised resuscitation trolleys should be considered (e.g. specific trolleys are required for paediatric and neonatal departments and non-magnetic trolleys are required for some medical imaging modalities). If a department requires more than one type of resuscitation trolley to be accommodated in their bay (e.g. both adult and paediatric trolleys) additional area will be required. Additional equipment, such as ECG machines, may be accommodated in this bay in some departments. The bay shall be a minimum depth of 800mm to ensure that equipment does not impede adjacent corridor circulation. A patient slide may need to be readily available if the resuscitation trolley is required and may be provided within this bay.
BVM | Bay - Vending Machine | 2 | Available 24 Hours | 1 - 2 intermittently |  |  | The Bay - Vending Machine provides space and services for vending machines in public and staff areas. The area may be in a recessed bay along a corridor or in an open area and should be located to ensure adjacent circulation paths are not impeded with intermittent use. Each additional vending machine will require approximately 1.5m2 of additional area as well as associated services. Additional Considerations: Sufficient clearance is required around the machines for manoeuvring in the case of removal for maintenance, repair or replacement. Bulkheads and joinery surrounds may be provided to prevent users from tipping or shaking machines but should be designed to allow for access for repairs and maintenance (e.g. removable). Alternative types of vending machines such as for toiletries, phone charging accessories, etc. that may be useful to patients, visitors, and staff, e.g. for unexpected overnight stays, and staff at end of trip areas, may also be considered. Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby in line with local infection control policies.
BWC | Bay - Wheelchair Park | 4 | Available 24 hours |  |  |  | An open bay for storing wheelchairs. Typically located in close proximity to the main entrance or department entry. Additional Design Considerations: The bay should be deep enough to ensure that wheelchairs do not impede adjacent circulation space; a minimum depth of 1300mm is recommended. The ability to secure wheelchairs (e.g. with locks or by enclosing the bay) to be considered as required.
BWTR | Bay - Water Fountain | 1 | Available 24 Hours | 1 intermittently |  |  | An area, typically associated with a main entry lobby or waiting area, for a drinking water dispenser. The water dispenser may be in a recessed bay or in an open area and should be located to ensure adjacent circulation paths are not impeded with intermittent use. Additional Considerations: A water dispenser with a spout to fill disposable cups or refill drink bottles is recommended. Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby in line with local infection control policies.
CHPT | Change Cubicle - Patient | 2 | up to 24 Hours | 1 patient |  |  | The Change Cubicle - Patient provides area and amenities for ambulant patients to change into a hospital gown or appropriate clothes prior to physical therapy, examination, diagnostic imaging, treatment, procedures or surgery, and to re-dress afterwards. The cubicle should provide facilities for temporarily hanging clothes and a bench seat or chair for the patient to sit on whilst changing. Additional Considerations: Provision of a door, cubicle partition system, or privacy curtain to enclose the change cubicle is to be determined to suit patient cohort and service requirements. Where possible, the cubicle should be located so the entry opening is discreet and not facing into high traffic areas. Where door is provided it must swing outward. For door to swing inward, additional area for circulation and emergency release hardware is required. In both cases it is required that the door can be opened from the outside in an emergency. The selection of door hardware, namely handles and locks/privacy latches, must ensure usability by people with limited dexterity and motor skills. Lighting control may be provided external to the change cubicle to serve a number of change cubicles in an area, particularly where cubicle systems or privacy curtains are provided. Enclosed change cubicles may have individual light switches or motion controlled lighting. Where two-way access is provided, e.g. from a corridor and directly from a treatment or imaging room, additional area may be required to provide appropriate circulation at the second entry. Where adjacent or with direct access to an imaging room or treatment room where imaging devices are used, the change room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant. Where paediatric services are provided, additional area within change cubicles will be required to support parents/carers assisting children to change. The provision of multiple benches with different seating heights (450mm-520mm for adults and 350mm for children) may also be considered to support paediatric patients. Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. A chair may be provided in lieu of a bench seat depending on patient cohort and service requirements. The depth of the seat for both chair and bench seat options is to be adequate to support movement while changing, and the weight rating of all seating, including provision for bariatric capacity, is to be considered. The colour of seating is to contrast with the flooring and walls to support visibility and reduce the risk of falls. An operational model for responding to calls from staff/patients will be required to support the provision of the patient to staff call button, staff assist call button and emergency call button, and inclusion is to be determined based on service requirements. Additional staff assist and emergency call buttons my be located outside of the cubicle and shared between a number of change rooms depending on service requirements.
CHPT-AC | Change Cubicle - Patient, Accessible | 4.5 | up to 24 Hours | 1 patient, 1 staff / carer assisting as required |  |  | The Change Cubicle - Patient, Accessible provides area and amenities for patients using wheelchairs, walking aids and/or requiring assistance to change into a hospital gown or appropriate clothes prior to physical therapy, examination, diagnostic imaging, treatment, procedures or surgery, and to re-dress afterwards. The cubicle should provide facilities for temporarily hanging clothes and a bench seat or chair for the patient to sit on whilst changing. Additional Considerations: Provision of a door, cubicle partition system, or privacy curtain to enclose the change cubicle is to be determined to suit patient cohort and service requirements. Where possible, the cubicle should be located so the entry opening is discreet and not facing into high traffic areas. Where door is provided it must swing outward. For door to swing inward, additional area for circulation and emergency release hardware is required. In both cases it is required that the door can be opened from the outside in an emergency. The selection of door hardware, namely handles and locks/privacy latches, must ensure usability by people with limited dexterity and motor skills. Lighting control may be provided external to the change cubicle to serve a number of change cubicles in an area, particularly where cubicle systems or privacy curtains are provided. Enclosed change cubicles may have individual light switches or motion controlled lighting. Where two-way access is provided, e.g. from a corridor and directly from a treatment or imaging room, additional area may be required to provide appropriate circulation at the second entry. Where adjacent or with direct access to an imaging room or treatment room where imaging devices are used, the change room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant. Where paediatric services are provided, additional area within change cubicles will be required to support parents/carers assisting children to change. The provision of multiple benches with different seating heights (450mm-520mm for adults and 350mm for children) may also be considered to support paediatric patients. Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. The depth of the seat is to be adequate to support movement while changing, and the weight rating of all seating, including provision for bariatric capacity, is to be considered. The colour of seating is to contrast with the flooring and walls to support visibility and reduce the risk of falls. An operational model for responding to calls from staff/patients will be required to support the provision of the patient to staff call button, staff assist call button and emergency call button, and inclusion is to be determined based on service requirements. Additional staff assist and emergency call buttons my be located outside of the cubicle and shared between a number of change rooms depending on service requirements.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | 12 | 24 Hours | Up to 3 |  | Sound attenuation level - medium; acoustic privacy required. | The Patient Change areas are provided for patients to change into gowns, to store their street clothing and to perform personal ablutions. Change Rooms should be divided into Male and Female areas on a proportional basis and will include Change Cubicle, Toilet, handbasin and lockers for secure storage of personal property.
CHST-10 | Change - Staff, 10m2 | 10 | Available 24 Hours | 1-3 staff, intermittently |  | Sound attenuation level high, Acoustic privacy is required. | A room for staff to change into appropriate work clothing or gowns, to store their street clothing and to perform personal ablutions. Change rooms are typically allocated as separate male and female areas on a proportional basis. The room will be comprised of showers, toilets, basins and lockers, with numbers to suit service and staff requirements. Secure storage for personal property may be provided dependent on operational policies and service requirements. Additional Design Considerations: Accessible change facilities for staff to be provided nearby. A proportion (minimum 2%) of lockers may be required to be accessible with locking devices located between 900mm to 1100mm AFFL. Secure, staff-only access to change rooms is required. Visual privacy from the entry door to the changing areas and cubicles is to be considered during planning. If provided for staff to change for sterile procedures, access to clean linen will be required
CHST-35 | Change - Staff, 35m2 | 35 | Available 24 Hours | Up to 16 staff, intermittently |  | Sound attenuation level high, Acoustic privacy is required. | A room for staff to change into appropriate work clothing or gowns, to store their street clothing and to perform personal ablutions. Change rooms are typically allocated as separate male and female areas on a proportional basis. The room will be comprised of showers, toilets, basins and lockers, with numbers to suit service and staff requirements. Secure storage for personal property may be provided dependent on operational policies and service requirements. Additional Design Considerations: Accessible change facilities for staff to be provided nearby. A proportion (minimum 2%) of lockers may be required to be accessible with locking devices located between 900mm to 1100mm AFFL. Secure, staff-only access to change rooms is required. Visual privacy from the entry door to the changing areas and cubicles is to be considered during planning.
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | 60 | Available 24 Hours | 1 patient; up to 6 staff |  | Acoustic privacy is required | A highly specialised procedure room where interventional Cardiac Catheter procedures are undertaken in an aseptic environment and may include administration of sedation or general anaesthesia. The Catheter Laboratory - Electrophysiology Studies may also be used for electrophysiology (EP) studies and treatment and is typically only provided in hospitals of tertiary level or higher, where required. A Control room will be located adjacent and may serve more than one procedure room. A clinical scrub area should be located immediately adjacent to the staff entry. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. A strut channel system able to carry moving loads may be required. Cable ducts from Control Room and Equipment room will be required. 'X-Ray in Use' lights are required outside each entry door. Power to imaging equipment should be on emergency supply. The Catheter Laboratory for EP studies will require radiofrequency shielding.
CLAB-I | Catheter Laboratory - Interventional | 55.5 | Available 24 Hours | 1 patient; up to 6 staff |  | Acoustic privacy is required | A procedure room where interventional Cardiac Catheter procedures are undertaken in a controlled, clean environment and may include administration of sedation or, much less commonly, general anaesthesia. A Control room will be located adjacent and may serve more than one procedure room. A clinical scrub area should be located immediately adjacent to the staff entry. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. A strut channel system able to carry moving loads may be required. Cable ducts from Control Room and Equipment room will be required. 'X-Ray in Use' lights are required outside each entry door. Power to imaging equipment should be on emergency supply.
CLCR-EP | Catheter Laboratory EP Control Room | 17 | Available 24 Hours | Up to 4 staff |  | Acoustic privacy is required | Room adjacent to Catheter Lab EP Procedure Room/s with direct visibility to the patient for remote control of equipment, and review and reporting of images. The Control Room may serve two procedure rooms. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. Cable ducts from Catheter Lab Procedure Room and Computer/Equipment room will be required.
CLCR-I | Catheter Laboratory Interventional Control Room | 14 | Available 24 Hours | Up to 3 staff |  | Acoustic privacy is required | Room adjacent to Catheter Lab Interventional Procedure Room/s with direct visibility to the patient for remote control of equipment, and review and reporting of images. The Control Room may serve two procedure rooms. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. Cable ducts from Catheter Lab Procedure Room and Equipment room will be required.
CLN-10 | Clean Store, 10m2 | 10 | 24 Hours | 1 - 2 staff intermittently |  |  | The Clean Store, 10m² provides space for the storage of clean consumables and equipment for patient care.
CLN-MED-20 | Clean Store / Medication Room, 20m2 | 20 | 24 Hours | 1 - 2 staff intermittently |  |  | The Clean Store / Medication Room, 20m² provides a space for the storage of clean consumables and the secure storage of medications, including intravenous fluids. The room may provide storage for drugs of dependence in accordance with relevant legislation. Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. Secured staff only access to the room is required. The provision and placement of CCTV cameras is dependent on jurisdictional policies. Refer to project specific requirements for the provision of automated medication management systems.
CLN-MED-S | Clean Store / Medication Room, Sub | 8 | 24 Hours | 1 - 2 staff intermittently |  |  | The Clean Store / Medication Room, Sub provides a small space for the storage of clean consumables and the secure storage of medications, including intravenous fluids. The room may provide storage for drugs of dependence in accordance with relevant legislation. Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. Secured staff only access to the room is required. The provision and placement of CCTV cameras is dependent on jurisdictional policies. Refer to project specific requirements for the provision of automated medication management systems.
CLRM | Cleaner's Room | 5 | 24 Hours | 1-2 staff intermittently |  |  | The Cleaner's Room is a secure room for the storage and decanting of cleaning materials, washing and storage of cleaning equipment and cleaner's trolley, and for liquid waste disposal. This room may be shared between multiple units depending on service requirements. Additional Considerations: Size requirements for a Cleaner's Room will be dependent on the department to be serviced and operational models for staffing and cleaning regimens that may dictate the type of equipment and number of trolleys to be accommodated. Where more than one trolley will be stored an additional 1.5m2 is required per trolley. The requirements to accommodate vacuum cleaners, floor scrubbers or other floor cleaning equipment within the Cleaner&#8217;s Room is to be determined at a project/department level in conjunction with assessment of finishes and cleaning requirements. Where operational models do not provide a centralised area for the storage of large cleaning equipment (e.g. floor scrubbers), additional area may be required in units or in shared areas between units depending on the additional equipment to be stored. Considerations regarding detergent/chemical management system to be confirmed at a project level, including water connection and associated services requirements (including back flow prevention). Extent and type of storage for chemicals and consumables is to suit service requirements. Consideration of the weight of chemical bottles is required when determining appropriate storage solutions (i.e. if storing chemicals in bottles over 1 litre then low-height shelving is required to avoid lifting of heavy items from high shelves). Hold open door hardware may be provided for hinged doors to allow for easy movement of trolleys in and out of the room. Controlled, staff-only access may be required if this room is provided in a public or patient care area.
CLUP-7 | Clean-Up Room, 7m2 | 7 | 24 Hours | 1 - 2 |  |  | The Clean-Up Room is used for holding of used trolleys and articles from an Operating Room, Procedure Room or Catheter Laboratory. Items may be sorted, rinsed or disposed of and despatched to waste holding/sterilising areas as appropriate.
COMM | Communications Room | 15 | 24 Hours | 1 - 2 intermittently |  |  | A secure room for engineering services to accommodate racks, backbone cabling and interface control panels for information and communication systems. Systems may include master antenna television (MATV), internet protocol television (IPTV), nurse call, security, telecommunications, building management system (BMS) and Fire/EWIS systems. Additional Considerations: The area shown is indicative; the size of the Communications Room will vary according to engineering consultant advice based on systems to be accommodated. Head end units for security, nurse call, BMS, TMV, IPTV/MATV to be accommodated as required. Equipment located in this room will require uninterruptible power fed from the essential supply (generator). Dedicated air conditioning that is monitored by the Building Management System (BMS) is required Provide adequate lighting to ensure visibility to both front and rear of racks. The configuration of power and data (i.e., wall mounted or ceiling mounted services) to supply the racks is to be determine base on the room layout and equipment selected. The Communication Room must be located such that it is not susceptible to possible water damage or excessive electromagnetic interference. Water or gas pipes must not pass through a Communication Room. Where a Distributed Antenna System (DAS) for in-building mobile reception is provided, the telco carrier base station equipment is to be located in the Communications Room. Refer to telco for spatial requirements to determine sizing of the Communications Room. A DAS shall conform to the most recent edition of the Mobile Carriers Forum Design Specification for Distributed Antenna Systems.
CONS | Consult Room | 12 | 24 Hours | 1 patient: 1-2 staff, 1-2 visitors |  | Sound attenuation level high, Acoustic privacy is essential. | The Consult Room will provide for private consultation and physical examination of patients with or without support persons present. A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements.
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | 16 | 24 Hours | 1 patient; 1-2 staff, 1-2 visitors |  | Sound attenuation level high, acoustic privacy is essential. | The Consult Room ENT/ Ophthalmology will provide for private consultation and examination of patients for ENT/ Ophthalmology using specialised equipment. The Consult room may also be used for general consultations. A second egress door may be required for staff safety and security and/or staff access, subject to jurisdictional policy. Ready access to a fridge will be required for retrieval of eye medication. If eye testing is provided via a visual acuity chart and mirror, a distance of 3m is required between the eye chart and mirror for effective eye testing.
CONS-UN | Consult Room - Universal Access | 17 | 24 Hours | 1 patient: 1-2 staff, 1-2 visitors |  | Sound attenuation level high, Acoustic privacy is essential. | The Consult Room - Universal Access will provide for private consultation and physical examination of a range of patients with or without support persons present. The spatial allowance will accommodate patients who (a) are using a wheelchair, including a bariatric sized wheelchair; or (b) require a hoist to transfer. The position of the basin, dispensers and other fittings also allows for use by staff in wheelchairs. A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. It is anticipated that one of these rooms may be provided within a 'pod' of consult rooms. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements.
CORR | Corridor - Patient Treatment Areas | 0 | 24 hours |  |  |  | The Corridor - Patient Treatment Areas indicates requirements for circulation spaces between patient treatment spaces, patient accommodation and clinical support spaces within departments. Corridor widths will vary between departments and will depend on the requirement for frequent bed transportation; widths must allow for the safe movement and passing of trolleys, beds, wheelchairs and other mobile equipment as required. Provision should be made for situations where oversized additional equipment, e.g. bed extensions or bariatric beds, are in use. Guidance for the calculation of areas (m2) for corridors is provided for in Health Planning Unit Schedules of Accommodation as circulation percentages. Refer to AusHFG Part C: Design for Access, Mobility, Safety and Security for further information. Additional Design Considerations: Wall protection is recommended to protect wall linings and finishes from damage from impact. The height of the wall protection will be dependent on equipment frequently moved through the space; a height range of 900mm minimum up to 1500mm is recommended depending on service requirements. Handrails are to be provided along not less than one side of all corridors in patient care areas to provide assistance and support for patients and visitors. Handrails are to be continuous along the corridors wherever practical. Cleaner's electrical outlets to be provided at regular intervals as per mandatory requirements. Corridor lighting, where patients are transported on beds/trolleys, should be positioned to prevent unnecessary glare to patient eyes. Light fittings shall be recessed, flush fitting and sealed to prevent dust ingress. Manual controls to power-operated doors shall be located on the continuous accessible path of travel no closer than 500 mm from an internal corner and between 1000 mm to 2000 mm from the hinged door leaf in any position as per the requirements of AS1428.1.
CTCR | CT Imaging Control Room | 12 | Available 24 Hours | Up to 4 staff |  | Acoustic privacy is required | Room adjacent to CT Imaging Room/s with direct visibility to the patient for remote control of equipment, and review and reporting of images. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. Cable ducts from CT Imaging and CT Equipment Room will be required. Additional space maybe required for an AW workstation if included in the Control Room which will require 2 GPOs.
CTIR | CT Imaging Room | 45 | Available 24 Hours | 1 patient; up to 3 staff assisting |  | Acoustic privacy is required | A Room for Computed Tomography (CT) scanning procedures with an adjacent Control Room and Equipment Room. The Control Room and Equipment room will need to be located in close proximity due to acceptable cable lengths. The Control Room may serve more than one CT Imaging Room. General Anaesthesia may be administered in this room. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. Unistrut ceiling able to carry moving loads may be required. Cable ducts between Control Room and Equipment Room will be required. 'X-ray in Use' lights are required outside each entry door. Power should be on emergency supply. Dimmable lighting is optional.
CTPR | CT Planning Room | 45 | 8am to 6pm, Monday – Friday (extended hours, weekends and/or emergency access may be required) | 1 patient; up to 3 staff assisting |  | Acoustic privacy is required | The CT Planning Room provides space and facilities for Computed Tomography (CT) scanning procedures as part of the planning of radiation therapy treatment for patients. A collocated Control Room with observation window is required for the remote operation of equipment. An Equipment Room may be required and will need to be in close proximity due to acceptable cable lengths. Cable ducts between the Scanning Room, Control Room and Equipment Room will be required. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. The CT Planning Room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant to suit the equipment procured. 'X-ray in Use' lights are required outside each entry door to be illuminated when scanning begins. Interlock system to doors recommended to prevent machine from running if door open and to stop the machine upon entry if in use. Additional Considerations: Additional medical gases may be provided (including additional oxygen, additional suction, nitrous oxide and scavenge) depending on clinical requirements, such as the provision of anaesthetic services. Dimmable lights are to be provided and lights are to be placed to avoid glare to patients. Back lit ceiling artwork may be installed for patient comfort and distraction. Where possible, it is preferred that ductwork in the ceiling is designed to the perimeter of room to allow for future flexibility to provide ceiling mounted equipment. The need for and extent of emergency and UPS power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Unistrut ceiling able to carry moving loads may be required. A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be provided depending on clinical/service requirements and will be coordinated to support the technologies provided in the Linear Accelerator Treatment Room. The provision of these technologies is to be confirmed by the project and may have additional design requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors.
DEN-MLB | Dental Laboratory, Minor | 12 | 8am to 6pm, daily | 1-2 staff |  | Sound attenuation high: Acoustic privacy required | The Minor Dental Laboratory provides facilities and equipment for dental clinicians/technicians to make adjustments to dentures or other dental prosthetics, and to store prosthetic supplies. Additional Design Considerations: Dust extraction is required at the source and may be integral to equipment in some instances. If Bunsen burner to be used in this room, gas outlet or portable gas is required and overhead joinery may need to be reviewed to provide appropriate clearance. A workstation with computer and barcode scanner may be provided for digital tracking and records.
DENSR-1 | Dental Surgery, Type 1 | 14.5 | Available 24 Hours | 1 patient, 1-2 staff, 1-2 visitors |  | Sound attenuation level high, Acoustic privacy is required. | The Dental Surgery provides for dental consultation, examination and treatment for patients. This Standard Component provides a configuration for switching between a a right-handed and left-handed set-up and should not be mirrored. Dental surgery layouts will vary and will be dependent on existing/proposed workflows and the equipment procured. Additional Design Considerations: Services will be required for the dental chair unit; these will be dependent on the chair model and supplier and include dental air, dental suction, filtered water, power and drainage. Facilities for viewing physical x-ray films brought in by patients may be provided in a central location as required. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Radiation shielding to be advised by Radiation Consultant. An external outlook is desirable.
DENSR-2 | Dental Surgery, Type 2 | 14.5 | Available 24 Hours | 1 patient, 1-2 staff, 1-2 visitors |  | Sound attenuation level high, Acoustic privacy is required. | The Dental Surgery provides for dental consultation, examination and treatment for patients. This Standard Component shows a right-handed configuration and should not be mirrored. The layout may be adjusted to provide an ambidextrous set up. Dental surgery layouts will vary and will be dependent on existing/proposed workflows and the equipment procured. Additional Design Considerations: Services will be required for the dental chair unit; these will be dependent on the chair model and supplier and include dental air, dental suction, filtered water, power and drainage. Facilities for viewing physical x-ray films brought in by patients may be provided in a central location as required. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Radiation shielding to be advised by Radiation Consultant. An external outlook is desirable.
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | 25 | 24 Hours | Up to 8 patients; 1-2 staff |  | Sound attenuation level medium, Acoustic privacy is required. | The Dining Room/ Beverage Bay is an area provided for patients within the Mental Health Unit to eat their meals, away from the bedroom environment. The Dining Room may be used for other patient activities when not in use for meals. Access and dining space should be provided for patients with disabilities. The Beverage Bay will include a servery counter and will require restricted access. Access to an external courtyard area is desirable. Finishes, fittings & fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. Dimmable lights are optional.
DINR | Dining - Patient | 40 | Up to 24 Hours | 16 patients seated, 3-4 staff intermittently |  | Sound attenuation level high; acoustic privacy is required. | The Dining Room is an area provided for patients to eat their meals away from the bedroom environment in an inpatient setting. The Dining Room may be used for other patient recreational activities when not in use for meals. In this instance, additional transfer of noise to adjacent patient care areas to be considered. Additional Considerations: Food services model, e.g. meal trolley (tray or re-thermalisation), servery, beverage bay, etc. will impact room design. A kitchen, servery or beverage bay may be collocated or combined with the Dining Room. Size of space will depend on number of beds and models of care; designed area based on 3m2 per person. Access will be required for patients with limited mobility including wheelchairs, walking frames and other walking aids. Design must also consider the needs of patients with dementia and frail/elderly. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. Duress provision will be dependent on service requirements. Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. Lighting to be consistent across the space. Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. Where possible a achieving a domestic appearance with furniture, fittings and finishes is recommended. The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. Natural light and external outlook is essential.
DISP-10 | Disposal Room, 10m2 | 10 | Up to 24 Hours | 1-2 staff, accessed intermittently |  |  | The Disposal Room provides for the temporary holding of waste, separated into various waste streams (general waste, clinical waste, cardboard recycling, co-mingled recycling, cytotoxic waste, confidential waste, sharps, soiled linen, etc.) prior to removal to a designated waste zone in the loading dock. Waste will be collected at regular times each day, or when requested, to prevent build-up of waste in the unit. Additional Considerations: Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes. Adequate space must be provided to allow for segregation of waste streams. The use of 660 L bins should be carefully considered due to the WHS risks associated with manual handling, however it is acknowledged in some areas with significant waste output they may be required. Where the weight of full waste receptacles is a concern, the use of tugs/ACVs is often required. Waste transfer may be manual, by motorised movers/tugs or via automated guided vehicle (AGV) systems. Where tugs and AGVs are being considered, it is important to confirm clearances, door widths and turning circles within the room, in the adjacent corridor and along path of travel to designated waste zone. Hold open door hardware may be required to allow for easy movement of bins and trolleys in and out of the room. Shelf may be provided for storage of small sharps bins prior to collection. If a handwashing basin is not provided within the Disposal Room, one should be located in close proximity. The location of hand hygiene facilities may be dependent on local infection control policies. Staff only access may be required if this room is provided in a public or patient care area.
DISP-15 | Disposal Room, 15m2 | 15 | Up to 24 Hours | 1-2 staff, accessed intermittently |  |  | The Disposal Room provides for the temporary holding of waste, separated into various waste streams (general waste, clinical waste, cardboard recycling, co-mingled recycling, cytotoxic waste, confidential waste, sharps, soiled linen, etc.) prior to removal to a designated waste zone in the loading dock. Waste will be collected at regular times each day, or when requested, to prevent build-up of waste in the unit. Additional Considerations: Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes. Adequate space must be provided to allow for segregation of waste streams. The use of 660 L bins should be carefully considered due to the WHS risks associated with manual handling, however it is acknowledged in some areas with significant waste output they may be required. Where the weight of full waste receptacles is a concern, the use of tugs/ACVs is often required. Waste transfer may be manual, by motorised movers/tugs or via automated guided vehicle (AGV) systems. Where tugs and AGVs are being considered, it is important to confirm clearances, door widths and turning circles within the room, in the adjacent corridor and along path of travel to designated waste zone. Dual access from within a unit and from an external services corridor may be provided depending on overall planning arrangement. Hold open door hardware may be required to allow for easy movement of bins and trolleys in and out of the room. Shelf may be provided for storage of small sharps bins prior to collection. If a handwashing basin is not provided within the Disposal Room, one should be located in close proximity. The location of hand hygiene facilities may be dependent on local infection control policies. Staff only access may be required if this room is provided in a public or patient care area.
DTUR-10 | Dirty Utility, 10m2 | 10 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility, 10m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 10m² fit out.
DTUR-12 | Dirty Utility, 12m2 | 12 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility, 12m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 12m² fit out.
DTUR-14 | Dirty Utility, 14m2 | 14 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility, 14m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. The Dirty Utility, 14m2 may provide access doors from both sides of the room. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 14m² fit out.
DTUR-S | Dirty Utility, Sub | 8 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility, Sub provides a small space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, Sub fit out.
ECHO-TOE | Echocardiography - Transoesophageal | 26 | Available 24 Hours | 1 patient; 1 - 2 staff |  | Acoustic privacy is required | Room for diagnostic echocardiography procedures including transoesophageal echocardiography. Echocardiography procedures may be performed under local anaesthesia and sedation. The Echocardiography room should be located close to patient toilet and change rooms.
ECL-10 | Equipment Clean-Up, 10m2 | 10 | 24 Hours | 1 - 2 |  |  | The Equipment Clean-Up Room is used for cleaning and maintaining of equipment used in the Unit. Storage may be required for holding cleaned equipment and spares. Equipment may also be recharged in this room. Natural light is desirable.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | 12 | 24 Hours | 1 - 2 staff intermittently |  |  | The Equipment Clean Up Room is used for cleaning of equipment used in patient care or loaned to outpatients following return. Storage will be required for holding cleaning equipment.
ECL-14 | Equipment Clean-Up, 14m2 | 14 | 24 Hours | 1 - 2 |  |  | The Equipment Clean-Up Room is used for cleaning and maintaining of equipment used in the Unit. Storage may be required for holding cleaned equipment and spares. Equipment may also be recharged in this room. Natural light is desirable.
ECL-8 | Equipment Clean-Up, 8m2 | 8 | 24 Hours | 1 - 2 |  |  | The Equipment Clean-Up Room is used for cleaning and maintaining of equipment used in the Unit. Storage may be required for holding cleaned equipment and spares. Equipment may also be recharged in this room. Natural light is desirable.
ENS-ACC | Ensuite - Accessible, 7m2 | 7 | 24 Hours | 1 patient; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for use by a patient with a disability to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The room shall comply with AS1428. The area and layout must accommodate an assisting nurse and a shower commode. Mobile patient lifters will not routinely be used within this space but the ensuite should accommodate this equipment in the case of a patient fall. Additional design requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining floor. The door is to be fitted with escape hardware.
ENS-BA | Ensuite - Bariatric, 7m2 | 7 | 24 Hours | 1 patient; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Bariatric is designed to meet the needs of bariatric (obese or morbidly obese) patients allowing the patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The Ensuite - Bariatric is associated with the 1 Bed Room - Bariatric. The area and layout must accommodate two assisting nurses and a shower commode with bariatric capability. The Ensuite and Bedroom will need to be planned as an integral suite so the use of a ceiling mounted hoist is optimised across the two rooms. The choice of Ensuite will depend on the patient type, the Operational Policy and floor layout of the facility. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.
ENS-BR | Ensuite - Birthing | 7 | 24 Hours | 1 mother; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Birthing Room is for a mother to wash, shower and use the toilet, either independently or with assistance. During labour, the shower may be used for extended periods to manage pain and two shower heads are provided to support this. The area and layout must accommodate an assisting midwife and a support person. Additional Considerations: The Ensuite - Birthing will have direct access from the Birthing Room. The shower floor must not have a raised hob and the entrance to the ensuite is to be flush with the adjoining flooring. A ladder or other wall mounted supportive fixtures may be included to provide support at various heights and facilitate different postures during active birthing. A birthing woman's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. Item to be suitable for wet area.
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting as required |  | Sound attenuation level high, Acoustic privacy is required. | The Ensuite - Mental Health will provide a shower, toilet and handbasin for use by patients in a mental health inpatient unit. The Ensuite will be lockable and master keyed from the outside. All fittings and fixtures used in consumer areas of the building must be of a type manufactured and marketed as anti-ligature; and installed in accordance with the manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. Selected fixtures are to have a breaking strain of not more than 15kg (e.g. shower curtain rail). Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting as required |  | Sound attenuation level high, Acoustic privacy is required. | The Ensuite - Mental Health will provide a shower, toilet and handbasin for use by patients in a mental health inpatient unit. The Ensuite will be lockable and master keyed from the outside. All fittings and fixtures used in consumer areas of the building must be of a type manufactured and marketed as anti-ligature; and installed in accordance with the manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. Selected fixtures are to have a breaking strain of not more than 15kg (e.g. shower curtain rail). Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.
ENS-SH | Ensuite - Shared, 6m2 | 6 | 24 Hours | 1 patient; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Shared is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse, patient lifter and wheelchair access. The Ensuite shared may be accessed from two patient rooms. Special privacy latching will be required to lock both entry doors on activation. The actual choice of Ensuite will depend on the patient type and the Operational Policy of the facility. The Ensuite - Shared may vary in configuration to suit different patient types or room types including: ENS-SH-A Shared ensuite - standard, ENS-SH-B Shared ensuite with additional access. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring.
ENS-SP | Ensuite - Special, 6m2 | 6 | 24 Hours | 1 patient; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Super is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The Ensuite - Super is associated with the 1 Bed Room - Special; the additional area and layout will facilitate two assisting nurses, patient lifter and wheelchair access. The Ensuite - Super may vary in configuration to suit different patient types or room types including: ENS-SP-A Ensuite Super, Inboard, ENS-SP-B Ensuite Super, Stand alone. The actual choice of Ensuite will depend on the patient type, the Operational Policy and floor layout of the facility. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse and a shower commode. The Ensuite and Bedroom should be planned as an integrated suite so the layout is optimised across the two rooms. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse and a shower commode. The Ensuite and Bedroom should be planned as an integrated suite so the layout is optimised across the two rooms. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse and a shower commode. The Ensuite and Bedroom should be planned as an integrated suite so the layout is optimised across the two rooms. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.
ENS-ST-B | Ensuite - Outboard, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse and a shower commode. The Ensuite and Bedroom should be planned as an integrated suite so the layout is optimised across the two rooms. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.
ENS-ST-C | Ensuite - Back to Back, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse and a shower commode. The Ensuite and Bed Room should be planned as an integrated suite so the layout is optimised across the two rooms. In the case of a Ensuite - Back to Back, this planning will involve integration across 2 bed rooms. The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.
FLUO | Fluoroscopy Room | 40 | Available 24 Hours | 1 patient; 1 - 2 staff |  | Acoustic privacy is required | The Fluoroscopy Room is a room for undertaking radiographic procedures involving contrast media. General anaesthesia may be given in this room. A control room is required accessed from the Fluoroscopy Room. An Equipment Room for equipment generating noise and heat is to be considered subject to equipment manufacturer. The Control Room and Equipment Room will need to be located in close proximity due to acceptable cable lengths. Power and control cabinets may be located within the room. An accessible toilet with changing facilities and shower accessed directly from the Fluoroscopy Room is required. A preparation area with sink is required in the room. The room may be used as an overflow general x-ray room. Additional Design Requirements: Radiation shielding to walls and lead lined glass as advised by Radiation Consultant. Shielded observation window will be required where patient observation cameras are not in use. Unistrut support at ceiling level and 3000mm AFFL ceiling may be required, depending on equipment to be installed. Cable ducting between the imaging unit table, equipment and control area will be required, depending on equipment type and layout. 'X-ray in Use' warning lights will be required outside each entry door. Equipment access route clearances to be considered.
FLUOC | Fluoroscopy Control Room | 12 | Available 24 hours | Up to 2 staff |  | Acoustic privacy is required | Room adjacent to the Fluoroscopy Room with direct visibility to the patient for remote control of equipment, and review and reporting of procedure images. Additional Design Considerations: Radiation shielding as advised by radiation consultant. Cable ducts from the imaging and equipment room will be required.
GENXR | General X-Ray Room | 38 | Available 24 Hours | 1 patient; 1 - 2 staff |  | Acoustic privacy is required | General X-ray is a room for undertaking general radiographic imaging, and may be located within the Imaging Unit or within an Emergency Unit. Additional Design Requirements: Radiation shielding to walls and glazing as advised by Radiation Consultant. Unistrut type ceiling may be required, depending on equipment to be installed. Cable ducting between the X-ray table, vertical bucky and control area will be required, depending on equipment type and layout. 'X-ray in Use' warning lights will be required outside each entry door. If located within the ED, quantity of services may need to align with Acute Treatment bays for trauma use.
GYAH-GP | Gymnasium, Group Therapy | 105 | 7am to 6pm, daily | up to 15 patients, 2-3 staff |  | Acoustic privacy is required | The Gymnasium - Group Therapy provides space and facilities for patient evaluation, rehabilitation exercise activities, therapy and ambulation training in a group setting. An open area is typically provided for aerobic/movement exercises and may also provide space for group debriefing, discussion and education after sessions. An external outlook and ready access to outdoor areas is desirable. The range of specialised exercise equipment, open exercise areas and number of clients / patients to be accommodated within a gymnasium will vary from unit to unit and will require confirmation to inform overall space requirements. Additional Design Requirements: RCD protection is required to body protected areas in accordance with AS/NZS3003. Quantity and location dependent on selected equipment and circuiting arrangements.
GYAH-ID | Gymnasium, Individual Treatment | 76 | 7am to 6pm, daily | up to 8 patients, 3 staff |  | Acoustic privacy is required | The Gymnasium - Individual Treatment provides space and facilities for one on one patient evaluation, therapy and ambulation training. A number of curtained bays with plinths are typically provided along with an open area accommodating a range of equipment such as stairs, parallel bars and exercise bikes. An external outlook and ready access to outdoor areas is desirable. The range of specialised exercise equipment, open exercise areas and number of clients / patients to be accommodated within a gymnasium will vary from unit to unit and will require confirmation to inform overall space requirements. Additional Design Requirements: RCD protection is required to body protected areas in accordance with AS/NZS3003. Quantity and location dependent on selected equipment and circuiting arrangements.
HYDP | Hydrotherapy Pool | 260 | 7am to 8pm, daily | Up to 12 patients, 2-3 staff |  |  | The Hydrotherapy Pool is for patient therapy, rehabilitation and exercise under supervision. The pool size indicated is 15m x 6m (90m2 - not including pool surrounds). Pool and surrounds to comply with AS 3979 - Hydrotherapy Pools. Additional Design Considerations: Ready access is required to adequate change facilities for clients/patients and staff, including accessible showers and toilets. Emergency call points may be wall mounted and/or ceiling-suspended depending on the staffing model and local operational policies. Appropriate storage for aids and equipment will be required separately to the storage of pool maintenance equipment and chemicals. Depth 0.9m to 1.5 m with gradual slope. Depth at deep end may be reduced if paediatric use is likely to be frequent. Ramp access and stair access to be provided with handrails. Pool handrails are required and are not to be recessed. All stainless steel railing to be chlorine resistant. Temperature of water to be 33-34 degrees. Temperature of air to be no more than 6 degrees below water temperature. Wet deck - single channel. Water to be earthed. Internal pool surface and pool surrounds shown as tiled. Tiles or other suitable surface to be non-slip; ensure a high level of slip resistance to tiles on the ramp (vertical surfaces of tiling do not need to be slip resistant). Pool blanket is optional for insulation for energy conservation. Hydraulic hoist may be required; weight rating to be confirmed at project level to suit service requirements. Underwater pressure jets for therapeutic purposes are optional. Departmental planning to provide external windows is recommended. Disinfection system to be advised by expert consultant. Pool may be made available to the community after-hours and on the weekends. Careful consideration will need to be given to location, controlled access and security.
INTF-MH | Interview Room - Mental Health | 14 | Varies | 1 Patient; 1-2 staff; 1-2 visitors |  | Sound attenuation high; acoustic privacy is required | The Interview Room - Mental Health provides a room that can be used by patients with mental health conditions for interviews or counselling. The room has been configured to reduce risks to both staff and patients. A secondary egress door is shown.All fittings must be of a type manufactured as anti ligature and installed in accordance with manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. All glass must be Grade A safety glass to comply with AS1288 and AS/ANZ 2208, specifically toughened laminated glass of min. 14.28mm thickness or equivalent approved. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.
INTV | Interview Room | 12 | 24 Hours | Up to 8 persons |  | Sound attenuation level high, Acoustic privacy is required. | The Interview Room provides space for confidential discussion and/or counselling between staff, patients and/or family members where required. The Interview Room may also be used as a multipurpose room for small staff groups or discussions. An external outlook is desirable. Assumes staff will bring their own devices as required. A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements
LAUN-MH | Laundry - Mental Health, 6m2 | 6 | 24 Hours | 1 - 2 |  |  | Domestic style laundry for use by mental health patients with staff supervision. The room will include a bench, laundry tub, domestic washing machine and dryer and ironing facilities. All fittings to be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. Door and joinery hardware should not provide ligature points. Airconditioning outlets to be tamper proof.
LAUN-PT | Laundry - Patient, 6m2 | 6 | 24 Hours | 1 - 2 |  |  | Domestic style laundry for patient use. The room will include a bench, laundry tub, domestic style washing machine, dryer and ironing facilities.
LINAC | Linear Accelerator Treatment Room | 165 | 8am to 6pm, Monday – Friday (extended hours, weekends and/or emergency access may be required) | 1 patient, 1-4 staff |  | Acoustic privacy is required | The Linear Accelerator Treatment Room provides space and facilities for the treatment of patients requiring external beam radiation therapy (EBRT). A collocated Control Room is required for the remote operation of equipment. Cable pathways for services between the Control Room, Modulator Room and Treatment Room must be established and coordinated prior to construction and developed based on vendor and physics requirements. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. The Treatment Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints, including the provision of a maze entry or shielded door. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. The modulator may need to be accommodated within the Treatment Room. If so, this will be concealed by a wall, with a door for access. Depending on the quality of the power supply at a site, a power conditioner may be required and is typically located with the modulator. Additional noise from this equipment should also be accounted for with acoustic treatment. Visibility of the Treatment Room from exit and via observation cameras is required to ensure all persons are clear of the room before treatment commences. A last person out button is to be provided, as well as a sensor gate and/or physical gate at the entry of the maze. A &#8216;Beam-On/Off&#8217; light system is required at the entry to be illuminated when treatment begins/ends. Additional Considerations: Additional medical gases may be provided (including additional oxygen, additional suction, nitrous oxide and scavenge) depending on clinical requirements such as the provision of anaesthetic services. Acoustic requirements will vary depending on the equipment procured and its proximity to the patient treatment area. For patient and staff comfort, acoustics should be considered to reduce the impact of noise from the equipment. Dimmable lights are to be provided and are to be placed to avoid glare to patients. Back lit ceiling artwork may be installed for patient comfort and speakers and connections should be provided to allow music to be played and controlled individually for each bunker. Air conditioning is to be provided to control the room temperature and humidity to meet the equipment suppliers&#8217; requirements; high equipment loads shall be accounted for. Air conditioning equipment shall be located outside of this room with ductwork to be installed to follow the entry maze with any penetrations considered to ensure radiation protection. Where possible, it is preferred that ductwork in the ceiling is designed to the perimeter of room for future flexibility to provide ceiling mounted equipment. Cooling shall be provided to the linear accelerator equipment in the form of chilled water to meet the supplier&#8217;s requirements, independent chiller equipment is preferred. The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. Small UPS units are normally required as a minimum to support control and operating equipment. In some cases, these are supplied with the medical equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be provided depending on clinical/service requirements. The provision of these technologies is to be confirmed by the project and may have additional requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. Allow sufficient distance between the isocentre of the machine and primary shielding wall for the flexibility to provide specialised treatments, e.g. Total Body Irradiation (TBI), depending on service requirements.
LINAC-CR | Linear Accelerator Control Room | 21 | 8am to 6pm, Monday – Friday (extended hours, weekends and/or emergency access may be required) | 2-5 staff |  | Acoustic privacy is required | The Linear Accelerator Control room is located adjacent to the Treatment Room for remote control of equipment with audio and visual contact with the patient via cameras, speakers and microphones. Each Treatment Room requires a Control Room. Cable pathways for services between the Control room to the Treatment Room must be established and coordinated prior to construction. Radiation shielding is to be as advised by a Radiation Consultant. Additional Considerations: Air conditioning to provide comfort conditions; high equipment loads shall be accounted for. The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. Small UPS units are normally required as a minimum to support control and operating equipment. In some cases, these are supplied with the medical equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Cable management and the potential for computers to be consolidated into a rack (either within the room or in a dedicated, collocated air conditioned room/cupboard) to be determined at project level. Provision of a height adjustable workstation may be considered depending on local policies and staff accessibility requirements.
LNGE-10 | Lounge - Patient / Visitor, 10m2 | 10 | Up to 24 Hours | Up to 6 patients/visitors; 1-2 staff intermittently |  | Sound attenuation level medium; acoustic privacy is required. | The Patient Lounge provides an environment away from clinical areas and/or patient bedrooms for patients and visitors to meet and socialise. It is an area where family groups can visit together with patients. A range of occupants will need to be accommodated including adults, children, able-bodied people as well as people with disabilities. Additional Considerations: The size of lounge areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. Access for a patient lifter or patient bed may be required depending on patient cohort and service requirements. The Patient Lounge is often located in close proximity to or combined with a Bay - Beverage. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. Duress provision will be dependent on service requirements. Provision of a hearing augmentation system may be required depending on television and amplification system provided. Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. Room may be designed to be open to a corridor. Additional transfer of noise to adjacent patient care areas to be considered if room is not enclosed. The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. Natural light and external outlook is essential.
LNGE-20 | Lounge - Patient / Visitor, 20m2 | 20 | Up to 24 Hours | Up to 10 patients/visitors; 1-2 staff intermittently |  | Sound attenuation level medium; acoustic privacy is required. | The Patient Lounge provides an environment away from clinical areas and/or patient bedrooms for patients and visitors to meet and socialise. It is an area where family groups can visit together with patients. A range of occupants will need to be accommodated including adults, children, able-bodied people as well as people with disabilities. Additional Considerations: The size of lounge areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. Access for a patient lifter or patient bed may be required depending on patient cohort and service requirements. The Patient Lounge is often located in close proximity to or combined with a Bay - Beverage. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. Duress provision will be dependent on service requirements. Provision of a hearing augmentation system may be required depending on television and amplification system provided. Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. Room may be designed to be open to a corridor. Additional transfer of noise to adjacent patient care areas to be considered if room is not enclosed. The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. Natural light and external outlook is essential.
MAMMO | Mammography Room | 16 | Available 24 Hours | 1 patient; Up to 2 staff assisting |  | Acoustic privacy is required | X-ray room for mammography imaging. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. Cable ducts between mammography unit and control area will be required. 'X-ray in Use' lights required outside each entry door.
MED-14 | Medication Room, 14m2 | 14 | 24 Hours | 1 - 2 staff intermittently |  |  | The Medication Room, 14m² is used for the secure storage of medications, including intravenous fluids, and a small amount of medication-related clean consumables. The room may provide storage for drugs of dependence in accordance with relevant legislation. Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. Secured staff only access to the room is required. The provision and placement of CCTV cameras is dependent on jurisdictional policies. Refer to project specific requirements for the provision of automated medication management systems.
MEET-15 | Meeting Room, 15m2 | 15 | Available 24 Hours | Up to 8 seated |  | Sound attenuation level high, Acoustic privacy is required. | A multipurpose room for staff meetings, education and training activities. Requirement for Hearing Augmentation to be confirmed. Videoconferencing systems and AV equipment are not required in all 15m2 meeting rooms, particularly where most use is for ad hoc meetings with BYO devices. Provision of equipment and services will need to be confirmed based on service requirements. Additional Considerations: Video conferencing systems and AV equipment will be dependent on service requirements and local ICT policies. The display system, sound system, microphone, room and video conferencing control and supporting AV equipment must be carefully considered to provide a cohesive solution for users. Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. To support video conferencing, decor should be light/neutral and free from busy patterns within the camera view for optimal image quality. Room booking panels may be provided to suit service/facility approach to room scheduling. Occupancy will vary, with the total number of people that may be accommodated in the space dependent on furniture layout. Furniture and layout will vary to suit service requirements. Furniture considerations include provision of stackable chairs and folding tables to support reconfiguration of the layout for flexible use of the space. Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. Acoustics to be carefully considered to ensure appropriate sound levels, particularly with video conferencing equipment provided, and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption. Background noise (e.g. from air conditioning) should be minimised. Hard surfaces may be covered to reduce reverberation as required. Where a meeting room is intended to be used with patients and/or family, additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be considered to suit service requirements. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. When used with patients and/or family in mental health settings, an alternative egress door should be provided. Where possible, equipment should be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Ready access to a telephone in an adjacent space may be required to answer pagers. An external outlook is desirable.
MEET-20 | Meeting Room, 20m2 | 20 | Available 24 Hours | Up to 12 seated |  | Sound attenuation level high, Acoustic privacy is required. | A multipurpose room for staff meetings, education and training activities. Requirement for Hearing Augmentation to be confirmed. Additional Considerations: Video conferencing systems and AV equipment will be dependent on service requirements and local ICT policies. The display system, sound system, microphone, room and video conferencing control and supporting AV equipment must be carefully considered to provide a cohesive solution for users. Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. To support video conferencing, decor should be light/neutral and free from busy patterns within the camera view for optimal image quality. Room booking panels may be provided to suit service/facility approach to room scheduling. Occupancy will vary, with the total number of people that may be accommodated in the space dependent on furniture layout. Furniture and layout will vary to suit service requirements. Furniture considerations include provision of stackable chairs and folding tables to support reconfiguration of the layout for flexible use of the space. Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. Acoustics to be carefully considered to ensure appropriate sound levels, particularly with video conferencing equipment provided, and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption. Background noise (e.g. from air conditioning) should be minimised. Hard surfaces may be covered to reduce reverberation as required. Where a meeting room is intended to be used with patients and/or family, additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be considered to suit service requirements. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. When used with patients and/or family in mental health settings, an alternative egress door should be provided. Where possible, equipment should be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Ready access to a telephone in an adjacent space may be required to answer pagers. An external outlook is desirable.
MEET-30 | Meeting Room, 30m2 | 30 | Available 24 Hours | Up to 18 seated |  | Sound attenuation level high, Acoustic privacy is required. | A multipurpose room for staff meetings, education and training activities. Requirement for Hearing Augmentation to be confirmed. Additional Considerations: Video conferencing systems and AV equipment will be dependent on service requirements and local ICT policies. The display system, sound system, microphone, room and video conferencing control and supporting AV equipment must be carefully considered to provide a cohesive solution for users. Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. To support video conferencing, decor should be light/neutral and free from busy patterns within the camera view for optimal image quality. Room booking panels may be provided to suit service/facility approach to room scheduling. Occupancy will vary, with the total number of people that may be accommodated in the space dependent on furniture layout. Furniture and layout will vary to suit service requirements. Furniture considerations include provision of stackable chairs and folding tables to support reconfiguration of the layout for flexible use of the space. Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. Acoustics to be carefully considered to ensure appropriate sound levels, particularly with video conferencing equipment provided, and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption. Background noise (e.g. from air conditioning) should be minimised. Hard surfaces may be covered to reduce reverberation as required. Where a meeting room is intended to be used with patients and/or family, additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be considered to suit service requirements. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. When used with patients and/or family in mental health settings, an alternative egress door should be provided. Where possible, equipment should be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Ready access to a telephone in an adjacent space may be required to answer pagers. An external outlook is desirable.
MEET-55 | Meeting Room, 55m2 | 55 | Available up to 24 Hours | Up to 45 seated |  | Sound attenuation level high, Acoustic privacy is required. | A large multipurpose room for staff meetings, education and training activities. Requirement for Hearing Augmentation to be confirmed. Additional Considerations: An operable wall may be provided to open this room to an adjoining meeting room, increasing capacity for lectures, training activities or events. Connections and coordination between AV and video conferencing equipment in adjoining rooms will need to be considered to support both separate and combined activities. Video conferencing systems and AV equipment will be dependent on service requirements and local ICT policies. The lectern design, display system, sound system, microphone, room and video conferencing control and supporting AV equipment must be carefully considered to provide a cohesive solution for users. To support video conferencing, decor should be light/neutral and free from busy patterns within the camera view for optimal image quality. Room booking panels may be provided to suit service/facility approach to room scheduling. Occupancy will vary, with the total number of people that may be accommodated in the space dependent on furniture layout. Furniture and layout will vary to suit service requirements. Furniture considerations include provision of chairs with integral note tables, stackable chairs and folding tables to support reconfiguration of the layout for flexible use of the space. A storage zone or enclosed storeroom may be provided to hold additional furniture to support alternate layouts. If multiple rooms are provided, furniture storage areas may be shared. Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. Acoustics to be carefully considered to ensure appropriate sound levels, particularly with video conferencing equipment provided, and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption. Background noise (e.g. from air conditioning) should be minimised. Hard surfaces may be covered to reduce reverberation as required. Where a meeting room is intended to be used with patients and/or family, additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be considered to suit service requirements. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. When used with patients and/or family in mental health settings, an alternative egress door should be provided. Where possible, equipment should be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Ready access to a telephone in an adjacent space may be required to answer pagers.
MEET-9 | Meeting Room, 9m2 | 9 | Available 24 Hours | Up to 4 seated |  | Sound attenuation level high, Acoustic privacy is required. | A small multipurpose room for staff interviews, meetings, education and training activities. This room may also function as a 'breakout' room in an open workstation environment. Requirement for Hearing Augmentation to be confirmed. Videoconferencing systems and AV equipment are not required in all 9m2 meeting rooms, particularly where most use is for ad hoc meetings with BYO devices. Provision of equipment and services will need to be confirmed based on service requirements. Additional Considerations: Video conferencing systems and AV equipment will be dependent on service requirements and local ICT policies. The display system, sound system, microphone, room and video conferencing control and supporting AV equipment must be carefully considered to provide a cohesive solution for users. Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. To support video conferencing, decor should be light/neutral and free from busy patterns within the camera view for optimal image quality. Room booking panels may be provided to suit service/facility approach to room scheduling. Acoustics to be carefully considered to ensure appropriate sound levels, particularly with video conferencing equipment provided, and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption. Background noise (e.g. from air conditioning) should be minimised. Hard surfaces may be covered to reduce reverberation as required. For small meeting spaces suitable for use with patients please refer to the Interview Room Standard Component. Ready access to a telephone in an adjacent space may be required to answer pagers. An external outlook is desirable.
MOR-AU | Mortuary - Autopsy Room | 30 | Available 24 Hours | Up to 4 |  |  | The Mortuary - Autopsy Room is for undertaking post mortem examinations. An observation area is to be provided to at least one Autopsy Room within a department. Layout of tables and orientation of observation bay may be adjusted to suit the type of autopsy being performed (e.g. coronial or non-coronial). The Mortuary - Autopsy Room should be located with ready access to Mortuary - Body Holding. Additional Design Considerations: doors to be sealed for odours, post mortem table to have water flushing system. Appropriate Smoke/Heat detection to be considered.
MOR-BH | Mortuary - Body Holding | 22 | 24 Hours | 1 - 2 staff intermittently |  |  | The Mortuary - Body Holding provides refrigerated storage for the temporary holding of bodies with an adjacent area to transfer a body from a trolley into storage. The room can be configured with refrigerated cabinets or as a cool room depending on service requirements. The Mortuary - Body Holding should be located with ready access to the Mortuary - Viewing Room.
MOR-BR | Mortuary - Body Reception | 7 | up to 24 Hours | 1 - 2 staff intermittently |  |  | The Mortuary - Body Reception is an area for receiving bodies from the hospital and checking-in to the holding room/cool room as well as the checking-out of bodies for release to funeral directors, relatives or for transfer to the coroner. This room should be located on a corridor that is in close proximity to both the staff-only mortuary entry and the exit to the funeral director's covered parking area. Entry to this area by authorised personnel only. Handwashing facilities should be located in close proximity.
MOR-VR | Mortuary - Viewing Room | 8 | up to 24 Hours | 4-5 visitors; 1 staff |  | Sound attenuation level high, Acoustic privacy is essential | The Mortuary - Viewing Room is provided for relatives and others to view a body with the support of a social worker. The Mortuary - Viewing Room will be located adjacent to the Mortuary - Waiting. A body may be viewed through a window from within the Mortuary - Waiting, with access provided between the two rooms provided to allow for viewing a body directly.
MOR-W | Mortuary - Waiting | 9 | up to 24 Hours | 4-5 visitors; 1 staff |  | Sound attenuation level high, Acoustic privacy is essential | The Mortuary - Waiting provides an area for relatives and others to await the viewing of a body and to have private discussions with social workers. The area should be comfortable and non-clinical in appearance with furnishings and artwork that are culturally appropriate. Natural light is desirable. The Mortuary - Waiting will be located adjacent to the Mortuary - Viewing Room. A body may be viewed through the window from within the Mortuary - Waiting, with access provided between the two rooms to view a body directly.
MRICR | MRI Control Room | 14 | Available 24 hours | Up to 3 staff |  |  | Room adjacent to the MRI Imaging Room with direct visibility to the patient for remote control of equipment, and review and reporting of procedure images. The MRI Control Room must be located with consideration of four safety exclusion zones leading toward the MRI Room. Additional Design Considerations: Magnetic and radiofrequency shielding as advised by Consultant. Cable ducts from the MRI Imaging and MRI Equipment room will be required. Additional space is required for an AW workstation if included in the Control Room which will require 2 GPOs.
MRIR | MRI Room | 46 | Available 24 hours | 1 patient; Up to 3 staff |  | Acoustic privacy is required | Imaging Room for Magnetic Resonance Imaging (MRI) scanning procedures with an adjacent MRI Equipment Room and Control Room with a direct view of the patient. The Control Room and Equipment room will need to be located in close proximity due to acceptable cable lengths. General anaesthesia may be administered in this room. Additional Design Considerations: The MRI suite design to conform to 4 safety exclusion zones, access control is required. Removable external wall panel to outside wall preferred where possible in order to replace the magnet. Magnetic and radiofrequency shielding are required, specialist consultant advice should be sought. Cable ducts between Control Room and Equipment Room will be required. Imaging equipment to be installed to manufacturer's specifications. Each magnet will have a chiller provided by supplier requiring UPS power, location will be project specific. Structural assessment is required to ensure the floor and access routes to the room will accommodate the weight of the MRI unit. All equipment and fittings in the room to be MRI compatible and constructed of non-ferrous material. Fluorescent luminaires are not permitted in the MRI Room. Consideration should be given to room acoustics - materials that reduce the impact of magnet noise should be included where possible. Temperature and humidity control required.
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | 16.5 | 24 Hours | 1 baby; 4-5 staff; 1-2 carers |  | Sound attenuation level high | A single bay for neonates requiring intensive/ high dependency nursing care and medical treatment, that may include monitoring, invasive or non-invasive ventilation (CPAP), nitric treatment, surgical intervention or cooling therapy. The bay will be in close proximity to a Type A scrub basin, shared between bays. The bay will require access for a mother in a bed and a transport trolley. Facilities for storing parent/carer's belongings is required. An external outlook is desirable from a group of neonatal bays. Lighting will require special consideration and should be dimmable, zoned in parent spaces, and direct overhead lighting should be avoided.
NBLD | Neonatal Bay - Low Dependency Care | 12.5 | 24 Hours | 1 baby; 1-2 staff; 1-2 carers |  | Sound attenuation level high | A single bay for neonates requiring low dependency nursing and medical treatment, that may include oxygen therapy, intravenous therapy and continuous cardiorespiratory monitoring. The bay will have ready access to a Type A Handwashing Basin, shared between bays. Facilities for storing parent/carer's belongings is required and access to baby bathing. An external outlook is desirable from a group of neonatal bays. Lighting will require special consideration and should be dimmable, zoned in parent spaces and direct overhead lighting should be avoided.
OFF-1P-12 | Office - 1 Person, 12m2 | 12 | 8am to 6pm, daily | 1 staff, up to 3 visitors |  | Sound attenuation level medium, Acoustic privacy is required. | An office to accommodate 1 staff member carrying out computer based and/or administrative tasks in privacy. The room size allows for a small meeting table within the room for meetings or interviews with visitors (including staff, patients or family) as required. Additional Considerations: Consider placement of power and data to support flexible arrangement of the layout to suit user requirements. Workstation length to service requirements and local WHS/office accommodation policies. An external outlook is desirable.
OFF-1P-9 | Office - 1 Person, 9m2 | 9 | 8am to 6pm, daily | 1 staff, up to 2 visitors |  | Sound attenuation level medium, Acoustic privacy is required. | An office to accommodate 1 staff member carrying out computer based and/or administrative tasks in privacy. Small meetings, ad hoc discussions or interviews with visitors (including staff, patients or family) may be held in this space, depending on service requirements. Additional Considerations: Consider placement of power and data to support flexible arrangement of the layout to suit user requirements. Workstation length to service requirements and local WHS/office accommodation policies. An external outlook is desirable.
OFF-2P | Office - 2 Person | 12 | 8am to 6pm, daily | 2 staff, up to 2 visitors |  | Sound attenuation level medium, Acoustic privacy is required. | An office to accommodate 2 staff members carrying out computer based and/or administrative tasks in privacy. Small meetings, ad hoc discussions or interviews with visitors (including staff, patients or family) may be held in this space, depending on service requirements. Additional Considerations: Workstation length to service requirements and local WHS/office accommodation policies. An external outlook is desirable.
OFF-CLN | Office - Clinical Workroom | 15 | Available 24 hours | 4 workstations |  | Sound attenuation level high, Acoustic privacy is required. | An Office - Clinical Workroom, typically adjoining or in close proximity to a Staff Station, is for staff to write up notes, review patient records and digital images, hold confidential discussions, store records and conduct handovers. One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Staff Station. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication. Additional Design Considerations: Location of power and data outlets (above or below the bench) is to meet local operational/WHS requirements. Cable management solutions to be considered to meet infection control and cleaning requirements. A desktop printer may be provided. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. Provision of height adjustable workstations may be considered depending on local policies and staff accessibility requirements.
OFF-WI-5 | Office - Write-up, 5m2 | 5 | 24 Hours | 2 staff members |  |  | The Write-up Bay provides a write-up bench for use by members of the patient care team. In this space the User may review and write-up patient records, enter patient data on computer and make telephone calls. If located within the Operating Unit it may also include an optional area for porters to wait until paged or called by staff. The Write-up space must not impede the corridor.
OFF-WS | Office - Workstation | 4.5 | 8am to 6pm, daily | 1 staff/visitor |  |  | A workstation within an open plan arrangement. Multiple staff may utilise this space at different times to carry out computer based and/or administrative tasks. Additional Considerations: Depending on overall layout, services may be wall mounted or workstations with soft-wired cable trays may be connected via an umbilical to the floor or ceiling. Workstation length to service requirements and local WHS/office accommodation policies. A modesty panel or extended acoustic panel may be required depending on layout. Shared document storage may be allocated separately to the workstation. Small meeting tables for informal discussions may be provided between a number of workstations in larger open plan areas. Where devices are to be brought with the user a dock and monitor(s) may be provided in lieu of a computer. Adequate coverage for Wireless Access Point (WAP) to be provided. An external outlook is desirable.
OPG | OPG Room | 12 | Available 24 Hours | 1 patient; 1 staff |  | Acoustic privacy is required | OPG is a room for undertaking orthopantomogram procedures which involve panoramic x-ray of the jaw area in dental examinations. The OPG unit may optionally be located within a Dental/ Oral Health unit or Imaging Unit. The OPG Room is designed to accommodate OPG, Ceph and Cone Beam CT imaging as required. An additional computer will be required if cone beam CT is included. The OPG imaging unit will require independent communications cabling to the related workstation. Room design will need to be adjusted if patients on beds need to be imaged. Additional Design Requirements: Radiation shielding to walls as advised by Radiation Consultant. 'X-ray in Use' warning lights will be required.
OVBR | Overnight Stay - Bedroom | 10 | Available 24 Hours | 1 staff/visitor |  | Sound attenuation level high, Acoustic privacy is required. | A 1 bed room with an adjoining ensuite for staff, parents or carers needing to remain on close call overnight. The room shall be lockable. Additional Design Considerations: An external outlook is required. Overnight stay bedroom and ensuite layouts may be adjusted to provide accessible facilities i.e. as required if a standalone suite is provided or in a portion of rooms if multiple overnight stay suites are provided.
OVES | Overnight Stay - Ensuite | 5 | Available 24 Hours | 1 staff/visitor |  | Acoustic privacy is required | An ensuite with shower, toilet and basin adjoining the overnight stay bedroom for staff, carers or parents needing to remain on close call overnight. Additional Design Considerations: Overnight stay bedroom and ensuite layouts may be adjusted to provide accessible facilities e.g. as required if a standalone suite is provided or in a portion of rooms if multiple overnight stay suites are provided.
PAR | Parenting Room | 9 | Available 24 Hours | Up to 2 |  | Sound attenuation level high, Acoustic privacy is required. | The Parenting Room is provided as a private space for parents to feed and change babies and will provide access for prams. The Parenting Room will be located to have ready access to a public amenities and waiting areas. Additional Design Considerations: Provision of a fridge may be considered if servicing a staff area; this will be dependent on operational policies. Custom joinery for baby changing facilities may be considered, dependent on operational policies and project requirements.
PBAT | Patient Bay, Emergency - Ambulance Triage | 6.5 | 24 Hours | 1 patient; 1-2 staff intermittently |  |  | A Patient Bed Bay used for assessment of patients on arrival by ambulance to the emergency department Ambulance Triage. The patient bay may be one of a number within the Ambulance Triage area. The patient bay constitutes a component of the Ambulance Triage area; it requires direct access and observation from write up facilities for ambulance, triage and administrative staff. It will also require direct access to a staff handwashing basin. Negative pressure requirements are for general directional airflow only. Air conditioning to be non recirculating.
PBIC | Patient Bay - Intensive Care | 24.5 | 24 Hours | 1 patient, 1 visitor, Up to 6-8 staff |  | Acoustic attenuation is required | An acuity adaptable, open bed bay for a patient requiring intensive medical treatment, nursing care and monitoring for potentially life threatening conditions. Visual access to a main Staff Station or Sub Staff Station is required. Screen curtains are required for patient privacy. Natural light is required to patient beds. Dialysis facilities may be required, assumed to be provided via mobile reverse osmosis water dialysis units. Mobile imaging may be required, shielding requirements must be confirmed with Radiation Consultant.
PBSC | Patient Bay - Specimen Collection | 9 | 8am to 6pm, daily | 1 patient, 1 staff |  |  | A Patient Bay used for the collection of specimens to be transferred to a laboratory for testing. Additional Considerations: Ready access to a handwashing basin is required. Ready access may be required to a pneumatic tube bay that is in a staff supervised area. Recliner must be able to lay flat to support the patient in the event of an adverse reaction (e.g. fainting). A desk may be provided in lieu of Workstation on Wheels depending on operational model. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. A risk assessment should be undertaken to inform staff safety requirements with adjoining cubicles which may require adjustments to the design and/or operational strategies, such as the use of mobile duress systems. Refer to the Pathology HPU for paediatric requirements.
PBTR-A | Patient Bay, Emergency - Acute Treatment | 12 | 24 Hours | 1 patient; 1-2 staff |  |  | The Patient Bay, Emergency - Acute Treatment may be used for assessment and treatment of patients with acute conditions and will be located within the Emergency Unit. The bay may have partition side nib walls. The Patient Bay will have close access to a staff handwashing basin and, wherever possible, clear line of sight to a staff station.
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | 15 | 24 Hours | 1 patient; 1-2 staff |  |  | The Patient Bay, Emergency - Acute Treatment Special is a multipurpose enclosed treatment space that acts as a Class S isolation bay and an acute treatment bay that is accessible for wheelchair users. A patient toilet must be provided in close proximity. It may also be used for paediatric patients in a mixed adult/paediatric environment. An Ensuite is required for Class S and/or paediatric use. With an Ensuite, Anteroom, negative pressure ventilation and other adaptions, it may also be used as a Class N Isolation enclosed treatment space. Glazing is recommended to side walls, if space planning allows.
PBTR-FT | Patient Bay, Emergency - Fast Track | 6.5 | 24 Hours | 1 patient; 1-2 staff intermittently |  |  | A short stay patient bay used for assessment and treatment of patients with non acute conditions. The patient bay will have close access to a staff handwashing basin and patient toilet.
PBTR-MD | Patient Bay - Medical Day Treatment | 9 | 8am to 6pm, daily | 1 patient: 1-2 staff, 1 visitor |  |  | The Patient Bay - Medical Day Treatment may be used for assessment and treatment of non-admitted patients receiving scheduled treatment in either a bed or recliner (e.g. for infusions such as antibiotics and chemotherapy). A staff handwashing basin will be provided for each 4 bays and the Patient Bay will have, wherever possible, clear line of sight to a staff station and close access to a patient toilet. Access to natural light and views is required. Medical Gases may be provided individually to each bay or shared between two bays depending on service requirements.
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | 10 | 24 Hours | 1 patient; 1-2 staff intermittently |  |  | A Patient Bed Bay used for assessment and treatment of patients with non acute conditions requiring a short episode of care of less than 24 hours. The Patient Bay will have close access to a staff handwashing basin and patient toilet.
PBTR-R | Patient Bay, Emergency - Resuscitation | 25 | 24 Hours | 1 patient; 4 - 5 staff |  |  | A Patient Bed Bay for assessment, resuscitation and treatment of patients with critical conditions, located within the Emergency Unit. The Bay may have partition side walls and a bench used for preparation and write-up. Resuscitation and diagnostic equipment should be located in close proximity which may include ventilator, cardiac pacemaking equipment, patient sliders and mobile X-ray machine. Accurate control of ambient temperature is required. Lead shielding may be required depending on use of X-ray equipment; to be assessed by Radiation Consultant.
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | 9 | 7am to 9pm, daily | 1 patient, 1 visitor, 1-2 staff |  |  | The Patient Bay - Renal Dialysis is for patients receiving haemodialysis therapy. Treatments for each patient may take from 3 to 6 hours, occurring up to 3 days per week. A staff handwashing basin will be provided for each 4 bays and the Patient Bay will have, wherever possible, clear line of sight to a staff station. Access to natural light and views is required. Furniture and furnishings should provide a high level of patient comfort and amenity.
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | 9 | 7am to 9pm, daily | 1 patient, 1 visitor, 1-2 staff |  |  | The Patient Bay - Renal Dialysis is for patients receiving haemodialysis therapy. Treatments for each patient may take from 3 to 6 hours, occurring up to 3 days per week. A staff handwashing basin will be provided for each 4 bays and the Patient Bay will have, wherever possible, clear line of sight to a staff station. Access to natural light and views is required. Furniture and furnishings should provide a high level of patient comfort and amenity.
PET-CT | PET-CT Imaging Room | 50 | Available 24 Hours | 1 patient; up to 3 staff assisting |  | Acoustic privacy is required | The PET-CT Imaging Room provides the area and facilities for Positron Emission Tomography-Computed Tomography (PET/CT) scanning procedures with a Control Room and Equipment Room (as required) located nearby. It is not essential that the control is directly adjacent to the Imaging Room where patients are monitored via observation cameras, however ready access is required to attend to patient needs. If the Control Room is adjacent an observation window may be provided and shielding requirements will need to be confirmed. Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access and support structure as required. The PET-CT Imaging Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. Additional Considerations: Configuration of medical gases is to be confirmed to meet clinical requirements such as the provision of anaesthetic services. Dimmable lights are recommended and are to be placed to avoid glare to patients. Back lit ceiling artwork may be installed for patient comfort. 'X-ray in Use' lights are required outside each entry door. Laser marker system for procedure planning may be required subject to model of care and equipment selected. Structural assessment is required to ensure the floor will be rigid with no vibration and will accommodate the weight of the PET-CT unit. Room temperature and humidity control is required. Temperature requirements for equipment are to be confirmed by the vendor, including requirement for circulated cooling water. The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the PET-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. An optional laser system for patient positioning and procedure planning has been indicated and may be provided subject to service requirements. A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be considered depending on clinical/service requirements (e.g. for radiation therapy planning). The provision of these technologies is to be confirmed by the project and may have additional requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. Consideration needs to be given to the clearances of equipment and replacement part delivery routes.
PHA-CO | Pharmacy - Counter | 9 | 8am to 8pm, daily | 1-2 staff |  | Sound attenuation level - Medium; acoustic privacy required. | The Pharmacy &#8211; Counter provides a reception point for the Pharmacy Unit for patients and staff to drop off prescriptions to be filled and collect dispensed prescriptions. The Counter is to have good visibility of the waiting area and visitors as they approach. Additional Design Requirements: Information on prescribed medications will be provided to patients at the counter and a degree of privacy is required for these discussions. Interview rooms may be located nearby to provide more private information or counselling. Cash handling and EFTPOS facilities may be required in this space depending on operational models and the proximity of the Unit to the central hospital cashier. Security glazing will be required. The design must support clear communication between pharmacy staff and patients with communication slots. A hearing augmentation system may be considered. Small items will also need to be passed through and forms may need to be signed &#8211; the design of the glazing needs to support this function. The ability to lock down the Unit, e.g. in evenings when the pharmacy is closed, is required. This may be achieved by lockable doors from public corridors to the waiting area, however lockable shutters to the counter may be considered.
PHA-DB | Pharmacy - Distribution Workstation | 6 | 8am to 8pm, daily | 1 staff |  |  | The Distribution Workstation provides workspace to sort and process dispensed medications to be distributed from the Pharmacy to clinical units (e.g. imprest medications) and may be used to prepare specialised packs (e.g. resuscitation trolley supplies). Additional Considerations: Ready access to bulk store and refrigerated storage is required from this area. Direct access to a dispatch/collection area is required for holding items prior to delivery. Printer and telephone facilities to be shared between multiple workstations. A Multifunction device is to be in close proximity to the distribution area. Ensure adequate lighting over workspace.
PHA-DS | Pharmacy - Dispensing Workstation | 4 | 8am to 8pm, daily | 1 staff |  |  | The Dispensing Workstation provides workspace to prepare, assemble and label patient medications for dispensing to inpatients and outpatients. The workstations can be configured to provide dispensing/assembly stations and a checking station as required. Dispensing workstations should be arranged to support effective workflows, reduce travel time and avoid error. These stations should be arranged such that extended reaches are avoided. Where dispensing workstations are arranged adjacent to each other, corridors in between them should be wide enough to provide unobstructed movement for staff and trolleys. Additional Considerations: Ready access to the bulk store and refrigerated storage is required. Printer and telephone facilities to be shared between multiple workstations. A Multifunction device is to be in close proximity to the dispensing area. Ensure adequate lighting over workspace - task lighting may be required.
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | 12 | 8am to 8pm, daily | Up to 2 Staff |  |  | The Preparation Room provides a dedicated area for the extemporaneous preparation and compounding of non-aseptically prepared products and cleaning of equipment as required. The Preparation Room should be located in close proximity to the dispensing area.
PHA-RE | Pharmacy - Returns Workstation | 6 | 8am to 8pm, daily | 1 staff |  |  | The Returns Workstation provides workspace to sort and process medication returns from within the hospital that are to be returned to stock or sent for disposal. Storage is required to accommodate the returns before they are processed. Additional Considerations: Ready access to refrigerated storage and disposal room is required from this area. Printer and telephone facilities to be shared between multiple workstations. A Multifunction device is to be in close proximity to the returns area. Ensure adequate lighting over workspace.
PLAY | Play Area - Paediatric | 10 | Available 24 Hours | Up to 4 |  | Acoustics: sound attenuation level - high. | An area, typically associated with a waiting area, where children may play while waiting with parents. The Play Area should allow access for prams and be located in close proximity to public amenities, including baby change facilities. The Play Area should be designed to minimise noise transfer to other areas. Additional Considerations: Provision of age appropriate furnishing, artwork and play equipment (if provided) to be based on service and population. Furniture that is easily wiped clean is recommended. Furniture suitable for adults is typically provided within the space to support supervision of children but may be provided in the adjacent waiting area if layout allows for adequate visibility. Provision of interactive board/projector technologies and associated services may be considered depending on operational policies and ICT support.
PLNT-WT | Plant - Water Treatment | 18 | 24 Hours | 1 - 2 staff |  | High level sound isolation | The Plant - Water Treatment is a lockable room for water treatment systems, including particle filters, water softeners, carbon filters and reverse osmosis (RO) water plant/systems, for the provision of safe water for patients receiving haemodialysis therapy. The Water Treatment Plant Room should be located in close proximity to the Renal Dialysis Unit to permit short tubing runs to each Treatment Bay, and permit staff to monitor and service the water treatment systems. Refer to manufacturer's specifications for details of RO water treatment plant equipment. In particular, this equipment will incorporate a heat disinfection function, and water saving features. The final components of the system will be determined by the quality of feed water and the ability of the overall system to produce and maintain appropriate water quality. Water treatment requirements to be confirmed by a dialysis water treatment specialist. Special Design Requirements: High level sound isolation is required to ensure noise generated from this room does not invade treatment spaces. Structural engineer's assessment must be sought for floor load bearing capacity with respect to water treatment and pre-treatment plant equipment. Ventilation, exhaust and/or air-conditioning must be designed to accommodate the heat loads of the specified equipment. Light is to be minimised; there are to be no windows provided. Service access will be required around the perimeter of plant equipment, clearances will be determined by manufacturer's specifications. A second door may be provided for separate deliveries and maintenance access if located in the patient treatment area. Pipework and components installed after the water inlet in this room shall not contain brass or copper. Options for cooling of high temperature (circa 90°C) waste water discharged from RO plant is to be considered. Where chilled water is not available, a chiller may be required outside the plant room. The maximum temperature of the feed water to be assessed to allow determination of any requirement for a heat exchanger or chiller design as determined by expert. The intent of this is ensure the temperature at the dialysis point for patient care is between 30-37°C. Redundancy within the pre-treatment and treatment devices/filters should be considered based on the hospitals service criticality level, the feed water quality or risk around quality, and the hospital location where supply of replacement equipment is difficult.
PLST | Plaster Room | 18 | 24 Hours | 1 patient; 2 -4 staff |  | Sound attenuation level - high; acoustic privacy is required | The Plaster Room allows for the application of plaster or other splints and for the closed reduction of displaced fractures or dislocations under sedative or regional anaesthesia. Typically provided as a dedicated room for high volume services, otherwise, a generic Treatment Room may be used with the inclusion of a plaster trap and other specific plastering equipment. The cast saw shall incorporate an integrated dust extraction system or the room shall have an independent dust extraction system suitably located to capture the dust at source. A room exhaust shall also be included to prevent dust from entering adjacent spaces. The plaster trap shall be easily accessible for cleaning and maintenance.
PROC | Procedure Room | 20 | 24 Hours | 1 patient; 2-4 staff |  | Sound attenuation level - High. Acoustic privacy is required. | The Procedure Room provides a controlled environment and facilities for carrying out procedures that do not require the full facilities of the Operating Suite. This may include suturing of wounds, complex dressings, lumbar puncture, catheterisations, administration of local anaesthesia and use of medical gases in connection with the procedures being performed. General anaesthesia will not be administered in this room. Additional Design Considerations: Lead shielding may be required depending on use of mobile imaging equipment. Treatment of bariatric patients including mobile, bariatric lifter access. The ceiling height has been nominally shown at 3000mm, however 2700mm is also acceptable and the height is to be determined based on ceiling mounted equipment and operational requirements.
PT-HOLD-A | Patient Bay - Holding, Chair | 6.5 | up to 24 Hours | 1 patient, 1 visitor, 1-2 staff intermittently |  |  | A Patient Bay - Holding provides facilities for patient holding and preparation prior to examination, diagnostic imaging, treatment, procedures or surgery. A handwashing basin will be provided close by to be shared between multiple bays. Staff observation is required and, where possible, a clear line of sight from a staff station is to be provided. Close access to a patient toilet is required. Additional Considerations: The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring equipment. The requirement for fixed wall mounted patient monitoring will be dependent on service requirements. A patient monitor may be located on the left or right side of bedhead depending on monitor functionality and staff workflows. Appropriate wall supports are required for mounting the bracket where a monitor is provided. Where patient monitoring is provided, criticality of monitoring is to be assessed. Provision of emergency/standby power or UPS is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. Facilities to accommodate bariatric patients within a select number of bays, including accommodating bariatric recliners, is to be considered to ensure sufficient amenity is provided. Provision will be dependent on service and patient cohort requirements. Depending on service requirements, enclosed holding bays may be provided. Where a Patient Bay is to be enclosed, additional area is required to accommodate a dedicated handwashing basin and circulation at the door. Observation windows may be required and the extent of glazing to be provided is to suit requirements for staff supervision. PPE may be consolidated between multiple bays. Provision of PPE and placement throughout the overall department will be dependent on local infection control policies. A mobile sharps bin will be shared between multiple bays as required. Where use of sharps is frequent, a wall mounted bin sharps bin may be considered. Electronic Medical Record (EMR) management may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays. Ensure circulation space is sufficient for bedside and bed end data entry. Parking for WOWs and facilities for battery charging are required to support this model of care. Alternative configurations, such as wall mounted monitors in bays, may be considered depending on local ICT policies. Patient entertainment systems may be considered depending on anticipated length of stay within the holding bay and patient cohort requirements (e.g. paediatrics). Solutions may include individual systems provided to each bay (with integration to patient handset for audio and content control), a central display screen visible from multiple bays, or portable solutions, such as tablets, brought to patients as needed. Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. Depending on anticipated length of stay and pre-procedure requirements, local control of lighting within the bay may be provided to allow patients to dim/adjust lighting levels to increase comfort. Access to natural light is required and an external outlook is recommended.
PT-HOLD-B | Patient Bay - Holding, Bed | 9 | up to 24 Hours | 1 patient, 1 visitor, 1-2 staff intermittently |  |  | A Patient Bay - Holding provides facilities for patient holding and preparation prior to examination, diagnostic imaging, treatment, procedures or surgery. A handwashing basin will be provided close by to be shared between multiple bays. Staff observation is required and, where possible, a clear line of sight from a staff station is to be provided. Close access to a patient toilet is required. Additional Considerations: The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring equipment. The requirement for fixed wall mounted patient monitoring will be dependent on service requirements. A patient monitor may be located on the left or right side of bedhead depending on monitor functionality and staff workflows. Appropriate wall supports are required for mounting the bracket where a monitor is provided. Where patient monitoring is provided, criticality of monitoring is to be assessed. Provision of emergency/standby power or UPS is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. Facilities to accommodate bariatric patients within a select number of bays, including accommodating bariatric beds, is to be considered to ensure sufficient amenity is provided. Provision will be dependent on service and patient cohort requirements. Patient transfer aids such as mobile hoists, patient slides and hover mats are to be considered for assisted patient transfers to and from beds in holding bays. A ceiling mounted hoist may also be considered for patient transfers. Selection of transfer aids will be dependent on service and patient cohort requirements as well as WHS risk assessment. Appropriate ceiling support is required for the provision of a ceiling mounted hoist. Depending on service requirements, enclosed holding bays may be provided. Where a Patient Bay is to be enclosed, additional area is required to accommodate a dedicated handwashing basin and circulation at the door. Observation windows may be required and the extent of glazing to be provided is to suit requirements for staff supervision. PPE may be consolidated between multiple bays. Provision of PPE and placement throughout the overall department will be dependent on local infection control policies. A mobile sharps bin will be shared between multiple bays as required. Where use of sharps is frequent, a wall mounted bin sharps bin may be considered. Electronic Medical Record (EMR) management may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays. Ensure circulation space is sufficient for bedside and bed end data entry. Parking for WOWs and facilities for battery charging are required to support this model of care. Alternative configurations, such as wall mounted monitors in bays, may be considered depending on local ICT policies. Patient entertainment systems may be considered depending on anticipated length of stay within the holding bay and patient cohort requirements (e.g. paediatrics). Solutions may include individual systems provided to each bay (with integration to patient handset for audio and content control), a central display screen visible from multiple bays, or portable solutions, such as tablets, brought to patients as needed. Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. Depending on anticipated length of stay and pre-procedure requirements, local control of lighting within the bay may be provided to allow patients to dim/adjust lighting level to increase comfort. Access to natural light is required and an external outlook is recommended.
PT-RS1 | Patient Bay - Recovery, Stage 1 | 9 | up to 24 Hours | 1 patient; 1-2 staff |  |  | A Patient Bay - Recovery, Stage 1 provides facilities for the recovery of patients from anaesthetic post procedure, and is located within the Operating Unit or Day Procedures Unit. A handwashing basin will be provided close by to be shared between up to 4 Patient Bays. Staff observation is required and a clear line of sight from a staff station should be provided. Additional Considerations: The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring and diagnostic equipment. A patient monitor may be located on the left or right side of bedhead depending on monitor functionality and staff workflows. Appropriate wall supports are required for mounting the bracket where a monitor is provided. Provision of emergency/standby power or UPS for patient monitoring is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. Facilities to accommodate bariatric patients within a select number of bays, including accommodating bariatric beds, is to be considered to ensure sufficient amenity is provided. Provision will be dependent on service and patient cohort requirements. Patient transfer aids such as mobile hoists, patient slides and hover mats are to be considered for assisted patient transfers to and from beds in holding bays. A ceiling mounted hoist may also be considered for patient transfers. Selection of transfer aids will be dependent on service and patient cohort requirements as well as WHS risk assessment. Appropriate ceiling support is required for the provision of a ceiling mounted hoist. Depending on service requirements, enclosed recovery bays may be provided. Where a Patient Bay is to be enclosed, additional area is required to accommodate a dedicated handwashing basin and circulation at the door. Observation windows may be required and the extent of glazing to be provided is to suit requirements for staff supervision. Additional area may be required in a percentage of Recovery Stage 1 bays to suit various services requirements, e.g. to support maternity patients or paediatric patients, for accommodating bariatric patients, for care of complex patients, or for extended recovery models. The percentage of bays that may be provided with increased area will be dependent on the anticipated case mix. Electronic Medical Record (EMR) management may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays. Ensure circulation space is sufficient for bedside and bed end data entry. Parking for WOWs and facilities for battery charging required to support this model of data entry. Alternative configurations, such as wall mounted monitors in bays, may be considered depending on local ICT policies. Access to natural light is required. Where windows are provided, integral blinds are required for infection prevention and control.
PTRY | Pantry | 9 | Up to 24 Hours | 1-2 staff intermittently |  |  | The Pantry is for staff preparing and/or heating refreshments and snacks for patients, washing utensils and crockery or temporarily storing dirty items for collection, storing food and drink and disposing of food waste. This room may be shared between multiple units depending on service requirements. Additional Considerations: If food re-thermalisation trolleys are to be located in this room during meal times an additional 2m2 per trolley will be required as well as appropriate power outlets. Refer to Bay - Meal Trolley (BMT) for requirements. Local food preparation regulations and infection control policies may require a Type B hand wash basin, separate to the sink, to be included in the room or may allow for it to be located nearby. Fridge dimensions will vary depending on selection and service requirements; clear area provided for the fridge is to allow for adequate ventilation and full opening of door. Where double door fridges are provided, additional area will be required. If an instantaneous boiling water tap/unit is provided, access should be restricted to the water unit e.g. within a cupboard. If system is located within a joinery unit, ensure appropriate ventilation is provided. Provision and type of ice machine will be dependent on service requirements and local infection prevention and control policies. Where ice machine is provided, ensure adequate support to bench for weight of appliance. Where tea service is provided the height of the hot water dispenser is to be considered to ensure large kettles can be filled easily. Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling streams indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal and anticipated traffic, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. Storage of nutritional supplements may require a lockable cupboard and will be dependent on service requirements. Temperature of fridge may need to be monitored. A data outlet, or alternative connection to suit project/equipment requirements, may be required for connection the Building Management System (BMS) depending on service requirements. Controlled, staff-only access may be required if this room is provided in a public or patient care area.
REC-E | Reception, Emergency | 20 | 24 Hours | Up to 3 staff members |  | Sound attenuation required, patient to staff communication acoustic to be considered | A Reception area for the Emergency Unit where patients/ visitors can be received, located adjacent to waiting areas. The room assumes one triage reception point and two administrative reception points, however triage can also be provided as a separate space. One administrative point is DDA compatible and can also be used for accessible triage reception. The number of triage and reception points should be adapted to meet staffing requirements. Additional Design Requirements: security glazing is optional, and subject to jurisdictional requirements; if included consideration of communication and pass-through of samples is required. Several possible door entries are shown: as a minimum a second egress is required for staff. Negative pressure requirement indicates general directional airflow only. Air conditioning to be non recirculating.
RECP-10 | Reception, 10m2 | 10 | 8am to 6pm, daily, dependent on function of unit | 1 staff |  | Sound attenuation level - Medium; acoustic privacy required. | A Reception area where visitors to a Unit can be received and directed to their destination or to a Waiting Area. The Reception may also act as an administrative base as well as controlling access to the Unit. Additional Considerations: Dependent on location, security glazing or shutters may be required. A recessed area for front access by wheelchair users is typically required. Depending on check in requirements at Reception, a set down area for visual access only may be sufficient. Adjustable height workstations may be provided in line with WHS policies and access for disabled staff working within the Reception area is to be considered. CCTV monitor, intercom and door release buttons linked to entry points may be required for access control depending on location. A desktop printer and labels printer may be provided as required. Printing, scanning and photocopying facilities may be consolidated with ready access from Reception to suit service requirements. Swipe card access to reception may be provided to suit security requirements.
RECP-15 | Reception, 15m2 | 15 | 8am to 6pm, daily, dependent on function of unit | 2 staff |  | Sound attenuation level - Medium; acoustic privacy required. | A Reception area where visitors to a Unit can be received and directed to their destination or to a Waiting Area. The Reception may also act as an administrative base as well as controlling access to the Unit. Additional Considerations: Dependent on location, security glazing or shutters may be required. A recessed area for front access by wheelchair users is typically required. Depending on check in requirements at Reception, a set down area for visual access only may be sufficient. Adjustable height workstations may be provided in line with WHS policies and access for disabled staff working within the Reception area is to be considered. CCTV monitor, intercom and door release buttons linked to entry points may be required for access control depending on location. A desktop printer and labels printer may be provided as required. Printing, scanning and photocopying facilities may be consolidated with ready access from Reception to suit service requirements. Swipe card access to reception may be provided to suit security requirements.
RECP-20 | Reception, 20m2 | 20 | 8am to 6pm, daily, dependent on function of unit | 3 staff |  | Sound attenuation level - Medium; acoustic privacy required. | A Reception area where visitors to a Unit can be received and directed to their destination or to a Waiting Area. The Reception may also act as an administrative base as well as controlling access to the Unit. Additional Considerations: Dependent on location, security glazing or shutters may be required. A recessed area for front access by wheelchair users is typically required. Depending on check in requirements at Reception, a set down area for visual access only may be sufficient. Adjustable height workstations may be provided in line with WHS policies and access for disabled staff working within the Reception area is to be considered. CCTV monitor, intercom and door release buttons linked to entry points may be required for access control depending on location. A desktop printer and labels printer may be provided as required. Printing, scanning and photocopying facilities may be consolidated with ready access from Reception to suit service requirements. Swipe card access to reception may be provided to suit security requirements.
REPR | Reporting Room | 12 | Available 24 Hours | Up to 4 (6 to 8 for limited periods for image reviews by team) |  | Sound attenuation level high, acoustic privacy is required. | Room within a Clinical or Diagnostic Unit for reviewing and reporting of computerised patient imaging/PACS images. Film images may also be viewed from time to time.
REPW | Reporting Workstation | 6 | Available 24 Hours | 1 staff member, 1 supervisor on occasion |  | Acoustic privacy is required | Single workstation within a Clinical or Diagnostic unit for reviewing and reporting of computerised patient imaging/ PACS images. Intended for use as a component in spaces with more than one workstation.
SECL | Seclusion Room | 14 | 24 Hours | 1 patient; 1-2 staff intermittently |  | Sound attenuation level very high, acoustic privacy is required. | A Seclusion Room provides for the sole confinement of a distressed or agitated person requiring separation for short periods at any hour of the day or night on an involuntary basis. An external outlook is required. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a minimum thickness of 14.28mm, or equivalent approved. Jurisdictional requirements may require an increase in the thickness of the glass for Seclusion Rooms. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. General lighting must be dimmable and/or have controlled switching to create a low stimulus environment. An internal observation window is required so observation is optimised and blind spots eliminated. Designers must carefully consider the design of the door, to ensure it has sufficient strength and robustness but still allows for speech to be heard through it. All finishes to be flush and not provide ligature points. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.
SECR | Security Observation Room | 12 | 24 Hours | Up to 2 staff |  | Sound attenuation level medium; acoustic privacy is required. | The Security Observation Room is a lockable room for security personnel to observe nearby areas and monitor surveillance equipment. This room may be provided as a satellite room separate to the main Security Department (e.g., in the Emergency Unit) or as a reception area for the Security Department. Security staff in will be responsible maintaining order and de-escalating developing situations where aggression may become an issue. Staff identification and access control cards may be produced by security staff in this room. Security staff may also receive, receipt and record lost items of value, contraband and weapons, including reporting to police services in line with jurisdictional policies and procedures. Security Observation Rooms are typically located close to the main entrance, after hours entrances and/or overseeing the emergency unit waiting area. Additional Considerations: ICT requirements, including computer, camera and printer may be required for creating identification and access control cards for staff as well as passes for contractors and visitors, depending on facility requirements. Requirements for photography for identification card are to be confirmed based operational policies. Where provided, a camera will need to be located near a computer with unobstructed view through an observation window towards a blank wall in an area with adequate lighting. Lockdown buttons to entry ways may be provided within the room dependent on service requirements and will be determined based on overall security strategy for the facility. The provision and configuration of a weapons safe within the room will be depending on operational policies and jurisdictional requirements. Clear signage indicating the function of the room is required.
SHAC | Shower - Accessible | 4 | 24 Hours | 1 patient; 1-2 staff assisting as required |  | Sound attenuation level high, Acoustic privacy is required. | The Shower - Accessible provides a shower for use by patients, visitors or staff with disabilities (with or without assistance). If the Shower - Accessible is located in a patient care area the nurse call system should be included and emergency release door hardware should be installed to allow staff access in an emergency. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system. The entrance to the room should be flush with the adjoining floor for access in commode chairs/wheelchairs. Facilities for hand hygiene and PPE to be available nearby if this room is for patient use. The room shall comply with Australian Standard 1428.1. Signage with braille tactile nominating 'Accessible Shower' required
SHPT | Shower - Patient | 4 | 24 Hours | 1 patient; 1-2 staff assisting as required |  | Sound attenuation level high, Acoustic privacy is required. | The Shower - Patient provides a shower and basin for use by patients (with or without assistance). Emergency release door hardware should be installed to allow staff access in an emergency. The entrance to the room should be flush with the adjoining floor for access in commode chairs/wheelchairs. Signage with braille tactile nominating 'Patient Shower' required
SHST | Shower - Staff | 3 | Available 24 Hours | 1 staff |  | Sound attenuation level high, Acoustic privacy is required. | A shower and changing area for use by staff. Additional Design Considerations: Secure, staff-only access to change rooms may be required if located in a public or patient care area. The Staff Shower may be gender specific or unisex.
SPECT-CT | SPECT-CT Imaging Room | 50 | Available 24 Hours | 1 patient; up to 3 staff assisting |  | Acoustic privacy is required | The SPECT-CT Imaging Room provides the area and facilities for Single Photon Emission Computed Tomography (SPECT) scanning procedures with an adjacent Control Room and Equipment Room. The SPECT-CT Imaging Room will be located with ready access to patient dosing areas. Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. The SPECT-CT Imaging Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints. Where shielding significantly increases the weight of the doors, automatic doors may be considered. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. Additional Considerations: Configuration of medical gases is to be confirmed to meet clinical requirements such as the provision of anaesthetic services. Dimmable lights are recommended and are to be placed to avoid glare to patients. Back lit ceiling artwork may be installed for patient comfort. 'X-ray in Use' lights are required outside each entry door. Room temperature and humidity control is required. Temperature requirements for equipment are to be confirmed by the vendor, including requirement for circulated cooling water. The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the SPECT-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Some models of SPECT/CT require three phase power to be supplied. Structural assessment is required to ensure the floor will be rigid with no vibration and will accommodate the weight of the SPECT-CT unit. Consideration needs to be given to the clearances of equipment and replacement part delivery routes. Where a service is may be performing minor interventional procedures, a Type A handwashing basin will be required instead of Type B.
SPECT-CTCR | SPECT-CT Control Room | 14 | Available 24 hours | Up to 3 staff |  | Acoustic privacy required | The SPECT-CT Control room is located adjacent to the SPECT-CT Imaging Room, with direct visibility to the patient, for remote control of equipment with audio and visual contact with the patient via cameras, speakers and microphones. Each Imaging Room requires a Control Room. Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. Additional Considerations: The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the SPECT-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Some models of SPECT/CT require three phase power to be supplied. Cable management and the potential for computers to be consolidated into a rack (either within the room or in a dedicated, collocated air conditioned room/cupboard) to be determined at project level. Provision of a height adjustable workstation may be considered depending on local policies and staff accessibility requirements.
SRM-15 | Staff Room, 15m2 | 15 | Available 24 Hours | Up to 8 staff, intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Staff Room is a shared facility for staff to use for respite, rest and relaxation during meal breaks, especially where it is difficult for staff to use common facilities particularly at night or due to distance. The room may also be used for small meetings or tutorials and for the storage of staff resources or library materials. Facilities for food and beverage preparation and storage should be provided. Additional Design Considerations: An external outlook is desirable. Staff only access may be required if this room is provided in a public or patient care area. A dishwasher may be provided depending on local operational polices. A side approach to the sink for wheelchair access has been shown; front access may be required depending on local/jurisdictional policies and staff requirements. The use of thermal heat detectors for fire detection is recommended. A portable fire extinguisher and fire blanket must be provided.
SRM-35 | Staff Room, 35m2 | 35 | Available 24 Hours | Up to 24 staff, intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Staff Room is a shared facility for staff to use for respite, rest and relaxation during meal breaks, especially where it is difficult for staff to use common facilities particularly at night or due to distance. The room may also be used for small meetings or tutorials and for the storage of staff resources or library materials. Facilities for food and beverage preparation and storage should be provided. Additional Design Considerations: An external outlook is desirable. Staff only access may be required if this room is provided in a public or patient care area. A dishwasher may be provided depending on local operational polices. Front access to the sink for wheelchair access has been shown; a side approach may be acceptable depending on local/jurisdictional policies and staff requirements. The use of thermal heat detectors for fire detection is recommended. A portable fire extinguisher and fire blanket must be provided.
SSTN-10 | Staff Station, 10m2 | 10 | 24 Hours | 2 workstations |  | Sound attenuation level medium, Acoustic privacy is required. | The Staff Station is the operational and administrative base of a unit and enquiry point for patients and visitors. It provides for the co-ordination of patient care, patient observation, write-up of clinical notes, data entry and making/receiving telephone calls. The Staff Station may also accommodate a receptionist/ward clerk. The number of workspaces and area (m2) requirements will vary depending on the type of department, activity level, number of full and part-time staff, operational models and building layout. One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Clinical Workroom. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations are provided). Additional Design Considerations: A set down area may be provided for side access by visitors and patients in wheelchairs. If the Staff Station also serves a reception function, a recessed area for front access by wheelchair users may be required. The room may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security as required in high risk areas. Standing-height workstations may be provided. A desktop printer and labels printer may be provided as required. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. Additional monitors may be required for patient monitoring or security purposes depending on service requirements. Placement and visibility of nurse annunciators in adjacent corridors needs to be considered and coordinated with other ceiling elements such as bulkheads. Any rooms that are accessed from behind the staff station will require additional area for appropriate door circulation clearance. Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444.
SSTN-14 | Staff Station, 14m2 | 14 | 24 Hours | 3 workstations |  | Sound attenuation level medium, Acoustic privacy is required. | The Staff Station is the operational and administrative base of a unit and enquiry point for patients and visitors. It provides for the co-ordination of patient care, patient observation, write-up of clinical notes, data entry and making/receiving telephone calls. The Staff Station may also accommodate a receptionist/ward clerk. The number of workspaces and area (m2) requirements will vary depending on the type of department, activity level, number of full and part-time staff, operational models and building layout. One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Clinical Workroom. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations are provided). Additional Design Considerations: A set down area may be provided for side access by visitors and patients in wheelchairs. If the Staff Station also serves a reception function, a recessed area for front access by wheelchair users may be required. The room may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security as required in high risk areas. Standing-height workstations may be provided. A desktop printer and labels printer may be provided as required. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. Additional monitors may be required for patient monitoring or security purposes depending on service requirements. Placement and visibility of nurse annunciators in adjacent corridors needs to be considered and coordinated with other ceiling elements such as bulkheads. Any rooms that are accessed from behind the staff station will require additional area for appropriate door circulation clearance. Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444.
SSTN-20 | Staff Station, 20m2 | 20 | 24 Hours | 4 workstations |  | Sound attenuation level medium, Acoustic privacy is required. | The Staff Station is the operational and administrative base of a unit and enquiry point for patients and visitors. It provides for the co-ordination of patient care, patient observation, write-up of clinical notes, data entry and making/receiving telephone calls. The Staff Station may also accommodate a receptionist/ward clerk. The number of workspaces and area (m2) requirements will vary depending on the type of department, activity level, number of full and part-time staff, operational models and building layout. One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Clinical Workroom. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations are provided). Additional Design Considerations: A set down area may be provided for side access by visitors and patients in wheelchairs. If the Staff Station also serves a reception function, a recessed area for front access by wheelchair users may be required. The room may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security as required in high risk areas. Standing-height workstations may be provided. A desktop printer and labels printer may be provided as required. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. Additional monitors may be required for patient monitoring or security purposes depending on service requirements. Placement and visibility of nurse annunciators in adjacent corridors needs to be considered and coordinated with other ceiling elements such as bulkheads. Any rooms that are accessed from behind the staff station will require additional area for appropriate door circulation clearance. Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444.
STAD | Store - Accountable Drugs | 7.5 | 24 Hours | 1 - 2 intermittently |  |  | The Store &#8211; Accountable Drugs is a strongroom located within the Pharmacy Unit for the storage of accountable (Schedule 8) drugs and medications and provides a secure caged area for assembling orders. This room is to comply with jurisdictional legislation and public health facility policy, including any special provisions for refrigerated medicines. The strong room should be designed in collaboration with an expert security consultant with assessment of the risks for the particular site. Additional Design Considerations: The strong room should be independent of the rest of the building structure with no beams or columns passing through the ceiling, walls or floor. The ceiling walls and floor should be built utilisiing suitable construction methods, e.g. reinforced concrete or steel plate modular forms (the wall thickness shown in this Standard Component is indicative only). A gate door is to be provided for security when the main door is open. The security door should be torch and drill resistant, fitted with an appropriate locking mechanism incorporating duress features and an internal release mechanism in case persons are trapped within. The strongroom will require adequate ventilation and a torch and drill resistant breather tube must be fitted to comply with fire regulations. Security monitoring and detection equipment should be incorporated into the alarm system, to detect any attack on the structure. A telephone should be installed for staff safety
STBK | Store - Bulk | 30 | Up to 24 Hours | 2-3 staff, accessed intermittently |  |  | The Store - Bulk is the primary storage area for all delivered supplies and equipment prior to distribution to hospital services / departments. The Bulk Store should be located with ready access to the loading dock area. Some departments, such as pharmacy, renal dialysis and pathology, will have bulk storage spaces that are managed independently. Additional Considerations: Type and extent of storage solutions for this room will depend on the departments to be serviced and operational models for stock and equipment delivery. Where a 'direct to imprest' model is used, consumable inventory is stored at a supply chain distribution centre and delivered to the hospital already packed into trolleys specific to the clinical area and immediately delivered to those areas. Long term storage is not required and less area is needed near the loading dock. A 'central bulk store' model refers to goods being delivered to the hospital in large quantities and stored in a central bulk store. The process involves the delivery of goods on pallets, goods are then checked, unloaded, and placed in a bulk store by hospital supply staff. Consumables will then be picked and packed from the central store and delivered to clinical units and other areas as required. Automated or motorised equipment may be considered to assist with the safe and efficient transfer of supply trolleys throughout the healthcare facility. Where tugs and AGVs are being considered, it is important to confirm clearances, door widths and turning circles within the room, in the adjacent corridor and along path of travel to all services / departments. Refrigerated storage requirements to be confirmed at project level. Wall protection is recommended to protect wall linings and finishes from damage from impact. The height of the wall protection will be dependent on equipment and trolleys frequently moved through the space; a height range of 900mm minimum up to 1500mm is recommended depending on trolley and equipment selection. Hold open door hardware may be required to allow for easy movement of pallet jacks and trolleys in and out of the room. Controlled, staff only access is required.
STCL | Store - Cleaner | 12 | Up to 24 Hours | 1-2 staff, accessed intermittently |  |  | The Store - Cleaner is a store provided for the central storage of consumables and bulk containers of cleaning chemicals. Large facilities may provide a separate room for the storage of chemicals depending on quantities, safety requirements and operational policies for centralised storage and decanting of chemicals to units. Additional Considerations: Hold open door hardware may be required to allow for easy movement of equipment and trolleys in and out of the room. Type and extent of storage solutions for this room will depend on the departments to be serviced and operational models for cleaning and restocking consumables. Type of storage provided for cleaning chemicals, particularly where the storage of significant quantities of chemicals containing flammable ingredients, to be assessed to meet safety and service requirements. A clean linen trolley, or equivalent, may be provided for storage of clean mop heads that are laundered either onsite or offsite. The size of trolley will vary depending on service model and size of facility. Controlled, staff only access is required.
STEQ-14 | Store - Equipment, 14m2 | 14 | Available 24 hours | 1-2 staff, intermittently |  |  | A secure room for the storage and recharging of mobile equipment when not in use. Clear space is required for parking mobile equipment including IV poles, wheelchairs, patient transfer equipment, trolleys and commode chairs. Hooks may be provided for hanging equipment and rails may be provided to mount equipment whilst recharging. Additional Design Considerations: Minimum and maximum shelving heights to suit local WHS and infection control policies, as well as fire safety requirements (e.g. the top of stored products is to be no nearer than 500mm to sprinkler deflectors).
STEQ-20 | Store - Equipment, 20m2 | 20 | Available 24 hours | 1-2 staff, intermittently |  |  | A secure room for the storage and recharging of mobile equipment when not in use. Clear space is required for parking mobile equipment including IV poles, wheelchairs, patient transfer equipment, trolleys and commode chairs. Hooks may be provided for hanging equipment and rails may be provided to mount equipment whilst recharging. Additional Design Considerations: Minimum and maximum shelving heights to suit local WHS and infection control policies, as well as fire safety requirements (e.g. the top of stored products is to be no nearer than 500mm to sprinkler deflectors).
STFS-10 | Store - Files, 10m2 | 10 | Available 24 hours | 1-2 staff intermittently |  |  | The Files Store is a secure room for the storage of departmental files or patient clinical records. Additional Considerations: Type, size and quantity of shelving to be selected to suit service requirements and WHS policies Fire rating to room to be in accordance with NCC and local jurisdiction Records Acts.
STFS-20 | Store - Files, 20m2 | 20 | Available 24 hours | 1-2 staff intermittently |  |  | The Files Store is a secure room for the storage of departmental files or patient clinical records. Additional Considerations: Type, size and quantity of shelving to be selected to suit service requirements and WHS policies. If compactus shelving is installed, the track may be surface mounted or recessed into the floor. Structural Engineer's advice to be sought on floor load bearing capacity and potential deflection effect on walls, doors, etc. Handwheel operation may be required to reduce operator strain depending on block load, refer to local WHS policies. Fire rating to room to be in accordance with NCC and local jurisdiction Records Acts.
STGN | Store - General | 9 | Available 24 hours | 1-2 staff, intermittently |  |  | A secure room for the storage of general supplies used within the department. Additional Design Considerations: Facilities to support restocking workflows, including the use of barcode systems, to be considered to suit operational requirements. Minimum and maximum shelving heights to suit local WHS and infection control policies, as well as fire safety requirements (e.g. the top of stored products is to be no nearer than 500mm to sprinkler deflectors).
STPP | Store - Patient Property | 8 | Available 24 Hours | 1 - 2 intermittently |  |  | A secure room for the storage of patient property including luggage.
STRT | Stress Testing | 20 | Available 24 Hours | 1 patient; 1 - 2 staff |  | Acoustic privacy is required | Room for undertaking patient diagnostic stress testing procedures. The Stress Testing room should be located close to patient toilet and change rooms.
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | 13 | 24 Hours | 1 patient; 1 staff, 1 support person |  | Sound attenuation level high, Acoustic privacy is essential. | The Triage Room, Type 1 will provide a private area for initial assessment, physical examination and commencement of first aid of patients presenting to the Emergency Unit. The Triage Room, Type 1 is for smaller Emergency Units, where the room acts as both the initial triage and follow-on triage assessment requiring physical examination. The desk location and glazing arrangements support this dual function. Weighing facilities, including baby weighing, should be provided nearby. Negative pressure requirement indicates general directional airflow only. Air conditioning to be non recirculating.
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | 13 | 24 Hours | 1 patient; 1 staff, 1 support person |  | Sound attenuation level high, Acoustic privacy is essential. | The Triage Room, Type 2 will provide a private area for initial assessment, physical examination and commencement of first aid of patients presenting to the Emergency Unit. The Triage Room, Type 2 is for Emergency Units that also maintain a separate triage reception function. The room will be located adjacent to, or in close proximity to the triage reception function. Weighing facilities, including baby weighing, should be located nearby. Negative pressure requirement indicates general directional airflow only. Air conditioning to be non recirculating.
TRMT | Treatment Room | 14 | 24 Hours | 1 patient; 1-2 staff |  | Sound attenuation level high, Acoustic privacy is required. | The Treatment Room provides a controlled environment, privacy and facilities for carrying out consultations, examinations, treatments and minor procedures.
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | 28 | up to 24 Hours | 2 patients, 2 -3 staff |  | Sound attenuation level - high; acoustic privacy is required | The Treatment Room - Hand Therapy/Splinting provides a controlled environment, privacy and facilities for carrying out treatment and rehabilitation performed by an occupational therapist or physiotherapist with patients that suffer from conditions affecting the hands and upper limbs, such as wounds, scars, burns, fractures or amputations. Additional Considerations: A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. Depending on operational model, the hand therapy treatment room may be an open area adjoining a space with other allied health treatment bays. If open, floor boxes may be required for power to height adjustable tables. Printing facilities to be shared within the overall department. Refrigeration requirements for some materials in warmer climates may need to be considered.
TRMT-POD | Treatment Room - Podiatry | 14 | up to 24 Hours | 1 patient, 1 visitor/carer, 1 staff |  | Sound attenuation level high, Acoustic privacy is required. | The Treatment Room - Podiatry provides space and facilities for podiatry consultation, examination and treatment. The room may be used for measuring and fitting prosthetic appliances but not for fabrication. Additional Considerations: Medication storage, clean-up facilities for instruments, sink and plaster trap facilities are to be provided nearby. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. An external outlook is desirable.
ULTR | Ultrasound Room | 14 | Available 24 Hours | 1 patient with up to 1 support person; 1-2 staff |  | Acoustic privacy is required | Room for diagnostic ultrasound imaging, located close to patient toilet and change rooms. The room will require access for patients on hospital beds.
ULTR-PR | Ultrasound Room - Procedures | 20 | Available 24 Hours | 1 patient with up to 1 support person; 2-3 staff |  | Acoustic privacy is required | Room for diagnostic ultrasound procedures such as breast biopsy, located close to patient toilet and change rooms. The room will require access for patients on hospital beds.
UTRM | Uptake Room | 10 | 8am to 6pm, daily | 1 patient, 1 staff |  |  | The Uptake Room is used to inject patients with a radiopharmaceutical and allow them to rest until 'uptake' has occurred before transfer to the scanning room. Patients need to be relaxed in a warm, quiet and dimmed environment to promote uptake. Uptake duration is typically 45 to 60 minutes. Additional Considerations: Visual and audio observation of the patient during this time is typically provided from the Control Room of the PET-CT Imaging Room and intercoms, cameras and display screens are to be provided to support patient observation. Injections of radiopharmaceuticals can be undertaken within the room or from outside the room via an automated dose delivery system, which will be accommodated outside each uptake room with a suitable lead-lined injection port in the wall that will allow the coil to be connected to both the machine and the patient (details should be confirmed with vendor) Radiation shielding is required to the room and is to be in accordance with a radiation shielding consultants advice. This will be based on the type of radiopharmaceutical, the number of patients seen on a daily basis and proximity to other services.
WAIT-10 | Waiting, 10m2 | 10 | 24 Hours | Up to 8 |  | Sound attenuation level - high | An area for visitors, families and patients to wait prior to or during visits to a department. A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. Waiting areas may be shared between departments. Public amenities including baby change facilities should be located nearby. An external outlook is desirable. Additional Considerations: Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. Acoustic treatments may be considered as required to ensure the noise level in the space is comfortable both in the waiting area and adjacent reception areas. Check-in kiosks may be located nearby and services will need to be confirmed based on system requirements. Provision of a hearing augmentation system may be required where a built in amplification system is provided, if a TV monitor is installed. Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection control policies.
WAIT-20 | Waiting, 20m2 | 20 | 24 Hours | Up to 17 |  | Sound attenuation level - high | An area for visitors, families and patients to wait prior to or during visits to a department. A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. Waiting areas may be shared between departments. Public amenities including baby change facilities should be located nearby. An external outlook is desirable. Additional Considerations: Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. Acoustic treatments may be considered as required to ensure the noise level in the space is comfortable both in the waiting area and adjacent reception areas. Check-in kiosks may be located nearby and services will need to be confirmed based on system requirements. Provision of a hearing augmentation system may be required where a built in amplification system is provided, if a TV monitor is installed. Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection control policies.
WAIT-30 | Waiting, 30m2 | 30 | 24 Hours | Up to 25 |  | Sound attenuation level - high. | An area for visitors, families and patients to wait prior to or during visits to a department. A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. Waiting areas may be shared between departments. Public amenities including baby change facilities should be located nearby. An external outlook is desirable. Additional Considerations: Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. Acoustic treatments may be considered as required to ensure the noise level in the space is comfortable both in the waiting area and adjacent reception areas. Check-in kiosks may be located nearby and services will need to be confirmed based on system requirements. In large waiting areas (e.g. Emergency Department, Main Entry) provision of facilities for phone charging may be considered. Provision of a hearing augmentation system may be required where a built in amplification system is provided, if a TV monitor is installed. Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection control policies.
WAIT-S | Waiting, Sub | 5 | 24 Hours | Up to 5 patient/visitors |  |  | The Waiting, Sub provides a satellite area for visitors, families and patients to wait within a unit, close to procedure/imaging rooms, consult rooms or offices. The size of satellite waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. Additional Considerations: Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection control policies.
WAIT-SEC | Waiting - Secure, 6m2 | 6 | 24 Hours | Up to 4 |  |  | The Secure Waiting is an area for visitors to a Mental Health Unit to wait in comfort prior to or during visits. The area will be secured and visitors will alert staff of their arrival to gain entry to the Unit. The waiting area will be located in close proximity to a reception area or staff station. Public amenties should be located in close proximity. All glazing (including external windows if provided), fittings and fixtures are to comply with Adult Acute Mental Health Inpatient Unit.
WCAC | Toilet - Accessible | 6 | 24 Hours | 1 |  | Sound attenuation level high, Acoustic privacy is required. | The Toilet - Accessible provides a toilet and basin for use by patients, visitors or staff with disabilities (with or without assistance). A baby change table may also be located in this room. If the Toilet - Accessible is located in a patient care area the nurse call system should be included and emergency release door hardware should be installed to allow staff access in an emergency. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system. The entrance to the room should be flush with the adjoining floor. The room shall comply with Australian Standard 1428.1. Signage with braille tactile nominating 'Unisex Accessible WC' required (including RH or LH dependent on layout).
WCPT | Toilet - Patient | 4 | 24 Hours | 1 patient; 1 staff assisting as required |  | Sound attenuation level high, Acoustic privacy is required. | The Toilet - Patient provides a toilet and basin for use by patients (with or without assistance). Emergency release door hardware should be installed to allow staff access in an emergency. The entrance to the room should be flush with the adjoining floor for access in commode chairs/wheelchairs. Signage with braille tactile nominating 'Unisex Patient WC' required
WCPU | Toilet - Public | 3 | 24 Hours | 1 |  | Sound attenuation level high, Acoustic privacy is required. | The Toilet - Public provides a toilet and basin for use by the general public. Signage with braille tactile nominating 'Unisex Public WC' required
WCST | Toilet - Staff | 3 | 24 Hours | 1 |  | Sound attenuation level high, Acoustic privacy is required. | The Toilet - Staff provides a toilet and basin for use by staff. Staff only access may be required if this room is provided in a public or patient care area. Signage with braille tactile nominating 'Unisex Staff WC' required

## Items
Standard Components - Items in room
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
1BR-BA | 1 Bed Room - Bariatric | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P2 (prefer P3) to extend under basin
1BR-BA | 1 Bed Room - Bariatric | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-BA | 1 Bed Room - Bariatric | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-BA | 1 Bed Room - Bariatric | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
1BR-BA | 1 Bed Room - Bariatric | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
1BR-BA | 1 Bed Room - Bariatric | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-BA | 1 Bed Room - Bariatric | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-BA | 1 Bed Room - Bariatric | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-BA | 1 Bed Room - Bariatric | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-BA | 1 Bed Room - Bariatric | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-BA | 1 Bed Room - Bariatric | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional
1BR-BA | 1 Bed Room - Bariatric | FA | DWGL-076 | DOOR: 1600mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
1BR-BA | 1 Bed Room - Bariatric | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to optional observation panel, if provided
1BR-BA | 1 Bed Room - Bariatric | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blinds where required
1BR-BA | 1 Bed Room - Bariatric | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-BA | 1 Bed Room - Bariatric | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-BA | 1 Bed Room - Bariatric | FFE | MMGE-020 | CHAIR: patient, bariatric | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-055 | LIFTER: patient, ceiling mounted, sling component, bariatric | 1 | for patient lifter motor
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-BA | 1 Bed Room - Bariatric | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FQTA-013 | TABLE: overbed | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-BA | 1 Bed Room - Bariatric | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-BA | 1 Bed Room - Bariatric | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 | display screen size to suit wall mounted location
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-004 | BED: patient, bariatric, electric with mattress | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-053 | LIFTER: patient, ceiling mounted, cassette motor for track, bariatric | 1 | for patient lifter track
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-061 | LIFTER: patient, ceiling mounted, track, traverse, bariatric | 1 | to connect to ensuite lifter
1BR-BA | 1 Bed Room - Bariatric | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-BA | 1 Bed Room - Bariatric | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-BA | 1 Bed Room - Bariatric | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-BA | 1 Bed Room - Bariatric | SE | LIFX-017 | LIGHT: night light | 1
1BR-BA | 1 Bed Room - Bariatric | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-BA | 1 Bed Room - Bariatric | SE | ELBO-015 | SWITCH: light, single | 3
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-109 | GPO: single, wall mounted | 1 | for patient entertainment display screen
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-BA | 1 Bed Room - Bariatric | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-BA | 1 Bed Room - Bariatric | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-CCU | 1 Bed Room - CCU | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
1BR-CCU | 1 Bed Room - CCU | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 11
1BR-CCU | 1 Bed Room - CCU | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
1BR-CCU | 1 Bed Room - CCU | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
1BR-CCU | 1 Bed Room - CCU | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2 | to basin
1BR-CCU | 1 Bed Room - CCU | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1
1BR-CCU | 1 Bed Room - CCU | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | ceiling tiles may also be acceptable dependent upon the acuity of patients to be accommodated and procedures to be performed within the room
1BR-CCU | 1 Bed Room - CCU | FA | DWWH-005 | WINDOW | 1 | external, natural light and outlook essential
1BR-CCU | 1 Bed Room - CCU | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | extent of glazing to suit service requirements
1BR-CCU | 1 Bed Room - CCU | FA | DWOB-001 | OBSERVATION: internal window | 1 | optional; extent of glazing to suit service requirements
1BR-CCU | 1 Bed Room - CCU | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-CCU | 1 Bed Room - CCU | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-CCU | 1 Bed Room - CCU | FFE | FIHR-019 | BRACKET: for suction bottle | 2
1BR-CCU | 1 Bed Room - CCU | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | optional, mobile sharps bin may be provided to be shared between multiple rooms
1BR-CCU | 1 Bed Room - CCU | FFE | MMGE-019 | CHAIR: patient | 1
1BR-CCU | 1 Bed Room - CCU | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-CCU | 1 Bed Room - CCU | FFE | DWWD-004 | BLIND: roller | 1 | to external window
1BR-CCU | 1 Bed Room - CCU | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to door and observation window
1BR-CCU | 1 Bed Room - CCU | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-CCU | 1 Bed Room - CCU | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 | to patient entertainment screen; configuration will be dependent on operational and ICT policies
1BR-CCU | 1 Bed Room - CCU | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-CCU | 1 Bed Room - CCU | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-CCU | 1 Bed Room - CCU | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-CCU | 1 Bed Room - CCU | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-CCU | 1 Bed Room - CCU | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 | type and extent of storage for patient property to suit operational policies
1BR-CCU | 1 Bed Room - CCU | FFE | FQTA-013 | TABLE: overbed | 1
1BR-CCU | 1 Bed Room - CCU | FFE | MGFP-004 | FLOWMETER: oxygen | 2
1BR-CCU | 1 Bed Room - CCU | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | optional, mobile sharps bin may be provided to be shared between multiple rooms
1BR-CCU | 1 Bed Room - CCU | FFE | MMGE-002 | ADAPTER: suction | 2
1BR-CCU | 1 Bed Room - CCU | FFE | MMGE-100 | SUCTION BOTTLE | 2
1BR-CCU | 1 Bed Room - CCU | FFE | HYBA-010 | BASIN: handwash, Type B | 1
1BR-CCU | 1 Bed Room - CCU | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-CCU | 1 Bed Room - CCU | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 | configuration will be dependent on operational and ICT policies
1BR-CCU | 1 Bed Room - CCU | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-CCU | 1 Bed Room - CCU | FFE | MMHA-005 | MONITOR: patient, cardiac | 1 | telemetry provision to suit service requirements
1BR-CCU | 1 Bed Room - CCU | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | optional, to patient locker; provision dependent on operational policies
1BR-CCU | 1 Bed Room - CCU | FFE | FIJO-209 | CUPBOARD: tall, single door, adj shelves and clothes rail, recessed | 1 | type and extent of storage for patient property to suit operational policies
1BR-CCU | 1 Bed Room - CCU | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
1BR-CCU | 1 Bed Room - CCU | FFE | PPPP-130 | TRACK: curtain, privacy, S shaped, angled | 1 | to door and observation window
1BR-CCU | 1 Bed Room - CCU | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to patient monitor
1BR-CCU | 1 Bed Room - CCU | SE | ELPR-006 | RCD: residual current device | 3 | on services panel
1BR-CCU | 1 Bed Room - CCU | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
1BR-CCU | 1 Bed Room - CCU | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to patient entertainment system
1BR-CCU | 1 Bed Room - CCU | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | SE | LIFX-011 | LIGHT: reading light | 1 | switch to patient handset and services panel
1BR-CCU | 1 Bed Room - CCU | SE | LIFX-017 | LIGHT: night light | 1 | switch to patient handset and wall near entry
1BR-CCU | 1 Bed Room - CCU | SE | ELBO-015 | SWITCH: light, single | 3 | 1 to general room lighting, 1 to night lighting, 1 on services panel to reading light
1BR-CCU | 1 Bed Room - CCU | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2
1BR-CCU | 1 Bed Room - CCU | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
1BR-CCU | 1 Bed Room - CCU | SE | MGAS-062 | OUTLET: suction, on services panel | 2
1BR-CCU | 1 Bed Room - CCU | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel
1BR-CCU | 1 Bed Room - CCU | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | above services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | SE | ELGP-109 | GPO: single, wall mounted | 1 | to bedhead; low level for electric bed
1BR-CCU | 1 Bed Room - CCU | SE | ELGP-109 | GPO: single, wall mounted | 1 | adjacent to patient chair
1BR-CCU | 1 Bed Room - CCU | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | to patient monitor
1BR-CCU | 1 Bed Room - CCU | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-CCU | 1 Bed Room - CCU | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-CCU | 1 Bed Room - CCU | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
1BR-CCU | 1 Bed Room - CCU | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | quantity to suit service requirements
1BR-CCU | 1 Bed Room - CCU | SE | ELGP-122 | GPO: emergency power, single, on services panel | 9 | type and quantity to suit service requirements
1BR-IC | 1 Bed Room - Intensive Care | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-IC | 1 Bed Room - Intensive Care | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
1BR-IC | 1 Bed Room - Intensive Care | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
1BR-IC | 1 Bed Room - Intensive Care | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-IC | 1 Bed Room - Intensive Care | FA | WLPR-012 | WALL PROTECTION: corner guards, to 900 AFFL, prefinished PVC | 1
1BR-IC | 1 Bed Room - Intensive Care | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
1BR-IC | 1 Bed Room - Intensive Care | FA | DWWH-005 | WINDOW | 1
1BR-IC | 1 Bed Room - Intensive Care | FA | DWGL-002 | DOOR: 910mm c/o, single leaf, half glazed, solid core/glass, paint | 1 | optional, additional door to adjoining space
1BR-IC | 1 Bed Room - Intensive Care | FA | DWSC-012 | DOOR: 1200mm c/o, 1 1/2 leaf, solid core, paint | 1 | optional to ensuite
1BR-IC | 1 Bed Room - Intensive Care | FA | DWGL-071 | DOOR: triple leaf, sliding, fully glazed, alum/safety glass, powdercoat/paint | 1
1BR-IC | 1 Bed Room - Intensive Care | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1 | to partition walls
1BR-IC | 1 Bed Room - Intensive Care | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-IC | 1 Bed Room - Intensive Care | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 11
1BR-IC | 1 Bed Room - Intensive Care | FFE | MGFP-002 | FLOWMETER: medical air | 3 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | FFE | DWWD-007 | BLIND: venetian, integral | 4 | to window and observation panel between rooms and to sub staff station, controls to both sides of internal observation windows
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIHR-019 | BRACKET: for suction bottle | 4
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | for staff
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-019 | CHAIR: patient | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQCW-035 | BIN: waste, recycling, plastics, 50L | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIRT-031 | TRACK: curtain, privacy | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQCW-016 | BIN: waste, general, 20L | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQCW-004 | BIN: waste, clinical, 120L | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | near entry
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMOP-027 | IV POLE: on pendant | 1 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQTA-013 | TABLE: overbed | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | MGFP-004 | FLOWMETER: oxygen | 4 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-142 | TROLLEY: sharps bin | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3 | wire basket bins
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-002 | ADAPTER: suction | 4 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-100 | SUCTION BOTTLE | 4 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMBE-013 | BED: patient, ICU, electric | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | optional
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMSP-020 | PENDANT: tandem, wet and dry combination (fixed or adjustable height) | 1 | with drawer for patient property
1BR-IC | 1 Bed Room - Intensive Care | FFE | ITCL-014 | CLOCK: analogue, electric | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-049 | MACHINE: dialysis | 1 | optional, if mobile dialysis required
1BR-IC | 1 Bed Room - Intensive Care | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMHA-023 | VENTILATOR | 1 | on pendant 1-A
1BR-IC | 1 Bed Room - Intensive Care | FFE | ITBU-006 | CONTROL PANEL: patient entertainment, handset | 1 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | optional
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMHA-030 | MONITOR: patient, cardiac, pendant mounted | 1 | on pendant 1-A
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQBS-055 | CHAIR: overnight fold out | 1 | can optionally be a visitor chair
1BR-IC | 1 Bed Room - Intensive Care | FFE | FIJO-213 | PANEL: joinery carcass end | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | FQSM-043 | TROLLEY: nested, set of 3, underbench | 1
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMBE-068 | LIFTER: patient, pendant mounted | 1 | optional
1BR-IC | 1 Bed Room - Intensive Care | FFE | MMGE-178 | PROCESSOR: reverse osmosis RO water, mobile | 1 | optional, if mobile dialysis required
1BR-IC | 1 Bed Room - Intensive Care | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
1BR-IC | 1 Bed Room - Intensive Care | SE | ELPR-006 | RCD: residual current device | 2 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for display screen
1BR-IC | 1 Bed Room - Intensive Care | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on tandem pendant, + indicator button & light
1BR-IC | 1 Bed Room - Intensive Care | SE | HYTP-008 | OUTLET: cold water | 1 | optional, for reverse osmosis water unit
1BR-IC | 1 Bed Room - Intensive Care | SE | LIFX-017 | LIGHT: night light | 2 | wall washers
1BR-IC | 1 Bed Room - Intensive Care | SE | ELBO-015 | SWITCH: light, single | 3 | optional, to ensuite and anteroom if required, one to night light
1BR-IC | 1 Bed Room - Intensive Care | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on tandem pendant, + indicator button & light
1BR-IC | 1 Bed Room - Intensive Care | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on tandem pendant, call button on the handset
1BR-IC | 1 Bed Room - Intensive Care | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | on tandem pendant, + indicator button & light
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4 | optional, if mobile dialysis required
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-IC | 1 Bed Room - Intensive Care | SE | ELPR-004 | MONITOR: line isolation | 1
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
1BR-IC | 1 Bed Room - Intensive Care | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
1BR-IC | 1 Bed Room - Intensive Care | SE | ELBO-012 | SWITCH: light, dimmer | 2 | one on pendant, one to wall
1BR-IC | 1 Bed Room - Intensive Care | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 6 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | optionally can be a data outlet, for patient entertainment system
1BR-IC | 1 Bed Room - Intensive Care | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 3 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-121 | GPO: emergency power, single, on pendant | 16 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
1BR-IC | 1 Bed Room - Intensive Care | SE | ELPR-007 | UPS: status indicator | 2 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | HYDR-015 | DRAIN: tundish unit, integral drainage outlets | 1 | optional, if mobile dialysis required
1BR-IC | 1 Bed Room - Intensive Care | SE | HYDR-016 | DRAIN: floor waste, sealed | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | door closer required. Obs panel could alternatively be provided in wall
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to window
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIDI-022 | DISPENSER: moisturiser | 1 | to basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin; sensor mixer optional
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional, consideration of sealing of ceiling fixing requried
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | FFE | FIRT-040 | TRACK: curtain, privacy, L shaped, angled | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replace with data outlet, decision to be made at project level
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MEEX-008 | EXHAUST: low level | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | LIFX-017 | LIGHT: night light | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELBO-015 | SWITCH: light, single | 4
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | door closer required. Obs panel could alternatively be provided in wall
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to window
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to optional observation panel, if provided
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-022 | DISPENSER: moisturiser | 1 | to basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin; sensor mixer optional
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional, consideration of sealing of ceiling fixing requried
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIRT-040 | TRACK: curtain, privacy, L shaped, angled | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replace with data outlet, decision to be made at project level
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MEEX-008 | EXHAUST: low level | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | LIFX-017 | LIGHT: night light | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELBO-015 | SWITCH: light, single | 4
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | FLVY-002 | FLOOR FINISH: vinyl, seamless, coved, cushioned | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | WLWA-003 | WALL FINISH: laminated composite board | 1 | to back of ensuite door
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | for High Dependency and intensive care areas, consider plywood or equivalent backing to ceiling finish
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | DWWH-005 | WINDOW | 1 | natural light and outlook essential
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | DWGL-074 | DOOR: 1120mm c/o, 1 1/2 leaf in/out opening, observation panel, solid core/safety glass, paint | 1 | lockable, anti ligature door hardware
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2 | to window/s, obs panel in door
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIBM-015 | NOTICEBOARD: fixed, velcro | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQDW-025 | DESK: built in, return end, anti ligature | 1 | laminate finish
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQSN-062 | SAFE: small | 1 | optional, for patient belongings, suitable for mental health environments, bolt into place
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | MMBE-017 | BED: patient, mental health, electric | 1 | or mattress on built-in plinth
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQBS-054 | STOOL: ottoman | 1 | suitable for mental health environments
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIBM-022 | MIRROR: fixed, safety glass, toughened and laminated, anti ligature | 1 | optional, glued to backing material and screw fixed
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIJO-210 | BEDHEAD: mental health | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQBS-056 | CHAIR: tub, mental health | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQTA-083 | TABLE: bedside, anti ligature | 1 | unit is weighted, optional choice of tamper proof wheels or sliders for mobility. Fixed unit is optional alternative
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIJO-215 | CUPBOARD: tall, shelf unit, fixed shelves, anti-ligature, 500D | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | LIFX-001 | LIGHT: night light, tamper proof, anti ligature | 1 | recommended to be on emergency power
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELBO-015 | SWITCH: light, single | 3 | plus two located outside door for light and night light; lighting to have controlled switching to create low stimulus environment. one may optionally be replaced with light motion sensor deactivation switch
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | optional depending on client age group and jurisdicational policy; mobile duress preferred; + indicator button & light
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELGP-109 | GPO: single, wall mounted | 2
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | to desk
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | optional
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ITSE-045 | SENSOR: motion detection, for lighting control, flush to ceiling | 1 | optional
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ITSE-047 | SENSOR: motion detection, for staff alert, flush to ceiling | 1
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | LIFX-034 | LIGHT: reading light, tamper proof, anti ligature, ceiling recessed | 1 | can also be wall recessed
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | FLVY-002 | FLOOR FINISH: vinyl, seamless, coved, cushioned | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | WLWA-003 | WALL FINISH: laminated composite board | 1 | for wall protection behind ensuite door
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | for High Dependency and intensive care areas, consider plywood or equivalent backing to ceiling finish
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | DWWH-005 | WINDOW | 1 | natural light and outlook essential
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1 | optional, dependent on jurisdicational policy and acuity level of unit. control to patient side
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | DWGL-074 | DOOR: 1120mm c/o, 1 1/2 leaf in/out opening, observation panel, solid core/safety glass, paint | 1 | lockable, anti ligature door hardware, obs panel can be omitted if obs window provided
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2 | to window/s and obs panel in door
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | optional, to optional obs panel in wall
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIBM-015 | NOTICEBOARD: fixed, velcro | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQDW-025 | DESK: built in, return end, anti ligature | 1 | laminate finish
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQSN-062 | SAFE: small | 1 | optional, for patient belongings, suitable for mental health environments, bolt into place
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | MMBE-017 | BED: patient, mental health, electric | 1 | or mattress on built-in plinth
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIJO-134 | CUPBOARD: tall, shelf unit, fixed shelves, anti-ligature, 600D | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQBS-054 | STOOL: ottoman | 1 | suitable for mental health environments
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIBM-022 | MIRROR: fixed, safety glass, toughened and laminated, anti ligature | 1 | optional, glued to backing material and screw fixed
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIJO-210 | BEDHEAD: mental health | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQBS-056 | CHAIR: tub, mental health | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQTA-083 | TABLE: bedside, anti ligature | 1 | unit is weighted, optional choice of tamper proof wheels or sliders for mobility. Fixed unit is optional alternative
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | LIFX-001 | LIGHT: night light, tamper proof, anti ligature | 1 | recommended to be on emergency power
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELBO-015 | SWITCH: light, single | 3 | Plus two additional located outside door for light and night light. Lighting to have controlled switching to create low stimulus environment. one may optionally be replaced with light motion sensor deactivation switch
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | optional depending on client age group and jurisdicational policy; mobile duress preferred; + indicator button & light
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELGP-109 | GPO: single, wall mounted | 2
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | to desk
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | optional
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ITSE-045 | SENSOR: motion detection, for lighting control, flush to ceiling | 1 | optional
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ITSE-047 | SENSOR: motion detection, for staff alert, flush to ceiling | 1
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | LIFX-034 | LIGHT: reading light, tamper proof, anti ligature, ceiling recessed | 1 | can also be wall recessed
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blind where required
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FQBS-055 | CHAIR: overnight fold out | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replace with data outlet, decision to be made at project level
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | LIFX-017 | LIGHT: night light | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blind where required
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FQBS-055 | CHAIR: overnight fold out | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replace with data outlet, decision to be made at project level
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | LIFX-017 | LIGHT: night light | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 3 | optional
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | DWWD-001 | BLIND: blackout | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | LIFX-017 | LIGHT: night light | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 3 | optional
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | DWWD-001 | BLIND: blackout | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELPR-006 | RCD: residual current device | 2 | to services panel
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | LIFX-017 | LIGHT: night light | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 3 | optional
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | DWWD-001 | BLIND: blackout | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | LIFX-017 | LIGHT: night light | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to optional observation panel, if provided
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | DWWD-001 | BLIND: blackout | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELPR-006 | RCD: residual current device | 2 | to services panel
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | LIFX-017 | LIGHT: night light | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to optional observation panel, if provided
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | DWWD-001 | BLIND: blackout | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELPR-006 | RCD: residual current device | 2 | to services panel
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | LIFX-017 | LIGHT: night light | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to optional observation panel, if provided
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | DWWD-001 | BLIND: blackout | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MMGE-019 | CHAIR: patient | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FQTA-013 | TABLE: overbed | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | LIFX-017 | LIGHT: night light | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELBO-015 | SWITCH: light, single | 3
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 3 | optional
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MGFP-002 | FLOWMETER: medical air | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | DWWD-001 | BLIND: blackout | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIHR-019 | BRACKET: for suction bottle | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMGE-019 | CHAIR: patient | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQBS-030 | CHAIR: visitor, patient | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQGE-010 | CURTAIN: privacy screen | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQTA-013 | TABLE: overbed | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MGFP-004 | FLOWMETER: oxygen | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMGE-002 | ADAPTER: suction | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMGE-100 | SUCTION BOTTLE | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-010 | BED: patient, electric with mattress | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIRT-041 | TRACK: curtain, privacy, U shaped, angled | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | LIFX-017 | LIGHT: night light | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELBO-015 | SWITCH: light, single | 3
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-109 | GPO: single, wall mounted | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MGFP-002 | FLOWMETER: medical air | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blind if required
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MMGE-019 | CHAIR: patient | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FQBS-030 | CHAIR: visitor, patient | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 2 | wardrobe
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FQGE-009 | CURTAIN: bed screen | 3
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 2 | optional, for patient lifter motor
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FQTA-013 | TABLE: overbed | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MMGE-002 | ADAPTER: suction | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MMGE-100 | SUCTION BOTTLE | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-010 | BED: patient, electric with mattress | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 2 | optional, for patient lifter track
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 2 | optional
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | FFE | FIRT-022 | TRACK: curtain, bedscreen, 2nd bed | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELPR-006 | RCD: residual current device | 4 | on services panel
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ITIN-070 | OUTLET: MATV | 2 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | for ceiling mounted display screen
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | on services panel, + indicator button & light
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | LIFX-011 | LIGHT: reading light | 2 | up/down light
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | LIFX-017 | LIGHT: night light | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 2 | on services panel
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELBO-015 | SWITCH: light, single | 4
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | on services panel
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | on services panel, + indicator button & light
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 2 | on services panel, + light switch on the handset
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | + indicator button & light
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-109 | GPO: single, wall mounted | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-208 | GPO: double, wall mounted | 2 | bedhead low level, for electric bed
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | on services panel, 1 outlet for telephone
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-105 | GPO: single, on services panel | 8 | on services panel
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on services panel
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blind if required
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MMGE-019 | CHAIR: patient | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FQBS-030 | CHAIR: visitor, patient | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 2 | wardrobe
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FQGE-009 | CURTAIN: bed screen | 3
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 2 | optional, for patient lifter motor
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FQTA-013 | TABLE: overbed | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MMGE-002 | ADAPTER: suction | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-010 | BED: patient, electric with mattress | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 2 | optional, for patient lifter track
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 2 | optional
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | FFE | FIRT-022 | TRACK: curtain, bedscreen, 2nd bed | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELPR-006 | RCD: residual current device | 4 | on services panel
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ITIN-070 | OUTLET: MATV | 2 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | for ceiling mounted display screen
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | on services panel, + indicator button & light
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | LIFX-011 | LIGHT: reading light | 2 | up/down light
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | LIFX-017 | LIGHT: night light | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 2 | on services panel
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELBO-015 | SWITCH: light, single | 4
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | on services panel
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | on services panel, + indicator button & light
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 2 | on services panel, + light switch on the handset
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | + indicator button & light
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-109 | GPO: single, wall mounted | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-208 | GPO: double, wall mounted | 2 | bedhead low level, for electric bed
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | on services panel, 1 outlet for telephone
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-105 | GPO: single, on services panel | 8 | on services panel
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on services panel
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MGFP-002 | FLOWMETER: medical air | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | DWWD-007 | BLIND: venetian, integral | 1 | optional, if internal observation window is provided, 2 way control
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blind if required
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIHR-019 | BRACKET: for suction bottle | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMGE-019 | CHAIR: patient | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQBS-030 | CHAIR: visitor, patient | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 2 | wardrobe
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQGE-009 | CURTAIN: bed screen | 3
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 2 | optional, for patient lifter motor
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQTA-013 | TABLE: overbed | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MGFP-004 | FLOWMETER: oxygen | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMGE-002 | ADAPTER: suction | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMGE-100 | SUCTION BOTTLE | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-010 | BED: patient, electric with mattress | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 2 | optional, for patient lifter track
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 2 | optional
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIRT-022 | TRACK: curtain, bedscreen, 2nd bed | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIRT-042 | TRACK: curtain, bedscreen, U shaped, angled | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELPR-006 | RCD: residual current device | 4 | on services panel
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITIN-070 | OUTLET: MATV | 2 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | for ceiling mounted display screen
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | on services panel, + indicator button & light
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | LIFX-011 | LIGHT: reading light | 2 | up/down light
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | LIFX-017 | LIGHT: night light | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 2 | on services panel
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 4
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | on services panel
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | on services panel, + indicator button & light
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 2 | on services panel, + light switch on the handset
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | + indicator button & light
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-109 | GPO: single, wall mounted | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-208 | GPO: double, wall mounted | 2 | bedhead low level, for electric bed
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | on services panel, 1 outlet for telephone
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-105 | GPO: single, on services panel | 8 | on services panel
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on services panel
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 6
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 4 | joinery can optionally be used as bulkhead above cupboard
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWWH-005 | WINDOW | 2 | natural light & outlook essential
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 2 | to ensuites
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MGFP-002 | FLOWMETER: medical air | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | DWWD-001 | BLIND: blackout | 2 | to windows, provide additional anti glare blind if required
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIHR-019 | BRACKET: for suction bottle | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMGE-019 | CHAIR: patient | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQBS-030 | CHAIR: visitor, patient | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 4 | wardrobe
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 2
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQGE-009 | CURTAIN: bed screen | 6
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 4 | optional, for patient lifter motor
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQTA-013 | TABLE: overbed | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MGFP-004 | FLOWMETER: oxygen | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMGE-002 | ADAPTER: suction | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMGE-100 | SUCTION BOTTLE | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-010 | BED: patient, electric with mattress | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | ITNE-049 | TELEPHONE: handset, desktop | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 4 | optional, for patient lifter track
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 4 | optional
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIRT-022 | TRACK: curtain, bedscreen, 2nd bed | 2
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELPR-006 | RCD: residual current device | 8 | on services panel
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITIN-070 | OUTLET: MATV | 4 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-101 | GPO: single, ceiling mounted | 4 | for ceiling mounted display screen
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-008 | BUTTON: nurse call, staff assist | 4 | on services panel, + indicator button & light
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | LIFX-011 | LIGHT: reading light | 4 | up/down light
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | LIFX-017 | LIGHT: night light | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 4 | on services panel
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 5
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 4 | on services panel
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 4 | on services panel
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 4 | on services panel
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 4 | on services panel, + indicator button & light
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 4 | on services panel, + light switch on the handset
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-004 | BUTTON: nurse call, emergency | 4 | + indicator button & light
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-109 | GPO: single, wall mounted | 1
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-208 | GPO: double, wall mounted | 4 | bedhead low level, for electric bed
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MMSP-026 | SERVICES PANEL: wall mounted | 4
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 4 | on services panel, 1 outlet for telephone
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-105 | GPO: single, on services panel | 16 | on services panel
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-122 | GPO: emergency power, single, on services panel | 16 | on services panel
ADLB | ADL Bathroom | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
ADLB | ADL Bathroom | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | significant change in colour from adjacent corridor to be avoided, to be suitable for bare feet, tiles are also acceptable
ADLB | ADL Bathroom | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
ADLB | ADL Bathroom | FA | WLWA-019 | WALL FINISH: vinyl, full height | 6 | tiles also acceptable
ADLB | ADL Bathroom | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant flush set ceiling is also acceptable
ADLB | ADL Bathroom | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 2
ADLB | ADL Bathroom | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1 | with privacy latch and emergency release
ADLB | ADL Bathroom | FA | FLGE-019 | FLOOR HOB: Shower | 1 | optional
ADLB | ADL Bathroom | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ADLB | ADL Bathroom | FFE | MMGE-024 | CHAIR: shower | 1 | commode chair or combined shower/commode chair is also acceptable
ADLB | ADL Bathroom | FFE | FIHR-026 | HOOK: coat | 4
ADLB | ADL Bathroom | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 2 | optional, dependent on infection control policy
ADLB | ADL Bathroom | FFE | FQGE-011 | CURTAIN: shower | 2 | optional, dependent on infection control policy.
ADLB | ADL Bathroom | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ADLB | ADL Bathroom | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ADLB | ADL Bathroom | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ADLB | ADL Bathroom | FFE | FIDI-036 | DISPENSER: toilet paper | 1
ADLB | ADL Bathroom | FFE | FIRT-006 | GRAB RAIL: WC | 1 | 1 is optional, dependent on service requirements
ADLB | ADL Bathroom | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | may be combined with rail for hand held shower
ADLB | ADL Bathroom | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | optional, dependent on service requirements and expected patient cohort
ADLB | ADL Bathroom | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | to basin
ADLB | ADL Bathroom | FFE | FIBM-007 | MIRROR: fixed, glass, full length | 1 | dressing
ADLB | ADL Bathroom | FFE | FQCW-037 | BIN: waste, sanitary | 1 | optional, dependent on waste management policy
ADLB | ADL Bathroom | FFE | FIDI-051 | HOLDER: soap/shampoo, recessed, vertical format | 2
ADLB | ADL Bathroom | FFE | FQBS-008 | BENCH SEAT: freestanding, patient transfer | 1 | portable, for over bath
ADLB | ADL Bathroom | FFE | HYBA-025 | BATH: domestic | 1 | warm water
ADLB | ADL Bathroom | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
ADLB | ADL Bathroom | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2 | diverter required for shower over bath
ADLB | ADL Bathroom | FFE | HYTP-020 | SHOWER: hand-held | 1 | vertical rail to have grabrail strength and fixings
ADLB | ADL Bathroom | FFE | HYWC-006 | TOILET SUITE: patient | 1 | 100mm clearout access point optional
ADLB | ADL Bathroom | FFE | HYTP-021 | SHOWER: hand-held, over bath | 1 | vertical rail to have grabrail strength and fixings
ADLB | ADL Bathroom | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 | shelf for patient belongings may be integral or separate
ADLB | ADL Bathroom | FFE | HYTP-028 | SPOUT: bath, wall mounted | 1
ADLB | ADL Bathroom | FFE | FIRT-044 | GRAB RAIL: bath, vertical | 1
ADLB | ADL Bathroom | FFE | FIRT-048 | GRAB RAIL: L-shaped | 1
ADLB | ADL Bathroom | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
ADLB | ADL Bathroom | SE | HYDR-004 | DRAIN: floor waste | 2
ADLB | ADL Bathroom | SE | ELBO-015 | SWITCH: light, single | 1
ADLB | ADL Bathroom | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 3 | optional; + indicator button & light
ADLB | ADL Bathroom | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ADLB | ADL Bathroom | SE | ELGP-209 | GPO: double, wall mounted, RCD protected | 1
ADLD | ADL Dining | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
ADLD | ADL Dining | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
ADLD | ADL Dining | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
ADLD | ADL Dining | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
ADLD | ADL Dining | FA | WLWA-022 | WALL FINISH: vinyl, to 900 AFFL | 3
ADLD | ADL Dining | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
ADLD | ADL Dining | FA | DWWH-005 | WINDOW | 1 | desirable
ADLD | ADL Dining | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ADLD | ADL Dining | FFE | FQGE-002 | ARTWORK | 1
ADLD | ADL Dining | FFE | FQBS-015 | CHAIR: dining | 3
ADLD | ADL Dining | FFE | DWWD-004 | BLIND: roller | 1
ADLD | ADL Dining | FFE | FQTA-085 | TABLE: square, 1100W, adjustable height | 1 | height adjustable between 750-850H
ADLD | ADL Dining | SE | ELPR-006 | RCD: residual current device | 1
ADLD | ADL Dining | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLD | ADL Dining | SE | ELBO-015 | SWITCH: light, single | 1
ADLD | ADL Dining | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLD | ADL Dining | SE | ELGP-208 | GPO: double, wall mounted | 2
ADLD | ADL Dining | SE | ITSE-006 | BUTTON: duress, fixed | 1
ADLK | ADL Kitchen | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent around sink
ADLK | ADL Kitchen | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 8
ADLK | ADL Kitchen | FA | WLWA-007 | WALL FINISH: splashback | 2
ADLK | ADL Kitchen | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
ADLK | ADL Kitchen | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | plasterboard flush set ceiling is also acceptable
ADLK | ADL Kitchen | FA | DWWH-005 | WINDOW | 1 | desirable
ADLK | ADL Kitchen | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ADLK | ADL Kitchen | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 2
ADLK | ADL Kitchen | FFE | DWWD-004 | BLIND: roller | 1
ADLK | ADL Kitchen | FFE | FIJO-131 | CUPBOARD: tall, single door, adj shelves, lockable | 1
ADLK | ADL Kitchen | FFE | FQSM-040 | PEDESTAL: mobile, drawer unit, lockable, 660H | 1 | under bench
ADLK | ADL Kitchen | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 1
ADLK | ADL Kitchen | FFE | FIJO-156 | CUPBOARD: wall mount, single door, adj shelves | 2
ADLK | ADL Kitchen | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ADLK | ADL Kitchen | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to sink
ADLK | ADL Kitchen | FFE | FIDI-030 | DISPENSER: soap | 1 | to sink
ADLK | ADL Kitchen | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
ADLK | ADL Kitchen | FFE | FQCA-046 | KETTLE: electric | 1
ADLK | ADL Kitchen | FFE | FQCA-067 | OVEN: microwave, domestic | 1 | on bench
ADLK | ADL Kitchen | FFE | FQCA-063 | OVEN: electric | 1 | retractable/side opening doors
ADLK | ADL Kitchen | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
ADLK | ADL Kitchen | FFE | FQCA-072 | RANGEHOOD | 1 | over cooktop
ADLK | ADL Kitchen | FFE | FQCA-031 | FRIDGE: domestic, 250L | 1
ADLK | ADL Kitchen | FFE | HYBA-041 | SINK: double, with drainer, half size rinse bowl | 1 | heat lined, warm water
ADLK | ADL Kitchen | FFE | FQCA-080 | TOASTER: domestic | 1
ADLK | ADL Kitchen | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 2
ADLK | ADL Kitchen | FFE | FIJO-205 | CUPBOARD: drawer unit, single drawer, lockable | 6
ADLK | ADL Kitchen | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead also acceptable
ADLK | ADL Kitchen | FFE | FIJO-213 | PANEL: joinery carcass end | 3
ADLK | ADL Kitchen | FFE | FIJO-223 | CUPBOARD: tall, oven cabinet | 1
ADLK | ADL Kitchen | FFE | FQCA-089 | COOKTOP: induction | 1 | controls to be located close to front
ADLK | ADL Kitchen | FFE | FIJO-224 | PANEL: joinery fixed panel | 5 | to sink and cooktop
ADLK | ADL Kitchen | SE | ELPR-006 | RCD: residual current device | 1
ADLK | ADL Kitchen | SE | ELBO-007 | SWITCH: emergency isolation | 1 | to cooktop and oven
ADLK | ADL Kitchen | SE | ELBO-015 | SWITCH: light, single | 1
ADLK | ADL Kitchen | SE | ELGP-109 | GPO: single, wall mounted | 2 | to range hood and fridge
ADLK | ADL Kitchen | SE | ELGP-208 | GPO: double, wall mounted | 4
ADLK | ADL Kitchen | SE | ELGE-001 | DIRECT CONNECTION: power | 2 | to cooktop and oven
ADLL | ADL Laundry | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
ADLL | ADL Laundry | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
ADLL | ADL Laundry | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
ADLL | ADL Laundry | FA | WLWA-007 | WALL FINISH: splashback | 1
ADLL | ADL Laundry | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
ADLL | ADL Laundry | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | plasterboard flush set ceiling is also acceptable
ADLL | ADL Laundry | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ADLL | ADL Laundry | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
ADLL | ADL Laundry | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ADLL | ADL Laundry | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2
ADLL | ADL Laundry | FFE | FIJO-156 | CUPBOARD: wall mount, single door, adj shelves | 1
ADLL | ADL Laundry | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ADLL | ADL Laundry | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to sink
ADLL | ADL Laundry | FFE | FIDI-030 | DISPENSER: soap | 1 | to sink
ADLL | ADL Laundry | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
ADLL | ADL Laundry | FFE | FQSM-030 | TROLLEY: laundry, basket | 1 | optional
ADLL | ADL Laundry | FFE | FQGE-015 | DRYER: clothes, domestic | 1
ADLL | ADL Laundry | FFE | FQGE-028 | IRON: clothes, electric | 1
ADLL | ADL Laundry | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
ADLL | ADL Laundry | FFE | HYBA-064 | SINK: single, laundry | 1 | with overflow drain, warm water
ADLL | ADL Laundry | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | with inset laundry tub
ADLL | ADL Laundry | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead also acceptable
ADLL | ADL Laundry | FFE | MMAH-039 | PLINTH: laundry | 2
ADLL | ADL Laundry | FFE | FIJO-222 | CUPBOARD: tall, single door, fixed shelf, ADL Laundry | 1
ADLL | ADL Laundry | FFE | FQCW-063 | MACHINE: washing, domestic, front loading | 1
ADLL | ADL Laundry | SE | ELPR-006 | RCD: residual current device | 1 | type 1 10mA in accordance with AS/NZS 3003
ADLL | ADL Laundry | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLL | ADL Laundry | SE | HYTP-008 | OUTLET: cold water | 1 | to washing machine
ADLL | ADL Laundry | SE | HYDR-004 | DRAIN: floor waste | 1
ADLL | ADL Laundry | SE | ELBO-015 | SWITCH: light, single | 1
ADLL | ADL Laundry | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLL | ADL Laundry | SE | ELGP-109 | GPO: single, wall mounted | 2 | to washing machine and dryer
ADLL | ADL Laundry | SE | ELGP-208 | GPO: double, wall mounted | 1 | 30mA RCD protection
AHBF | After Hours Blood Fridge | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
AHBF | After Hours Blood Fridge | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
AHBF | After Hours Blood Fridge | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
AHBF | After Hours Blood Fridge | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
AHBF | After Hours Blood Fridge | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
AHBF | After Hours Blood Fridge | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional, to laboratory if adjacent
AHBF | After Hours Blood Fridge | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
AHBF | After Hours Blood Fridge | FA | CLCN-009 | CORNICE: wall trim fixing | 1
AHBF | After Hours Blood Fridge | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
AHBF | After Hours Blood Fridge | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
AHBF | After Hours Blood Fridge | FFE | ITNE-003 | BAR CODING: reader | 1
AHBF | After Hours Blood Fridge | FFE | FIJO-017 | BENCH: 600D, open under | 1 | laboratory grade
AHBF | After Hours Blood Fridge | FFE | MMLA-053 | FRIDGE: blood products, single door | 1 | sections may be lockable; BMS monitored, audible alarm 24hr; size is to suit service requirements
AHBF | After Hours Blood Fridge | FFE | FIJO-213 | PANEL: joinery carcass end | 1
AHBF | After Hours Blood Fridge | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to fridge for temperature monitoring
AHBF | After Hours Blood Fridge | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
AHBF | After Hours Blood Fridge | SE | ITBU-001 | ALARM: equipment monitoring, temperature | 1 | may be integral to fridge
AHBF | After Hours Blood Fridge | SE | ELBO-015 | SWITCH: light, single | 1
AHBF | After Hours Blood Fridge | SE | ELGP-208 | GPO: double, wall mounted | 2
AHBF | After Hours Blood Fridge | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to fridge
AHBF | After Hours Blood Fridge | SE | ITSE-038 | READER: access control, general | 2 | 1 to entry, 1 is optional to laboratory door if provided
AHDR | After Hours Drug Store | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
AHDR | After Hours Drug Store | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
AHDR | After Hours Drug Store | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
AHDR | After Hours Drug Store | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
AHDR | After Hours Drug Store | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
AHDR | After Hours Drug Store | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | from corridor
AHDR | After Hours Drug Store | FA | DWGL-007 | DOOR: 910mm c/o, single leaf, observation panel, solid core/safety glass, paint | 1 | optional, if room located with direct access from pharmacy
AHDR | After Hours Drug Store | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
AHDR | After Hours Drug Store | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
AHDR | After Hours Drug Store | FFE | FIJO-141 | CUPBOARD: underbench, single door, adj shelves, lockable | 1
AHDR | After Hours Drug Store | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2
AHDR | After Hours Drug Store | FFE | ITSE-012 | CAMERA: CCTV | 1 | optional, provision and placement dependent on local policies
AHDR | After Hours Drug Store | FFE | MMGE-036 | FRIDGE: drugs, underbench | 1
AHDR | After Hours Drug Store | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
AHDR | After Hours Drug Store | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
AHDR | After Hours Drug Store | FFE | FQSM-045 | SHELVING: storage solution, 400W x 600D x 2100H nom., wire, mobile | 2 | storage solution/mix of storage options to be tailored to suit project requirements
AHDR | After Hours Drug Store | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to drug fridge, for temperature monitoring
AHDR | After Hours Drug Store | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
AHDR | After Hours Drug Store | SE | ELBO-015 | SWITCH: light, single | 1
AHDR | After Hours Drug Store | SE | ELGP-208 | GPO: double, wall mounted | 2
AHDR | After Hours Drug Store | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to drug fridge
AHDR | After Hours Drug Store | SE | ITSE-006 | BUTTON: duress, fixed | 1 | optional
AHDR | After Hours Drug Store | SE | ITSE-038 | READER: access control, general | 2
AIRLE-12 | Airlock - Entry, 12m2 | FA | FLGE-016 | FLOOR MAT: recessed, composite slip resistant | 1
AIRLE-12 | Airlock - Entry, 12m2 | FA | FLSK-008 | SKIRTING: to suit glazing system over | 6
AIRLE-12 | Airlock - Entry, 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
AIRLE-12 | Airlock - Entry, 12m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
AIRLE-12 | Airlock - Entry, 12m2 | FA | DWWH-005 | WINDOW | 4 | safety glass
AIRLE-12 | Airlock - Entry, 12m2 | FA | DWGL-050 | DOOR: 1600mm c/o, double leaf, fully glazed, alum/safety glass, powdercoat/paint | 2 | automated doors, provision to hold open doors via key switch to be considered
AIRLE-12 | Airlock - Entry, 12m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
AIRLE-12 | Airlock - Entry, 12m2 | FFE | FIHR-002 | BRACKET: for CCTV camera, ceiling mounted | 1
AIRLE-12 | Airlock - Entry, 12m2 | FFE | ITSE-012 | CAMERA: CCTV | 1 | as required for access and security to suit operational policies
AIRLE-12 | Airlock - Entry, 12m2 | FFE | MEEX-018 | AIR CURTAIN: external door | 1 | optional
AIRLE-12 | Airlock - Entry, 12m2 | FFE | FIDI-055 | DISPENSER: umbrella cover | 1 | optional
AIRLE-12 | Airlock - Entry, 12m2 | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | to camera
AIRLE-12 | Airlock - Entry, 12m2 | SE | ITSE-024 | DOOR RELEASE: access control, emergency override | 1
AIRLE-12 | Airlock - Entry, 12m2 | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1 | to camera
AIRLE-12 | Airlock - Entry, 12m2 | SE | ITSE-049 | INTERCOM: external, audiovisual, wall mounted | 1 | as required for access and security to suit operational policies, may be located to internal door
AIRLE-12 | Airlock - Entry, 12m2 | SE | ITSE-050 | READER: access control, external | 1 | as required for access and security to suit operational policies
AIRLE-12 | Airlock - Entry, 12m2 | SE | ITSE-051 | BUTTON: push to exit | 1 | may be within airlock to external door or nearby adjacent to internal door
AIRLE-6 | Airlock - Entry, 6m2 | FA | FLGE-016 | FLOOR MAT: recessed, composite slip resistant | 1
AIRLE-6 | Airlock - Entry, 6m2 | FA | FLSK-008 | SKIRTING: to suit glazing system over | 6
AIRLE-6 | Airlock - Entry, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
AIRLE-6 | Airlock - Entry, 6m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
AIRLE-6 | Airlock - Entry, 6m2 | FA | DWWH-005 | WINDOW | 2 | safety glass
AIRLE-6 | Airlock - Entry, 6m2 | FA | DWGL-026 | DOOR: 1200mm c/o, single leaf, sliding, fixed panel, fully glazed | 2 | automated doors, provision to hold open doors via key switch to be considered
AIRLE-6 | Airlock - Entry, 6m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
AIRLE-6 | Airlock - Entry, 6m2 | FFE | FIHR-002 | BRACKET: for CCTV camera, ceiling mounted | 1
AIRLE-6 | Airlock - Entry, 6m2 | FFE | ITSE-012 | CAMERA: CCTV | 1 | as required for access and security to suit operational policies
AIRLE-6 | Airlock - Entry, 6m2 | FFE | MEEX-018 | AIR CURTAIN: external door | 1 | optional
AIRLE-6 | Airlock - Entry, 6m2 | FFE | FIDI-055 | DISPENSER: umbrella cover | 1 | optional
AIRLE-6 | Airlock - Entry, 6m2 | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | to camera
AIRLE-6 | Airlock - Entry, 6m2 | SE | ITSE-024 | DOOR RELEASE: access control, emergency override | 1
AIRLE-6 | Airlock - Entry, 6m2 | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1 | to camera
AIRLE-6 | Airlock - Entry, 6m2 | SE | ITSE-049 | INTERCOM: external, audiovisual, wall mounted | 1 | as required for access and security to suit operational policies, may be located to internal door
AIRLE-6 | Airlock - Entry, 6m2 | SE | ITSE-050 | READER: access control, external | 1 | as required for access and security to suit operational policies
AIRLE-6 | Airlock - Entry, 6m2 | SE | ITSE-051 | BUTTON: push to exit | 1 | may be within airlock to external door or nearby adjacent to internal door
ANRM | Anteroom | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl is required to basin; significant change in colour from adjacent area to be avoided
ANRM | Anteroom | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
ANRM | Anteroom | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to 'Acrovyn'
ANRM | Anteroom | FA | WLWA-007 | WALL FINISH: splashback | 1
ANRM | Anteroom | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
ANRM | Anteroom | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
ANRM | Anteroom | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to 'Acrovyn'
ANRM | Anteroom | FA | DWGL-002 | DOOR: 910mm c/o, single leaf, half glazed, solid core/glass, paint | 2 | From Corridor to Anteroom. Staff movement.
ANRM | Anteroom | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ANRM | Anteroom | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
ANRM | Anteroom | FFE | FIHR-026 | HOOK: coat | 4
ANRM | Anteroom | FFE | MMGE-137 | TROLLEY: PPE | 1
ANRM | Anteroom | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ANRM | Anteroom | FFE | FIDI-022 | DISPENSER: moisturiser | 1 | to basin, optional. Depends on operational policy.
ANRM | Anteroom | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ANRM | Anteroom | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ANRM | Anteroom | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
ANRM | Anteroom | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
ANRM | Anteroom | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer to BHW-B (similar)
ANRM | Anteroom | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | Elbow action levers or handsfree optional.
ANRM | Anteroom | SE | ELBO-015 | SWITCH: light, single | 2
AUD-CR | Audiology Control Room | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
AUD-CR | Audiology Control Room | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 6
AUD-CR | Audiology Control Room | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 2
AUD-CR | Audiology Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
AUD-CR | Audiology Control Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
AUD-CR | Audiology Control Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 2 | acoustic seals to suit testing requirements
AUD-CR | Audiology Control Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
AUD-CR | Audiology Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
AUD-CR | Audiology Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
AUD-CR | Audiology Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
AUD-CR | Audiology Control Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
AUD-CR | Audiology Control Room | FFE | FIDI-021 | DISPENSER: mask | 1
AUD-CR | Audiology Control Room | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1
AUD-CR | Audiology Control Room | FFE | MMAH-005 | BOOTH: audiometric | 1 | one way window (non-reflective); acoustic seals to suit testing requirements
AUD-CR | Audiology Control Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | optional
AUD-CR | Audiology Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
AUD-CR | Audiology Control Room | FFE | FQDW-031 | WORKSTATION: straight, adj height, 1650W x 750D x 750H nom. | 1
AUD-CR | Audiology Control Room | FFE | MMAH-036 | CONSOLE: control, audiometric booth | 1 | optional, dependent on service requirements
AUD-CR | Audiology Control Room | FFE | MMAH-042 | DEVICE: tympanometer | 1
AUD-CR | Audiology Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
AUD-CR | Audiology Control Room | SE | ELPR-006 | RCD: residual current device | 1
AUD-CR | Audiology Control Room | SE | ELGP-208 | GPO: double, wall mounted | 3 | provision of emergency power to be determined based on service requirements
AUD-CR | Audiology Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
AUD-CR | Audiology Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
AUD-CR | Audiology Control Room | SE | MMSP-032 | SERVICES PANEL: instrument jack | 1 | optional
AUD-TR | Audiology Testing Room | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
AUD-TR | Audiology Testing Room | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
AUD-TR | Audiology Testing Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | acoustic seals to suit testing requirements
AUD-TR | Audiology Testing Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
AUD-TR | Audiology Testing Room | FFE | FQBS-012 | CHAIR: child | 1
AUD-TR | Audiology Testing Room | FFE | FQBS-014 | CHAIR: client | 2
AUD-TR | Audiology Testing Room | FFE | FQBS-039 | LOUNGE: 1 seat | 1
AUD-TR | Audiology Testing Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
AUD-TR | Audiology Testing Room | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 1
AUD-TR | Audiology Testing Room | FFE | FQDW-001 | DESK: adj height, 1500W x 750D x 750H nom. | 1
AUD-TR | Audiology Testing Room | FFE | FIHR-029 | HOOK: equipment | 2 | for headphones
AUD-TR | Audiology Testing Room | FFE | FQTA-003 | TABLE: children's play | 1
AUD-TR | Audiology Testing Room | FFE | MMAH-005 | BOOTH: audiometric | 1 | with one way window (non-reflective)
AUD-TR | Audiology Testing Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
AUD-TR | Audiology Testing Room | FFE | MMAH-036 | CONSOLE: control, audiometric booth | 1
AUD-TR | Audiology Testing Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
AUD-TR | Audiology Testing Room | FFE | ITAV-061 | SPEAKER: audiology | 2 | wall mounted, calibrated for testing space
AUD-TR | Audiology Testing Room | FFE | MMAH-043 | DEVICE: visual reinforcement audiometry | 2 | wall mounted, may be provided as a screen or puppet box, inclusion is dependent on service requirements
AUD-TR | Audiology Testing Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
AUD-TR | Audiology Testing Room | SE | ELPR-006 | RCD: residual current device | 1
AUD-TR | Audiology Testing Room | SE | ELGP-208 | GPO: double, wall mounted | 6 | provision of emergency power to be determined based on service requirements
AUD-TR | Audiology Testing Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
AUD-TR | Audiology Testing Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
AUD-TR | Audiology Testing Room | SE | MMSP-032 | SERVICES PANEL: instrument jack | 4 | optional, as required for remote operation of equipment
BATH | Bathroom | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
BATH | Bathroom | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
BATH | Bathroom | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
BATH | Bathroom | FA | WLWA-019 | WALL FINISH: vinyl, full height | 6 | tiles are also acceptable
BATH | Bathroom | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
BATH | Bathroom | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1 | privacy latch
BATH | Bathroom | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
BATH | Bathroom | FFE | MMGE-024 | CHAIR: shower | 1
BATH | Bathroom | FFE | FIHR-026 | HOOK: coat | 2
BATH | Bathroom | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | optional, refer to local infection control policy
BATH | Bathroom | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to entry door
BATH | Bathroom | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, refer to local infection control policy
BATH | Bathroom | FFE | FQCW-016 | BIN: waste, general, 20L | 1
BATH | Bathroom | FFE | FQSM-033 | TROLLEY: shower | 1 | height adjustable bath may be provided
BATH | Bathroom | FFE | FIDI-014 | DISPENSER: disposable glove | 1
BATH | Bathroom | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
BATH | Bathroom | FFE | FIDI-030 | DISPENSER: soap | 1
BATH | Bathroom | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | to drop down grab rail
BATH | Bathroom | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 2 | one with toilet paper dispenser, one with nurse call pendant
BATH | Bathroom | FFE | FIBM-006 | MIRROR: fixed, glass | 1
BATH | Bathroom | FFE | FQCW-037 | BIN: waste, sanitary | 1
BATH | Bathroom | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 | or soap dispenser
BATH | Bathroom | FFE | FIRT-016 | RAIL: towel | 1 | with grab rail strength/fixings
BATH | Bathroom | FFE | HYBA-005 | BASIN: handwash, accessible | 1
BATH | Bathroom | FFE | HYWC-001 | TOILET SUITE: accessible | 1 | with backrest
BATH | Bathroom | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2
BATH | Bathroom | FFE | HYTP-020 | SHOWER: hand-held | 1 | to shower
BATH | Bathroom | FFE | HYTP-035 | TAPWARE: mixer, basin, accessible | 1
BATH | Bathroom | FFE | HYTP-045 | SHOWER: hand-held, accessible | 1
BATH | Bathroom | FFE | FIRT-045 | GRAB RAIL: shower, horizontal and vertical | 1
BATH | Bathroom | FFE | FIGE-011 | BACKREST: accessible toilet | 1
BATH | Bathroom | FFE | FIRT-047 | TRACK: curtain, privacy, U shaped | 1
BATH | Bathroom | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | IPX4 rating required
BATH | Bathroom | SE | HYDR-004 | DRAIN: floor waste | 2 | special floor drain required if height adjustable bath provided
BATH | Bathroom | SE | ELBO-015 | SWITCH: light, single | 1
BATH | Bathroom | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | IPX4 rating required
BATH | Bathroom | SE | ITCL-031 | PENDANT: nurse call, patient to staff | 1 | to toilet, IPX4 rating required, additional required for height adjustable bath if provided
BATH | Bathroom | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | IPX4 rating required
BATH | Bathroom | SE | ELGP-208 | GPO: double, wall mounted | 1 | IPX4 rating required
BBEV | Bay - Beverage | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10/pendulum P3 or agreed equivalent around sink; coordinated with adjacent area, significant change in colour to be avoided
BBEV | Bay - Beverage | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | coordinated with adjacent area
BBEV | Bay - Beverage | FA | WLPR-010 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | coordinated with adjacent wall protection
BBEV | Bay - Beverage | FA | WLWA-007 | WALL FINISH: splashback | 2 | to back of bench and return wall
BBEV | Bay - Beverage | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BBEV | Bay - Beverage | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | coordinated with adjacent area
BBEV | Bay - Beverage | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BBEV | Bay - Beverage | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
BBEV | Bay - Beverage | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 1 | optional; configuration of joinery to meet storage requirements
BBEV | Bay - Beverage | FFE | FIJO-104 | CUPBOARD: drawer unit, 3 equal | 2
BBEV | Bay - Beverage | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | size, type and quantity of bins dependent on local waste management policies
BBEV | Bay - Beverage | FFE | HYGE-003 | BOILING/CHILLED WATER UNIT: Combination | 1 | provide grille in joinery for ventilation
BBEV | Bay - Beverage | FFE | HYTP-029 | TAPWARE: boiling/chilled water unit (comb) | 1 | instant hot/cold water tap to sink
BBEV | Bay - Beverage | FFE | FQCA-015 | DISPENSER: ice, potable | 1 | optional; item to comply with infection control requirements
BBEV | Bay - Beverage | FFE | FQCA-067 | OVEN: microwave, domestic | 1
BBEV | Bay - Beverage | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
BBEV | Bay - Beverage | FFE | FQCA-032 | FRIDGE: domestic, 300L | 1 | clear area for fridge to allow for adequate ventilation and full opening of door
BBEV | Bay - Beverage | FFE | FIJO-069 | BENCH TOP: 750D, joinery under, laminate finish | 1 | minimum depth 600mm; where an ice machine is provided the depth may need to increase to accommodate
BBEV | Bay - Beverage | FFE | FIJO-163 | CUPBOARD: tall, single microwave | 1
BBEV | Bay - Beverage | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead is also acceptable
BBEV | Bay - Beverage | FFE | FIJO-212 | BULKHEAD: joinery | 1 | optional, provide if wall mounted joinery provided, plasterboard bulkhead is also acceptable
BBEV | Bay - Beverage | FFE | FQCW-062 | BIN: waste, recycling, comingled, 50L | 1 | size, type and quantity of bins dependent on local waste management policies
BBEV | Bay - Beverage | FFE | HYBA-080 | SINK: single, with drainer, accessible | 1
BBEV | Bay - Beverage | SE | HYTP-008 | OUTLET: cold water | 1 | to boiling/ chilled water unit
BBEV | Bay - Beverage | SE | ELBO-015 | SWITCH: light, single | 1 | optional, lighting and controls to be coordinated with adjacent area
BBEV | Bay - Beverage | SE | ELGP-109 | GPO: single, wall mounted | 3 | 1 to fridge, 1 to microwave, 1 to boiling/ chilled water unit
BBEV | Bay - Beverage | SE | ELGP-208 | GPO: double, wall mounted | 2 | over bench
BBLD | Bay - Blood Fridge | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BBLD | Bay - Blood Fridge | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4 | coordinated with adjacent area
BBLD | Bay - Blood Fridge | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BBLD | Bay - Blood Fridge | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BBLD | Bay - Blood Fridge | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | coordinated with adjacent area
BBLD | Bay - Blood Fridge | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 | coordinated with adjacent area
BBLD | Bay - Blood Fridge | FFE | MMLA-053 | FRIDGE: blood products, single door | 2 | sections may be lockable; BMS monitored, audible alarm 24hr; quantity and size is to suit service requirements
BBLD | Bay - Blood Fridge | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | for temperature monitoring
BBLD | Bay - Blood Fridge | SE | ITBU-001 | ALARM: equipment monitoring, temperature | 2 | may be integral to fridge
BBLD | Bay - Blood Fridge | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 2
BBW | Bay - Blanket / Fluid Warmer | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | FA | WLPR-006 | WALL PROTECTION: corner guards | 1 | coordinated with adjacent wall protection
BBW | Bay - Blanket / Fluid Warmer | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BBW | Bay - Blanket / Fluid Warmer | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area, flush set ceiling is also acceptable
BBW | Bay - Blanket / Fluid Warmer | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | FFE | MMGE-010 | CABINET: blanket/ fluid warming | 1 | for fluids only, blankets only or a combination of fluids and blankets; configuration to suit service requirements
BBW | Bay - Blanket / Fluid Warmer | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional; provide for connection to BMS where temperature monitoring required for fluids; alternative connection may be required depending on BMS or equipment requirements
BBW | Bay - Blanket / Fluid Warmer | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
BES | Bay - Emergency Shower | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
BES | Bay - Emergency Shower | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
BES | Bay - Emergency Shower | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 1
BES | Bay - Emergency Shower | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1
BES | Bay - Emergency Shower | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
BES | Bay - Emergency Shower | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
BES | Bay - Emergency Shower | FFE | HYTP-023 | SHOWER: safety, eyewash combination | 1
BES | Bay - Emergency Shower | SE | HYDR-004 | DRAIN: floor waste | 1
BHW | Bay - Height/ Weight | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BHW | Bay - Height/ Weight | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | coordinated with adjacent area
BHW | Bay - Height/ Weight | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BHW | Bay - Height/ Weight | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BHW | Bay - Height/ Weight | FA | WLWA-022 | WALL FINISH: vinyl, to 900 AFFL | 3 | height dependent on type and height of mobile equipment, crash rails are also acceptable
BHW | Bay - Height/ Weight | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area
BHW | Bay - Height/ Weight | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BHW | Bay - Height/ Weight | FFE | MMGE-089 | SCALES: electronic, chair | 1 | optional, dependent on service requirements
BHW | Bay - Height/ Weight | FFE | MMGE-188 | SCALES: electronic, standing, with stadiometer | 1 | bariatric capacity will be dependent on service requirements; stadiometer may be separate wall mounted or floor standing item; scales may include integral grab rails for support
BHW | Bay - Height/ Weight | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, dependent on equipment requirements
BHW | Bay - Height/ Weight | SE | ELGP-208 | GPO: double, wall mounted | 1
BHWS-A | Bay - Handwashing, Type A | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4
BHWS-A | Bay - Handwashing, Type A | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | if bay is recessed
BHWS-A | Bay - Handwashing, Type A | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | floor finish of adjacent area must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin. significant change in colour to be avoided
BHWS-A | Bay - Handwashing, Type A | FA | WLWA-007 | WALL FINISH: splashback | 3
BHWS-A | Bay - Handwashing, Type A | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BHWS-A | Bay - Handwashing, Type A | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | ceiling tiles are also acceptable, ceiling to be coordinated with adjacent area
BHWS-A | Bay - Handwashing, Type A | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
BHWS-A | Bay - Handwashing, Type A | FFE | FQCW-016 | BIN: waste, general, 20L | 1
BHWS-A | Bay - Handwashing, Type A | FFE | FIDI-014 | DISPENSER: disposable glove | 1
BHWS-A | Bay - Handwashing, Type A | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
BHWS-A | Bay - Handwashing, Type A | FFE | FIDI-030 | DISPENSER: soap | 1
BHWS-A | Bay - Handwashing, Type A | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1
BHWS-A | Bay - Handwashing, Type A | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
BHWS-A | Bay - Handwashing, Type A | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
BHWS-B | Bay - Handwashing, Type B | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
BHWS-B | Bay - Handwashing, Type B | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | if bay is recessed
BHWS-B | Bay - Handwashing, Type B | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | floor finish of adjacent area must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin. significant change in colour to be avoided
BHWS-B | Bay - Handwashing, Type B | FA | WLWA-007 | WALL FINISH: splashback | 3
BHWS-B | Bay - Handwashing, Type B | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BHWS-B | Bay - Handwashing, Type B | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | ceiling tiles are also acceptable, ceiling to be coordinated with adjacent area
BHWS-B | Bay - Handwashing, Type B | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
BHWS-B | Bay - Handwashing, Type B | FFE | FQCW-016 | BIN: waste, general, 20L | 1
BHWS-B | Bay - Handwashing, Type B | FFE | FIDI-014 | DISPENSER: disposable glove | 1
BHWS-B | Bay - Handwashing, Type B | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
BHWS-B | Bay - Handwashing, Type B | FFE | FIDI-030 | DISPENSER: soap | 1
BHWS-B | Bay - Handwashing, Type B | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | optional, dependent on service requirements
BHWS-B | Bay - Handwashing, Type B | FFE | HYBA-010 | BASIN: handwash, Type B | 1
BHWS-B | Bay - Handwashing, Type B | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
BIRM-A | Birthing Room, Without Pool | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
BIRM-A | Birthing Room, Without Pool | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
BIRM-A | Birthing Room, Without Pool | FA | WLPR-006 | WALL PROTECTION: corner guards | 3
BIRM-A | Birthing Room, Without Pool | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
BIRM-A | Birthing Room, Without Pool | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BIRM-A | Birthing Room, Without Pool | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
BIRM-A | Birthing Room, Without Pool | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1
BIRM-A | Birthing Room, Without Pool | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
BIRM-A | Birthing Room, Without Pool | FA | DWWH-005 | WINDOW | 1
BIRM-A | Birthing Room, Without Pool | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | with hold open device to support bed movement as required
BIRM-A | Birthing Room, Without Pool | FA | DWGE-015 | DOOR: concertina folding leaf | 1 | 2000 wide
BIRM-A | Birthing Room, Without Pool | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
BIRM-A | Birthing Room, Without Pool | FFE | MGFP-002 | FLOWMETER: medical air | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-A | Birthing Room, Without Pool | FFE | FQBS-001 | BASSINET | 1 | optional
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1
BIRM-A | Birthing Room, Without Pool | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | 1 to bedhead cupboard, 1 to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | mounted on trolley
BIRM-A | Birthing Room, Without Pool | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | to staff write-up
BIRM-A | Birthing Room, Without Pool | FFE | DWWD-004 | BLIND: roller | 1
BIRM-A | Birthing Room, Without Pool | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
BIRM-A | Birthing Room, Without Pool | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 1 | to staff write-up
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-156 | CUPBOARD: wall mount, single door, adj shelves | 1
BIRM-A | Birthing Room, Without Pool | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
BIRM-A | Birthing Room, Without Pool | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
BIRM-A | Birthing Room, Without Pool | FFE | FIDI-019 | DISPENSER: gown/apron | 1
BIRM-A | Birthing Room, Without Pool | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
BIRM-A | Birthing Room, Without Pool | FFE | FIDI-014 | DISPENSER: disposable glove | 2 | 1 to basin, 1 to room
BIRM-A | Birthing Room, Without Pool | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
BIRM-A | Birthing Room, Without Pool | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
BIRM-A | Birthing Room, Without Pool | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
BIRM-A | Birthing Room, Without Pool | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
BIRM-A | Birthing Room, Without Pool | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 | type and extent of storage for patient property to suit operational policies
BIRM-A | Birthing Room, Without Pool | FFE | FQBS-044 | LOUNGE: 2 seat, sofa bed | 1
BIRM-A | Birthing Room, Without Pool | FFE | FQTA-013 | TABLE: overbed | 1
BIRM-A | Birthing Room, Without Pool | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-A | Birthing Room, Without Pool | FFE | MMMA-011 | MIXER: oxygen and nitrous oxide | 1 | to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-194 | SHELF: laminate | 2 | to equipment store cupboard, type and quantity of storage options to be determined based on service requirements
BIRM-A | Birthing Room, Without Pool | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | for suturing and small procedures
BIRM-A | Birthing Room, Without Pool | FFE | MMGE-002 | ADAPTER: suction | 2 | 1 to bedhead cupboard, 1 to resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | FFE | MMGE-100 | SUCTION BOTTLE | 2 | 1 to bedhead cupboard, 1 to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | FFE | FQSM-016 | TROLLEY | 1 | to equipment store cupboard
BIRM-A | Birthing Room, Without Pool | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
BIRM-A | Birthing Room, Without Pool | FFE | MMBE-005 | BED: patient, birthing, electric | 1
BIRM-A | Birthing Room, Without Pool | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
BIRM-A | Birthing Room, Without Pool | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
BIRM-A | Birthing Room, Without Pool | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | to staff write-up, dual monitors may be provided as required to suit operational, EMR and ICT requirements; a workstation on wheels is also acceptable
BIRM-A | Birthing Room, Without Pool | FFE | MMMA-015 | RESUSCITAIRE: infant, mobile | 1 | Mobile resuscitaire shown. Item may be wall mounted where suitable product is available.
BIRM-A | Birthing Room, Without Pool | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
BIRM-A | Birthing Room, Without Pool | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | optional, to patient locker
BIRM-A | Birthing Room, Without Pool | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 | to staff write-up
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-129 | CUPBOARD: tall, single door, adj shelves | 1 | type and extent of storage to suit service requirements
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-099 | CAC: cable access cap | 1 | to staff write-up bench
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-162 | CUPBOARD: tall, single door, to conceal services | 1
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-209 | CUPBOARD: tall, single door, adj shelves and clothes rail, recessed | 1 | wardrobe, type and extent of storage for patient property to suit operational policies
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-212 | BULKHEAD: joinery | 3
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-213 | PANEL: joinery carcass end | 1 | below FIJO-156 to separate dirty linen trolley from hand wash, storage for clean and dirty linen to suit local operational policies
BIRM-A | Birthing Room, Without Pool | FFE | FIHR-068 | BRACKET: for alcohol based hand rub, attached to bed | 1
BIRM-A | Birthing Room, Without Pool | FFE | MMMA-031 | DEVICE: patient, fetal, cardiotocography (CTG), on trolley | 1 | to equipment store cupboard
BIRM-A | Birthing Room, Without Pool | FFE | MMMA-043 | SUPPORT FIXTURE: birthing, hook, ceiling mounted | 1 | optional, provision dependent on birthing aids/supportive equipment to be used
BIRM-A | Birthing Room, Without Pool | FFE | FIJO-233 | CUPBOARD: tall, infant resuscitaire | 1 | Configuration of joinery to suit resuscitare equipment selected, including consideration of maneuverability and provision of sufficient space for emergency resuscitation procedures. Confirm design with users at project level.
BIRM-A | Birthing Room, Without Pool | FFE | MMMA-041 | SUPPORT FIXTURE: birthing, ladder, wall mounted | 1
BIRM-A | Birthing Room, Without Pool | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to staff write-up for wall mounted phone
BIRM-A | Birthing Room, Without Pool | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to staff write-up
BIRM-A | Birthing Room, Without Pool | SE | ELPR-006 | RCD: residual current device | 3 | 2 to bedhead, 1 to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | ELPR-006 | RCD: residual current device | 2 | to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment system, may be replaced with data outlet depending on ICT policies
BIRM-A | Birthing Room, Without Pool | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to patient entertainment system
BIRM-A | Birthing Room, Without Pool | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | with indicator button and light, to bedhead
BIRM-A | Birthing Room, Without Pool | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | LIFX-011 | LIGHT: reading light | 1 | to bedhead
BIRM-A | Birthing Room, Without Pool | SE | LIFX-017 | LIGHT: night light | 1 | to bedhead
BIRM-A | Birthing Room, Without Pool | SE | ELBO-015 | SWITCH: light, single | 1 | to bedhead MSP for reading light
BIRM-A | Birthing Room, Without Pool | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | with indicator button and light, to bedhead
BIRM-A | Birthing Room, Without Pool | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | to bedhead
BIRM-A | Birthing Room, Without Pool | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light, to bedhead
BIRM-A | Birthing Room, Without Pool | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level for patient bed
BIRM-A | Birthing Room, Without Pool | SE | ELGP-208 | GPO: double, wall mounted | 3 | 2 to staff write-up, 1 to lounge
BIRM-A | Birthing Room, Without Pool | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
BIRM-A | Birthing Room, Without Pool | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
BIRM-A | Birthing Room, Without Pool | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
BIRM-A | Birthing Room, Without Pool | SE | ITSE-006 | BUTTON: duress, fixed | 1 | to staff write-up
BIRM-A | Birthing Room, Without Pool | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2 | 1 to bedhead, 1 inside bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | SE | ELBO-012 | SWITCH: light, dimmer | 2 | 1 to entry door, 1 to staff write up for general room lights
BIRM-A | Birthing Room, Without Pool | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 to bedhead, 1 to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | SE | ELGP-122 | GPO: emergency power, single, on services panel | 6 | to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | 5 to bedhead, 3 to bedhead cupboard
BIRM-B | Birthing Room, With Pool | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
BIRM-B | Birthing Room, With Pool | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
BIRM-B | Birthing Room, With Pool | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to birthing pool
BIRM-B | Birthing Room, With Pool | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
BIRM-B | Birthing Room, With Pool | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
BIRM-B | Birthing Room, With Pool | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BIRM-B | Birthing Room, With Pool | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
BIRM-B | Birthing Room, With Pool | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1
BIRM-B | Birthing Room, With Pool | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
BIRM-B | Birthing Room, With Pool | FA | DWWH-005 | WINDOW | 2
BIRM-B | Birthing Room, With Pool | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | with hold open device to support bed movement as required
BIRM-B | Birthing Room, With Pool | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
BIRM-B | Birthing Room, With Pool | FA | DWGE-017 | DOOR: concertina folding leaf | 1 | 1800 wide
BIRM-B | Birthing Room, With Pool | FFE | MGFP-002 | FLOWMETER: medical air | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | FFE | FQBS-001 | BASSINET | 1 | optional
BIRM-B | Birthing Room, With Pool | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1
BIRM-B | Birthing Room, With Pool | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | mounted on trolley
BIRM-B | Birthing Room, With Pool | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | FFE | DWWD-004 | BLIND: roller | 2
BIRM-B | Birthing Room, With Pool | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
BIRM-B | Birthing Room, With Pool | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
BIRM-B | Birthing Room, With Pool | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
BIRM-B | Birthing Room, With Pool | FFE | FIDI-019 | DISPENSER: gown/apron | 1
BIRM-B | Birthing Room, With Pool | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
BIRM-B | Birthing Room, With Pool | FFE | FIDI-014 | DISPENSER: disposable glove | 2 | 1 to basin, 1 to room
BIRM-B | Birthing Room, With Pool | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
BIRM-B | Birthing Room, With Pool | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 | type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | FFE | FQBS-044 | LOUNGE: 2 seat, sofa bed | 1
BIRM-B | Birthing Room, With Pool | FFE | FQTA-013 | TABLE: overbed | 1
BIRM-B | Birthing Room, With Pool | FFE | MGFP-004 | FLOWMETER: oxygen | 3 | 1 to bedhead cupboard, 1 to resuscitaire cupboard, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | FFE | MMMA-011 | MIXER: oxygen and nitrous oxide | 1 | to bedhead cupboard
BIRM-B | Birthing Room, With Pool | FFE | FIJO-194 | SHELF: laminate | 2 | to equipment store cupboard, type and quantity of storage options to be determined based on service requirements
BIRM-B | Birthing Room, With Pool | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | for suturing and small procedures
BIRM-B | Birthing Room, With Pool | FFE | MMGE-002 | ADAPTER: suction | 2 | 1 to bedhead cupboard, 1 to resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | FFE | MMGE-100 | SUCTION BOTTLE | 2 | 1 to bedhead cupboard, 1 to resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | FFE | FQSM-016 | TROLLEY | 1 | to equipment store cupboard
BIRM-B | Birthing Room, With Pool | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
BIRM-B | Birthing Room, With Pool | FFE | MMBE-005 | BED: patient, birthing, electric | 1
BIRM-B | Birthing Room, With Pool | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
BIRM-B | Birthing Room, With Pool | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | to staff write-up, dual monitors may be provided as required to suit operational, EMR and ICT requirements; a workstation on wheels is also acceptable
BIRM-B | Birthing Room, With Pool | FFE | MMMA-015 | RESUSCITAIRE: infant, mobile | 1
BIRM-B | Birthing Room, With Pool | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
BIRM-B | Birthing Room, With Pool | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2 | 1 to shower, 1 to spout for birthing pool
BIRM-B | Birthing Room, With Pool | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | optional, to patient locker
BIRM-B | Birthing Room, With Pool | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | FFE | FIJO-129 | CUPBOARD: tall, single door, adj shelves | 1 | type and extent of storage to suit service requirements
BIRM-B | Birthing Room, With Pool | FFE | HYTP-021 | SHOWER: hand-held, over bath | 1
BIRM-B | Birthing Room, With Pool | FFE | HYBA-023 | BATH: birthing | 1 | Birthing pools can vary significantly in shape and the pool shown is indicative only. Final selection will have implications for required area and clearances. Ergonomic assessment of birthing pool options should be undertaken prior to selection.
BIRM-B | Birthing Room, With Pool | FFE | FIJO-099 | CAC: cable access cap | 1 | to staff write-up bench
BIRM-B | Birthing Room, With Pool | FFE | FIJO-162 | CUPBOARD: tall, single door, to conceal services | 1
BIRM-B | Birthing Room, With Pool | FFE | FIJO-209 | CUPBOARD: tall, single door, adj shelves and clothes rail, recessed | 1 | wardrobe, type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | FFE | FIJO-212 | BULKHEAD: joinery | 5
BIRM-B | Birthing Room, With Pool | FFE | FIJO-213 | PANEL: joinery carcass end | 2 | 1 below FIJO-156 to separate dirty linen trolley from hand wash, storage for clean and dirty linen to suit local operational policies, 1 below write-up bench
BIRM-B | Birthing Room, With Pool | FFE | FIHR-068 | BRACKET: for alcohol based hand rub, attached to bed | 1
BIRM-B | Birthing Room, With Pool | FFE | MMMA-031 | DEVICE: patient, fetal, cardiotocography (CTG), on trolley | 1 | to equipment store cupboard
BIRM-B | Birthing Room, With Pool | FFE | MMMA-043 | SUPPORT FIXTURE: birthing, hook, ceiling mounted | 1 | optional, provision dependent on birthing aids/supportive equipment to be used
BIRM-B | Birthing Room, With Pool | FFE | FIJO-233 | CUPBOARD: tall, infant resuscitaire | 1 | Configuration of joinery to suit resuscitare equipment selected, including consideration of maneuverability and provision of sufficient space for emergency resuscitation procedures. Confirm design with users at project level.
BIRM-B | Birthing Room, With Pool | FFE | MMMA-041 | SUPPORT FIXTURE: birthing, ladder, wall mounted | 1
BIRM-B | Birthing Room, With Pool | FFE | HYTP-048 | SPOUT: birthing pool, high flow, wall mounted | 1
BIRM-B | Birthing Room, With Pool | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to staff write-up for wall mounted phone
BIRM-B | Birthing Room, With Pool | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | SE | ELPR-006 | RCD: residual current device | 3 | 2 to bedhead, 1 to bedhead cupboard
BIRM-B | Birthing Room, With Pool | SE | ELPR-006 | RCD: residual current device | 2 | to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment system, may be replaced with data outlet depending on ICT policies
BIRM-B | Birthing Room, With Pool | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to patient entertainment system
BIRM-B | Birthing Room, With Pool | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | with indicator button and light, 1 to bedhead, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | MGAS-053 | OUTLET: scavenge, on services panel | 2 | 1 to bedhead cupboard, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | HYDR-004 | DRAIN: floor waste | 1 | to birthing pool area
BIRM-B | Birthing Room, With Pool | SE | LIFX-011 | LIGHT: reading light | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | LIFX-017 | LIGHT: night light | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | ELBO-015 | SWITCH: light, single | 1 | to bedhead for reading light
BIRM-B | Birthing Room, With Pool | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 3 | 2 to bedhead cupboard, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 2 | 1 to bedhead cupboard, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to bedhead cupboard
BIRM-B | Birthing Room, With Pool | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to bedhead cupboard
BIRM-B | Birthing Room, With Pool | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | with indicator button and light
BIRM-B | Birthing Room, With Pool | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light, 1 to bedhead, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level for patient bed
BIRM-B | Birthing Room, With Pool | SE | ELGP-208 | GPO: double, wall mounted | 3 | 2 to staff write-up, 1 to lounge
BIRM-B | Birthing Room, With Pool | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
BIRM-B | Birthing Room, With Pool | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
BIRM-B | Birthing Room, With Pool | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
BIRM-B | Birthing Room, With Pool | SE | ITSE-006 | BUTTON: duress, fixed | 2 | 1 to staff write-up, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | MMSP-026 | SERVICES PANEL: wall mounted | 4 | 2 to bedhead, 1 to infant resuscitaire cupboard, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | ELBO-012 | SWITCH: light, dimmer | 2 | 1 to entry door, 1 to staff write up for general room lights
BIRM-B | Birthing Room, With Pool | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 to bedhead, 1 to bedhead cupboard
BIRM-B | Birthing Room, With Pool | SE | ELGP-122 | GPO: emergency power, single, on services panel | 6 | to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | 5 to bedhead, 3 to bedhead cupboard
BIRM-B | Birthing Room, With Pool | SE | HYGE-028 | DEVICE: backflow prevention | 1 | to birthing pool area
BLIN | Bay - Linen | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BLIN | Bay - Linen | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | coordinated with adjacent area
BLIN | Bay - Linen | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BLIN | Bay - Linen | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BLIN | Bay - Linen | FA | WLWA-021 | WALL FINISH: vinyl, to 1800 AFFL | 1
BLIN | Bay - Linen | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area, flush set ceiling is also acceptable
BLIN | Bay - Linen | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BLIN | Bay - Linen | FFE | FIHR-029 | HOOK: equipment | 3 | optional, for storage of linen bags
BLIN | Bay - Linen | FFE | MMGE-109 | TROLLEY: clean linen | 1 | with cover as required to suit infection prevention and control policies
BLIN | Bay - Linen | FFE | FIJO-129 | CUPBOARD: tall, single door, adj shelves | 1 | optional, for storage of additional items such as pillows, privacy curtains, shower curtains, etc.
BLIN | Bay - Linen | FFE | FIJO-212 | BULKHEAD: joinery | 1 | optional, to joinery cupboard if provided, plasterboard bulkhead is also acceptable
BLIN | Bay - Linen | SE | ELBO-015 | SWITCH: light, single | 1 | optional, lighting and controls to be coordinated with adjacent area, may be provided if bay is enclosed
BMEQ | Bay - Mobile Equipment | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4 | coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | FA | WLPR-006 | WALL PROTECTION: corner guards | 1 | coordinated with adjacent wall protection
BMEQ | Bay - Mobile Equipment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BMEQ | Bay - Mobile Equipment | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 3 | height dependent on type and height of mobile equipment, crash rails are also acceptable
BMEQ | Bay - Mobile Equipment | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 1 | optional
BMEQ | Bay - Mobile Equipment | FFE | MMBE-042 | SLIDE: patient | 1 | optional
BMEQ | Bay - Mobile Equipment | SE | ELGP-208 | GPO: double, wall mounted | 2 | type, quantity and configuration of outlets to be determined based on equipment requirements
BMFD-3 | Bay - Multifunction Device, 3m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
BMFD-3 | Bay - Multifunction Device, 3m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
BMFD-3 | Bay - Multifunction Device, 3m2 | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
BMFD-3 | Bay - Multifunction Device, 3m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BMFD-3 | Bay - Multifunction Device, 3m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
BMFD-3 | Bay - Multifunction Device, 3m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
BMFD-3 | Bay - Multifunction Device, 3m2 | FFE | FQCW-038 | BIN: waste, secure | 1 | type and size of bins is to suit waste management policies and may be rationalised with bins provided in adjacent area
BMFD-3 | Bay - Multifunction Device, 3m2 | FFE | FQCW-029 | BIN: waste, recycling, paper, 240L | 1 | type and size of bins is to suit waste management policies and may be rationalised with bins provided in adjacent area
BMFD-3 | Bay - Multifunction Device, 3m2 | FFE | ITNE-021 | MULTIFUNCTION DEVICE: floorstanding | 1 | recommended manufacturer clearances zones to be considered, bins and other moveable items may be within clearance zones
BMFD-3 | Bay - Multifunction Device, 3m2 | FFE | FIJO-129 | CUPBOARD: tall, single door, adj shelves | 1 | stationary storage to suit service requirements, mobile is storage also acceptable
BMFD-3 | Bay - Multifunction Device, 3m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1
BMFD-3 | Bay - Multifunction Device, 3m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
BMFD-3 | Bay - Multifunction Device, 3m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
BMFD-7 | Bay - Multifunction Device, 7m2 | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
BMFD-7 | Bay - Multifunction Device, 7m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
BMFD-7 | Bay - Multifunction Device, 7m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 2
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FQCW-038 | BIN: waste, secure | 1 | type and size of bins is to suit waste management policies and may be rationalised with bins provided in adjacent area
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FQCW-029 | BIN: waste, recycling, paper, 240L | 1 | type and size of bins is to suit waste management policies and may be rationalised with bins provided in adjacent area
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | ITNE-021 | MULTIFUNCTION DEVICE: floorstanding | 1 | recommended manufacturer clearances zones to be considered, bins and other moveable items may be within clearance zones
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FIJO-129 | CUPBOARD: tall, single door, adj shelves | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | FFE | FIJO-212 | BULKHEAD: joinery | 2
BMFD-7 | Bay - Multifunction Device, 7m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
BMFD-7 | Bay - Multifunction Device, 7m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
BMT | Bay - Meal Trolley | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BMT | Bay - Meal Trolley | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | coordinated with adjacent area
BMT | Bay - Meal Trolley | FA | WLPR-006 | WALL PROTECTION: corner guards | 1 | coordinated with adjacent wall protection
BMT | Bay - Meal Trolley | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BMT | Bay - Meal Trolley | FA | WLWA-021 | WALL FINISH: vinyl, to 1800 AFFL | 1
BMT | Bay - Meal Trolley | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area, flush set ceiling is also acceptable
BMT | Bay - Meal Trolley | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BMT | Bay - Meal Trolley | FFE | FQCA-082 | TROLLEY: food delivery, hot/cold | 2 | type of meal trolley will be dependent on food service delivery model
BMT | Bay - Meal Trolley | SE | ELGP-109 | GPO: single, wall mounted | 2 | power requirements will be dependent on type of meal trolley
BMT | Bay - Meal Trolley | SE | ELGP-140 | GPO: three phase, single | 2 | optional, power requirements will be dependent on type of meal trolley
BPATH | Bay - Pathology Point of Care Testing (POCT) | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9 | coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BPATH | Bay - Pathology Point of Care Testing (POCT) | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BPATH | Bay - Pathology Point of Care Testing (POCT) | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | FA | WLWA-009 | WALL FINISH: splashback, laminate | 3 | coved, integral to bench
BPATH | Bay - Pathology Point of Care Testing (POCT) | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FIHR-016 | BRACKET: for sharps bin | 1
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FIJO-141 | CUPBOARD: underbench, single door, adj shelves, lockable | 1 | lockable; extent of storage to suit testing requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | quantity and type of bins to be based on local waste management policies
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1 | lockable; extent of storage to suit testing requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | with wide opening
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1 | quantity and type of bins to be based on local waste management policies
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | MMLA-049 | DEVICE: point of care | 2 | quantity and type to suit service requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FQGE-056 | PRINTER: desktop, labels | 1
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | MMLA-055 | FRIDGE: laboratory, underbench | 1 | lockable; temperature monitored
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | may be wall mounted
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | ITNE-003 | BAR CODING: reader | 1 | optional, dependent on software requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FIJO-069 | BENCH TOP: 750D, joinery under, laminate finish | 1 | laboratory grade
BPATH | Bay - Pathology Point of Care Testing (POCT) | FFE | FIJO-099 | CAC: cable access cap | 1
BPATH | Bay - Pathology Point of Care Testing (POCT) | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | quantity to suit project specific equipment requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | to computer
BPATH | Bay - Pathology Point of Care Testing (POCT) | SE | ITBU-001 | ALARM: equipment monitoring, temperature | 1 | to fridge, dependent on requirements, may be integral to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 5 | quantity to suit project specific equipment requirements, confirm UPS requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to fridge
BPROP | Bay - Property, Staff | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BPROP | Bay - Property, Staff | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3 | coordinated with adjacent area
BPROP | Bay - Property, Staff | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | align height with locker doors
BPROP | Bay - Property, Staff | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
BPROP | Bay - Property, Staff | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | coordinated with adjacent area
BPROP | Bay - Property, Staff | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BPROP | Bay - Property, Staff | FFE | FQSN-048 | LOCKER: 2 tier (half size) | 2 | quantity and size of lockers to be based on staffing and service requirements
BPROP | Bay - Property, Staff | FFE | FQSN-050 | LOCKER: 4 tier (quarter size) | 6 | quantity and size of lockers to be based on staffing and service requirements
BPROP | Bay - Property, Staff | FFE | FIJO-212 | BULKHEAD: joinery | 1 | optional; plasterboard bulkhead is also acceptable
BPTS | Bay - Pneumatic Tube Station | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BPTS | Bay - Pneumatic Tube Station | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BPTS | Bay - Pneumatic Tube Station | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | FFE | FQSN-001 | BASKET: drop in, pneumatic station | 1 | may be lockable depending on location, service and security requirements
BPTS | Bay - Pneumatic Tube Station | FFE | MMLA-072 | RACK: canister storage (pneumatic tube) | 1 | quantity to suit service requirements
BPTS | Bay - Pneumatic Tube Station | FFE | MMGE-097 | STATION: pneumatic tube | 1 | with audible alarm
BPTS | Bay - Pneumatic Tube Station | SE | LIFX-015 | LIGHT: pneumatic tube alert light | 1
BPTS | Bay - Pneumatic Tube Station | SE | ELGE-001 | DIRECT CONNECTION: power | 1 | direct connection to station
BRES | Bay - Resuscitation Trolley | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4 | coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BRES | Bay - Resuscitation Trolley | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BRES | Bay - Resuscitation Trolley | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 3 | crash rails are also acceptable
BRES | Bay - Resuscitation Trolley | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 1 | optional
BRES | Bay - Resuscitation Trolley | FFE | MMBE-042 | SLIDE: patient | 1 | optional
BRES | Bay - Resuscitation Trolley | FFE | MMHA-027 | TROLLEY: resuscitation, adult | 1 | type dependent on service requirements
BRES | Bay - Resuscitation Trolley | FFE | MMHA-016 | SUCTION: TWIN-O-VAC UNIT | 1
BRES | Bay - Resuscitation Trolley | FFE | MMHA-002 | DEFIBRILLATOR | 1
BRES | Bay - Resuscitation Trolley | FFE | FIHR-090 | BRACKET: for oxygen cylinder, trolley mounted | 1 | optional
BRES | Bay - Resuscitation Trolley | FFE | MMHA-033 | CYLINDER: gas, oxygen | 1 | optional
BRES | Bay - Resuscitation Trolley | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2
BVM | Bay - Vending Machine | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BVM | Bay - Vending Machine | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4 | coordinated with adjacent area
BVM | Bay - Vending Machine | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
BVM | Bay - Vending Machine | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BVM | Bay - Vending Machine | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | coordinated with adjacent area
BVM | Bay - Vending Machine | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BVM | Bay - Vending Machine | FFE | FQCA-055 | MACHINE: vending, cold, drinks | 1 | quantity and type of machine dependent on service requirements
BVM | Bay - Vending Machine | FFE | FQCA-057 | MACHINE: vending, snacks | 1 | quantity and type of machine dependent on service requirements
BVM | Bay - Vending Machine | FFE | FIJO-212 | BULKHEAD: joinery | 1 | optional
BVM | Bay - Vending Machine | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 to each vending machine
BVM | Bay - Vending Machine | SE | ELGP-109 | GPO: single, wall mounted | 2 | 1 to each vending machine
BWC | Bay - Wheelchair Park | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area
BWC | Bay - Wheelchair Park | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4 | coordinated with adjacent area
BWC | Bay - Wheelchair Park | FA | WLPR-006 | WALL PROTECTION: corner guards | 1 | coordinated with adjacent wall protection
BWC | Bay - Wheelchair Park | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
BWC | Bay - Wheelchair Park | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 3 | crash rails are also acceptable
BWC | Bay - Wheelchair Park | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 | coordinated with adjacent area
BWC | Bay - Wheelchair Park | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BWC | Bay - Wheelchair Park | FFE | MMBE-045 | WHEELCHAIR | 2 | quantity to suit service requirements
BWC | Bay - Wheelchair Park | FFE | MMBE-050 | WHEELCHAIR: bariatric | 1 | quantity to suit service requirements
BWC | Bay - Wheelchair Park | SE | ELGP-208 | GPO: double, wall mounted | 1 | optional
BWTR | Bay - Water Fountain | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
BWTR | Bay - Water Fountain | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | floor finish of adjacent area must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under water dispenser. significant change in colour to be avoided.
BWTR | Bay - Water Fountain | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BWTR | Bay - Water Fountain | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | coordinated with adjacent area
BWTR | Bay - Water Fountain | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 1
BWTR | Bay - Water Fountain | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
BWTR | Bay - Water Fountain | FFE | FQCW-016 | BIN: waste, general, 20L | 1
BWTR | Bay - Water Fountain | FFE | HYGE-011 | CHILLED WATER UNIT: fixed | 1
BWTR | Bay - Water Fountain | FFE | FQCA-014 | DISPENSER: cup | 1
BWTR | Bay - Water Fountain | SE | ELGP-111 | GPO: single, wall mounted, RCD protected | 1 | optional, for refrigerated units only
CHPT | Change Cubicle - Patient | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CHPT | Change Cubicle - Patient | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
CHPT | Change Cubicle - Patient | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
CHPT | Change Cubicle - Patient | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
CHPT | Change Cubicle - Patient | FA | CLFS-002 | CEILING: fibre cement, flush set, suspended, paint, washable | 1 | drop-in tile ceiling is also acceptable
CHPT | Change Cubicle - Patient | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening, with privacy latch; cubicle partition system or curtain track with privacy curtain are also acceptable
CHPT | Change Cubicle - Patient | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CHPT | Change Cubicle - Patient | FFE | FIGE-003 | BENCH SEAT: fixed, indoor | 1 | colour of seating to contrast with flooring and walls as per AS1428 luminance contrast requirements
CHPT | Change Cubicle - Patient | FFE | FIHR-026 | HOOK: coat | 2
CHPT | Change Cubicle - Patient | FFE | FIRT-006 | GRAB RAIL: WC | 1 | L-shaped grabrail
CHPT | Change Cubicle - Patient | FFE | FIBM-005 | MIRROR: fixed, glass, 1200H nom. | 1
CHPT | Change Cubicle - Patient | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | with indicator button and light
CHPT | Change Cubicle - Patient | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | with indicator button and light, low for access from seated position or floor
CHPT | Change Cubicle - Patient | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
CHPT | Change Cubicle - Patient | SE | ITSE-044 | SENSOR: motion detection, for lighting control | 1 | light switch is also acceptable
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | Default= vinyl, carpet also acceptable
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | Feather edged vinyl if carpeted
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | To be decided at project level.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | WLWA-007 | WALL FINISH: splashback | 1 | To basin. Selection of material to comply with Part D Infection Prevention and Control AusHFG.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional, 910mm outward opening, privacy latch, with emergency release
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIGE-003 | BENCH SEAT: fixed, indoor | 1 | To change cubicle. Or chair, consider weight capacity.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | WLPT-001 | PARTITION: change cubicle | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 | Optional
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIHR-026 | HOOK: coat | 2
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIDI-030 | DISPENSER: soap | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | MMGE-122 | TROLLEY: gowns | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIRT-006 | GRAB RAIL: WC | 2 | Ambulant provision.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FQSN-048 | LOCKER: 2 tier (half size) | 4 | 16 half lockers or quarter lockers.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FQSN-050 | LOCKER: 4 tier (quarter size) | 2
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 | To Female Change Rooms. Optional, depends on Waste Management Policy.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | FIJO-191 | SHELF: above basin | 1 | Or integrated with basin.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | WLPT-005 | PARTITION: toilet | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | HYBA-011 | BASIN: handwash, Type C | 1 | With vanity, or ensuite basin with integral shelf for patient belongings.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 | to basin
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | SE | HYDR-004 | DRAIN: floor waste | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | SE | ELBO-015 | SWITCH: light, single | 1
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light. WC and change cubicle.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | Optional.
CHPT-AC | Change Cubicle - Patient, Accessible | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CHPT-AC | Change Cubicle - Patient, Accessible | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
CHPT-AC | Change Cubicle - Patient, Accessible | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
CHPT-AC | Change Cubicle - Patient, Accessible | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
CHPT-AC | Change Cubicle - Patient, Accessible | FA | CLFS-002 | CEILING: fibre cement, flush set, suspended, paint, washable | 1 | drop-in tile ceiling is also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening, with accessible privacy latch; cubicle system or curtain track with privacy curtain are also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CHPT-AC | Change Cubicle - Patient, Accessible | FFE | FIGE-003 | BENCH SEAT: fixed, indoor | 1 | colour of seating to contrast with flooring and walls as per AS1428.1 luminance contrast requirements
CHPT-AC | Change Cubicle - Patient, Accessible | FFE | FIHR-026 | HOOK: coat | 2 | 1 mounted at accessible height to AS1428.1 requirements
CHPT-AC | Change Cubicle - Patient, Accessible | FFE | FIRT-006 | GRAB RAIL: WC | 1 | L-shaped grabrail
CHPT-AC | Change Cubicle - Patient, Accessible | FFE | FIBM-006 | MIRROR: fixed, glass | 1
CHPT-AC | Change Cubicle - Patient, Accessible | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | with indicator button and light
CHPT-AC | Change Cubicle - Patient, Accessible | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | with indicator button and light, low for access from seated position or floor
CHPT-AC | Change Cubicle - Patient, Accessible | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
CHPT-AC | Change Cubicle - Patient, Accessible | SE | ITSE-044 | SENSOR: motion detection, for lighting control | 1 | light switch is also acceptable
CHST-10 | Change - Staff, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 12 | to be tiles if tiled floor
CHST-10 | Change - Staff, 10m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
CHST-10 | Change - Staff, 10m2 | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
CHST-10 | Change - Staff, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 6
CHST-10 | Change - Staff, 10m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | water resistant ceiling tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | FA | DWSC-001 | DOOR: 850mm c/o, single leaf, solid core, paint | 1 | with closer as required for privacy
CHST-10 | Change - Staff, 10m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CHST-10 | Change - Staff, 10m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 4 | to shower; tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | FFE | FIGE-003 | BENCH SEAT: fixed, indoor | 2 | 1 x to shower, material to be suitable for wet areas
CHST-10 | Change - Staff, 10m2 | FFE | FIHR-026 | HOOK: coat | 4 | 2 x to changing area optional; quantity to be based on staffing and service requirements
CHST-10 | Change - Staff, 10m2 | FFE | FIRT-033 | TRACK: curtain, shower | 1 | optional
CHST-10 | Change - Staff, 10m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | optional
CHST-10 | Change - Staff, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CHST-10 | Change - Staff, 10m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CHST-10 | Change - Staff, 10m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 x to basin, 1 x to shower
CHST-10 | Change - Staff, 10m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1
CHST-10 | Change - Staff, 10m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CHST-10 | Change - Staff, 10m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | to basin
CHST-10 | Change - Staff, 10m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 | optional, to toilet in female change rooms
CHST-10 | Change - Staff, 10m2 | FFE | WLPT-004 | PARTITION: shower | 1
CHST-10 | Change - Staff, 10m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 | optional, to shower
CHST-10 | Change - Staff, 10m2 | FFE | WLPT-005 | PARTITION: toilet | 1 | lift off hinges to inward opening sanitary compartment doors
CHST-10 | Change - Staff, 10m2 | FFE | HYBA-012 | BASIN: handwash, Type C, with vanity unit | 1
CHST-10 | Change - Staff, 10m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
CHST-10 | Change - Staff, 10m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
CHST-10 | Change - Staff, 10m2 | FFE | HYTP-018 | SHOWER: fixed rose | 1
CHST-10 | Change - Staff, 10m2 | FFE | HYWC-008 | TOILET SUITE: standard | 1 | with 100mm clearout access point
CHST-10 | Change - Staff, 10m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1 | optional, over lockers, plasterboard bulkhead is also acceptable
CHST-10 | Change - Staff, 10m2 | FFE | FQSN-054 | LOCKER: 2 tier with shoe storage | 2
CHST-10 | Change - Staff, 10m2 | FFE | FQSN-055 | LOCKER: 4 tier with shoe storage | 2
CHST-10 | Change - Staff, 10m2 | SE | HYDR-004 | DRAIN: floor waste | 1
CHST-10 | Change - Staff, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
CHST-10 | Change - Staff, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
CHST-10 | Change - Staff, 10m2 | SE | ITSE-038 | READER: access control, general | 1 | to entry door from corridor
CHST-35 | Change - Staff, 35m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 33 | to be tiles if tiled floor
CHST-35 | Change - Staff, 35m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
CHST-35 | Change - Staff, 35m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 2
CHST-35 | Change - Staff, 35m2 | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basins
CHST-35 | Change - Staff, 35m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 16
CHST-35 | Change - Staff, 35m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | water resistant ceiling tiles are also acceptable
CHST-35 | Change - Staff, 35m2 | FA | DWSC-001 | DOOR: 850mm c/o, single leaf, solid core, paint | 2 | with closer as required for privacy
CHST-35 | Change - Staff, 35m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CHST-35 | Change - Staff, 35m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 8 | to shower; tiles are also acceptable
CHST-35 | Change - Staff, 35m2 | FFE | ITNE-052 | TELEPHONE: handset, wall mount | 1 | optional
CHST-35 | Change - Staff, 35m2 | FFE | FIGE-003 | BENCH SEAT: fixed, indoor | 2 | to showers, material to be suitable for wet areas
CHST-35 | Change - Staff, 35m2 | FFE | FQBS-007 | BENCH SEAT: freestanding, indoor | 1
CHST-35 | Change - Staff, 35m2 | FFE | FIHR-026 | HOOK: coat | 16 | optional, quantity and configuration to be determined to suit operational requirements
CHST-35 | Change - Staff, 35m2 | FFE | FIRT-033 | TRACK: curtain, shower | 2 | optional
CHST-35 | Change - Staff, 35m2 | FFE | FQGE-011 | CURTAIN: shower | 2 | optional
CHST-35 | Change - Staff, 35m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 2 | to basins
CHST-35 | Change - Staff, 35m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basins
CHST-35 | Change - Staff, 35m2 | FFE | FIDI-030 | DISPENSER: soap | 4 | 2 x to basins, 2 x to showers
CHST-35 | Change - Staff, 35m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 3
CHST-35 | Change - Staff, 35m2 | FFE | FIRT-006 | GRAB RAIL: WC | 2 | to ambulant toilet
CHST-35 | Change - Staff, 35m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 2
CHST-35 | Change - Staff, 35m2 | FFE | MMGE-109 | TROLLEY: clean linen | 1
CHST-35 | Change - Staff, 35m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | to basins
CHST-35 | Change - Staff, 35m2 | FFE | FIBM-007 | MIRROR: fixed, glass, full length | 1
CHST-35 | Change - Staff, 35m2 | FFE | FQCW-037 | BIN: waste, sanitary | 3 | optional, to toilets in female change rooms
CHST-35 | Change - Staff, 35m2 | FFE | WLPT-004 | PARTITION: shower | 2
CHST-35 | Change - Staff, 35m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 2 | optional, to showers
CHST-35 | Change - Staff, 35m2 | FFE | WLPT-005 | PARTITION: toilet | 2 | lift off hinges to inward opening sanitary compartment doors
CHST-35 | Change - Staff, 35m2 | FFE | HYBA-012 | BASIN: handwash, Type C, with vanity unit | 2
CHST-35 | Change - Staff, 35m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 2
CHST-35 | Change - Staff, 35m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2
CHST-35 | Change - Staff, 35m2 | FFE | HYTP-018 | SHOWER: fixed rose | 2
CHST-35 | Change - Staff, 35m2 | FFE | HYWC-008 | TOILET SUITE: standard | 2 | with 100mm clearout access point
CHST-35 | Change - Staff, 35m2 | FFE | HYWC-010 | TOILET SUITE: ambulant | 1 | with 100mm clearout access point
CHST-35 | Change - Staff, 35m2 | FFE | FIJO-212 | BULKHEAD: joinery | 3 | optional, over lockers, plasterboard bulkhead is also acceptable
CHST-35 | Change - Staff, 35m2 | FFE | WLPT-016 | PARTITION: toilet, ambulant | 1
CHST-35 | Change - Staff, 35m2 | FFE | FQSN-054 | LOCKER: 2 tier with shoe storage | 6
CHST-35 | Change - Staff, 35m2 | FFE | FQSN-055 | LOCKER: 4 tier with shoe storage | 17
CHST-35 | Change - Staff, 35m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, to wall phone if provided
CHST-35 | Change - Staff, 35m2 | SE | HYDR-004 | DRAIN: floor waste | 3
CHST-35 | Change - Staff, 35m2 | SE | ELBO-015 | SWITCH: light, single | 2
CHST-35 | Change - Staff, 35m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
CHST-35 | Change - Staff, 35m2 | SE | ITSE-038 | READER: access control, general | 2 | to entry door from corridor
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | at 3000 mm AFFL
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | to control room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWGL-006 | DOOR: 910mm c/o, single leaf, observation panel, solid core/lead glass, lead shielding, paint | 2 | staff access to sterile stock/ scrub areas
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MGFP-002 | FLOWMETER: medical air | 3 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIHR-019 | BRACKET: for suction bottle | 4 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | wall mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-119 | TROLLEY: equipment | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 | for slave monitor
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-122 | TROLLEY: gowns | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-045 | IV STAND: mobile | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MGFP-004 | FLOWMETER: oxygen | 4 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1 | under bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMHA-027 | TROLLEY: resuscitation, adult | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-088 | SAFE: dangerous drugs, small | 1 | optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-142 | TROLLEY: sharps bin | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FQBS-052 | STOOL: mobile, high, adj height | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-002 | ADAPTER: suction | 4 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-100 | SUCTION BOTTLE | 4 | on pendant mounted brackets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMOP-040 | MACHINE: anaesthetic with integral monitors | 1 | optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMSP-015 | PENDANT: single, anaesthetic (fixed or adjustable height) | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | ITCL-021 | CLOCK: clock system slave dual time / elapsed time | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMHA-002 | DEFIBRILLATOR | 1 | on resus trolley
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMSP-029 | LIGHT: operating, single, 550 diam nom. | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1 | on wall bracket
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMSP-018 | PENDANT: single, wet and dry combination (fixed or adjustable height) | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-329 | DEVICE: imaging, ultrasound scanning unit | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-100 | INJECTOR: contrast, CT | 1 | optionally can be on table or ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-212 | BULKHEAD: joinery | 1 | over cupboards
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-377 | WARMER: contrast | 1 | on bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-385 | SYSTEM: imaging, cath lab, dual plane, ceiling | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-389 | TABLE: operating, fixed, narrow table plate, cath lab, dual plane | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-390 | SHIELD: radiation, upper body, mobile, cath lab | 2 | ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-396 | DISPLAY SCREEN: cath lab, multi modality | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-220 | CUPBOARD: tall, double door, glazed, catheter hanging | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-398 | SYSTEM: electrophysiology, cath lab | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-400 | STAND: ceiling, with traverse bridge, cath lab | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-221 | CUPBOARD: tall, double door, glazed | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | handsfree to control room, outside room, to control room, delete from room list if listed in adjacent accessway
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELPR-006 | RCD: residual current device | 4 | 1 to each pendant, 1 for wall mounted outlets and 1 for floor box outlets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 1 | under table
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-003 | CONTROL PANEL: lighting | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-001 | BUTTON: emergency stop | 1 | optional, for equipment shut-off
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | LIFX-008 | LIGHT: task light, built in | 2 | over bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 3 | outside all entry points. Delete from room list if listed in adjacent room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGFP-001 | ALARM PANEL: medical gases | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | 2 above bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 9
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELPR-004 | MONITOR: line isolation | 2 | 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors as specified
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITCL-023 | CONTROL PANEL: master clock system | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-012 | SWITCH: light, dimmer | 4
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-024 | OUTLET: data, double RJ45, on pendant | 2 | on pendant, 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 3 | on pendant, 2 to EP pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 2 | on pendant, 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on pendant, 2 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on pendant, 2 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-051 | OUTLET: scavenge, on pendant | 2 | on pendant, 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on pendant, 2 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-121 | GPO: emergency power, single, on pendant | 16 | on pendant, 8 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-225 | GPO: emergency power, double, in floorbox | 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MEEX-016 | RETURN AIR: grille, low level | 4
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELPR-007 | UPS: status indicator | 2
CLAB-I | Catheter Laboratory - Interventional | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CLAB-I | Catheter Laboratory - Interventional | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 18
CLAB-I | Catheter Laboratory - Interventional | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
CLAB-I | Catheter Laboratory - Interventional | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
CLAB-I | Catheter Laboratory - Interventional | FA | WLWA-005 | WALL FINISH: paint, scrub resistant | 5
CLAB-I | Catheter Laboratory - Interventional | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | at 3000 mm AFFL
CLAB-I | Catheter Laboratory - Interventional | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | to control room
CLAB-I | Catheter Laboratory - Interventional | FA | DWGL-006 | DOOR: 910mm c/o, single leaf, observation panel, solid core/lead glass, lead shielding, paint | 2 | staff access to sterile stock/ scrub areas, with sliding cover for privacy
CLAB-I | Catheter Laboratory - Interventional | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
CLAB-I | Catheter Laboratory - Interventional | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLAB-I | Catheter Laboratory - Interventional | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 20
CLAB-I | Catheter Laboratory - Interventional | FFE | MGFP-002 | FLOWMETER: medical air | 1 | on pendant/s
CLAB-I | Catheter Laboratory - Interventional | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | on pendant/s
CLAB-I | Catheter Laboratory - Interventional | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
CLAB-I | Catheter Laboratory - Interventional | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | wall mounted
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-119 | TROLLEY: equipment | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 | for slave monitor
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-122 | TROLLEY: gowns | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-045 | IV STAND: mobile | 2
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | on pendant/s
CLAB-I | Catheter Laboratory - Interventional | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1 | under bench
CLAB-I | Catheter Laboratory - Interventional | FFE | MMHA-027 | TROLLEY: resuscitation, adult | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-088 | SAFE: dangerous drugs, small | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-142 | TROLLEY: sharps bin | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | FQBS-052 | STOOL: mobile, high, adj height | 2
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-002 | ADAPTER: suction | 2 | on pendant/s
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-100 | SUCTION BOTTLE | 2 | on pendant mounted brackets
CLAB-I | Catheter Laboratory - Interventional | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 3
CLAB-I | Catheter Laboratory - Interventional | FFE | MMSP-015 | PENDANT: single, anaesthetic (fixed or adjustable height) | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 2
CLAB-I | Catheter Laboratory - Interventional | FFE | MMHA-002 | DEFIBRILLATOR | 1 | on resus trolley
CLAB-I | Catheter Laboratory - Interventional | FFE | MMSP-029 | LIGHT: operating, single, 550 diam nom. | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1 | on wall bracket
CLAB-I | Catheter Laboratory - Interventional | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-329 | DEVICE: imaging, ultrasound scanning unit | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 2
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-108 | INJECTOR: contrast, table mounted | 1 | optionally can be mobile or ceiling mounted
CLAB-I | Catheter Laboratory - Interventional | FFE | FIJO-212 | BULKHEAD: joinery | 1 | over cupboards
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-377 | WARMER: contrast | 1 | on bench
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-387 | SYSTEM: imaging, cath lab, single plane, ceiling | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-388 | TABLE: operating, fixed, narrow, cath lab, single plane | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-390 | SHIELD: radiation, upper body, mobile, cath lab | 1 | ceiling mounted
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-396 | DISPLAY SCREEN: cath lab, multi modality | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | FIJO-220 | CUPBOARD: tall, double door, glazed, catheter hanging | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | MMMI-400 | STAND: ceiling, with traverse bridge, cath lab | 1
CLAB-I | Catheter Laboratory - Interventional | FFE | FIJO-221 | CUPBOARD: tall, double door, glazed | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
CLAB-I | Catheter Laboratory - Interventional | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3
CLAB-I | Catheter Laboratory - Interventional | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | handsfree to control room
CLAB-I | Catheter Laboratory - Interventional | SE | ELPR-006 | RCD: residual current device | 3 | 1 to pendant, 1 for wall mounted outlets, 1 for floor box outlets
CLAB-I | Catheter Laboratory - Interventional | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 1 | under table
CLAB-I | Catheter Laboratory - Interventional | SE | ELBO-003 | CONTROL PANEL: lighting | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | to wall, + indicator button & light
CLAB-I | Catheter Laboratory - Interventional | SE | ELBO-001 | BUTTON: emergency stop | 1 | optional, for equipment shut-off
CLAB-I | Catheter Laboratory - Interventional | SE | LIFX-008 | LIGHT: task light, built in | 2 | over bench
CLAB-I | Catheter Laboratory - Interventional | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 3 | outside all entry points, delete from room list if listed in adjacent room
CLAB-I | Catheter Laboratory - Interventional | SE | MGFP-001 | ALARM PANEL: medical gases | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | to wall, + indicator button & light
CLAB-I | Catheter Laboratory - Interventional | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3 | 2 above bench
CLAB-I | Catheter Laboratory - Interventional | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 9
CLAB-I | Catheter Laboratory - Interventional | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ELPR-004 | MONITOR: line isolation | 1 | 1 to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
CLAB-I | Catheter Laboratory - Interventional | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors as specified
CLAB-I | Catheter Laboratory - Interventional | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ELBO-012 | SWITCH: light, dimmer | 4
CLAB-I | Catheter Laboratory - Interventional | SE | ITIN-024 | OUTLET: data, double RJ45, on pendant | 1 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | MGAS-061 | OUTLET: suction, on pendant | 2 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | ELGP-132 | GPO: UPS, single, on pendant | 2 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | ELGP-121 | GPO: emergency power, single, on pendant | 8 | to pendant
CLAB-I | Catheter Laboratory - Interventional | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
CLAB-I | Catheter Laboratory - Interventional | SE | ELGP-225 | GPO: emergency power, double, in floorbox | 3
CLAB-I | Catheter Laboratory - Interventional | SE | MEEX-016 | RETURN AIR: grille, low level | 4
CLAB-I | Catheter Laboratory - Interventional | SE | ELPR-007 | UPS: status indicator | 1
CLCR-EP | Catheter Laboratory EP Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CLCR-EP | Catheter Laboratory EP Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
CLCR-EP | Catheter Laboratory EP Control Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CLCR-EP | Catheter Laboratory EP Control Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
CLCR-EP | Catheter Laboratory EP Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CLCR-EP | Catheter Laboratory EP Control Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
CLCR-EP | Catheter Laboratory EP Control Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | to procedure room
CLCR-EP | Catheter Laboratory EP Control Room | FA | DWGL-002 | DOOR: 910mm c/o, single leaf, half glazed, solid core/glass, paint | 1
CLCR-EP | Catheter Laboratory EP Control Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 4
CLCR-EP | Catheter Laboratory EP Control Room | FFE | DWWD-004 | BLIND: roller | 1 | to observation window for patient privacy; refer to local infection control policies
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 2
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITBU-013 | DISPLAY SCREEN: patient flow system | 1 | patient journey board
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITNE-023 | PRINTER: networked | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1 | optional
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2 | on bench, 1 cordless optional
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 2 | part of communications system integrated with imaging system
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 2
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FIJO-099 | CAC: cable access cap | 6
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | for reporting station
CLCR-EP | Catheter Laboratory EP Control Room | FFE | MMMI-369 | DISPLAY SCREEN: contrast injector | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FIHR-070 | BRACKET: for display screen, dual, desk mounted | 2 | for reporting station
CLCR-EP | Catheter Laboratory EP Control Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | MMMI-386 | CONTROL UNIT: c/w display, control box and keyboard, Cath Lab | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | MMMI-392 | DISPLAY SCREEN: DCS, cath lab | 1 | haemodynamic monitoring display
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 2
CLCR-EP | Catheter Laboratory EP Control Room | FFE | MMMI-397 | COMPUTER: control, c/w dual display & keyboard, 3D mapping | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | MMMI-399 | SYSTEM: electrophysiology recording, c/w display screens | 1
CLCR-EP | Catheter Laboratory EP Control Room | FFE | MMGE-182 | MACHINE: Electrophysiology, cardiac pacing | 1
CLCR-EP | Catheter Laboratory EP Control Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 4
CLCR-EP | Catheter Laboratory EP Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 6 | 2 outlets for telephone
CLCR-EP | Catheter Laboratory EP Control Room | SE | ELPR-006 | RCD: residual current device | 4
CLCR-EP | Catheter Laboratory EP Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1 | optional
CLCR-EP | Catheter Laboratory EP Control Room | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | for control room temperature, optional
CLCR-EP | Catheter Laboratory EP Control Room | SE | MGFP-001 | ALARM PANEL: medical gases | 1
CLCR-EP | Catheter Laboratory EP Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 7
CLCR-EP | Catheter Laboratory EP Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CLCR-EP | Catheter Laboratory EP Control Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3
CLCR-EP | Catheter Laboratory EP Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
CLCR-EP | Catheter Laboratory EP Control Room | SE | ELGP-130 | GPO: UPS, single | 15
CLCR-I | Catheter Laboratory Interventional Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
CLCR-I | Catheter Laboratory Interventional Control Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CLCR-I | Catheter Laboratory Interventional Control Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
CLCR-I | Catheter Laboratory Interventional Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CLCR-I | Catheter Laboratory Interventional Control Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | to procedure room
CLCR-I | Catheter Laboratory Interventional Control Room | FA | DWGL-002 | DOOR: 910mm c/o, single leaf, half glazed, solid core/glass, paint | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FA | DWGL-006 | DOOR: 910mm c/o, single leaf, observation panel, solid core/lead glass, lead shielding, paint | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 3
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | DWWD-004 | BLIND: roller | 1 | to observation window for patient privacy; refer to local infection control policies
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITBU-013 | DISPLAY SCREEN: patient flow system | 1 | patient journey board
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITNE-009 | COMPUTER: hi performance, for clinical / PACS use | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITNE-023 | PRINTER: networked | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1 | optional
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2 | on bench, 1 cordless optional
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 2 | part of communications system integrated with imaging system
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 2
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIJO-099 | CAC: cable access cap | 5
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | for reporting station
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | MMMI-369 | DISPLAY SCREEN: contrast injector | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIHR-070 | BRACKET: for display screen, dual, desk mounted | 1
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 3
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | MMMI-386 | CONTROL UNIT: c/w display, control box and keyboard, Cath Lab | 2
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 3
CLCR-I | Catheter Laboratory Interventional Control Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 2
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 6 | 2 outlets for telephone
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ELPR-006 | RCD: residual current device | 3
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1 | optional
CLCR-I | Catheter Laboratory Interventional Control Room | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | for control room temperature, optional
CLCR-I | Catheter Laboratory Interventional Control Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1
CLCR-I | Catheter Laboratory Interventional Control Room | SE | MGFP-001 | ALARM PANEL: medical gases | 1
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 8
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
CLCR-I | Catheter Laboratory Interventional Control Room | SE | ELGP-130 | GPO: UPS, single | 7
CLN-10 | Clean Store, 10m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CLN-10 | Clean Store, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
CLN-10 | Clean Store, 10m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
CLN-10 | Clean Store, 10m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
CLN-10 | Clean Store, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CLN-10 | Clean Store, 10m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
CLN-10 | Clean Store, 10m2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
CLN-10 | Clean Store, 10m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLN-10 | Clean Store, 10m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 5 | extent dependent on type and height storage solution
CLN-10 | Clean Store, 10m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CLN-10 | Clean Store, 10m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
CLN-10 | Clean Store, 10m2 | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 2 | remove if desk provided in lieu of bench
CLN-10 | Clean Store, 10m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | desk is also acceptable
CLN-10 | Clean Store, 10m2 | FFE | FQSM-046 | SHELVING: storage solution, 600W x 400D x 2100H nom., wire, mobile | 5 | type and quantity of storage options to be determined based on service requirements
CLN-10 | Clean Store, 10m2 | FFE | FQSM-048 | SHELVING: storage solution, shelving, 600W x 400D x 2100H nom., wire, mobile | 2 | type and quantity of storage options to be determined based on service requirements
CLN-10 | Clean Store, 10m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
CLN-10 | Clean Store, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
CLN-10 | Clean Store, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 3 | extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 3 | extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | MMGE-087 | SAFE: dangerous drugs, medium | 1 | size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 8
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | ITSE-012 | CAMERA: CCTV | 1 | optional, provision and placement dependent on local policies
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | MMGE-034 | FRIDGE: drugs, large | 1 | size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQSM-046 | SHELVING: storage solution, 600W x 400D x 2100H nom., wire, mobile | 5 | type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQCW-061 | BIN: waste, pharmaceutical | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQSM-048 | SHELVING: storage solution, shelving, 600W x 400D x 2100H nom., wire, mobile | 4 | type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-052 | DISPENSER: sticker roll | 1 | optional
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to drug fridge, for temperature monitoring
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 2 x optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | LIFX-008 | LIGHT: task light, built in | 2 | under wall mounted joinery
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELBO-015 | SWITCH: light, single | 1 | to task light
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELBO-010 | SWITCH: light, 2-way | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to drug fridge
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ITSE-038 | READER: access control, general | 2
CLN-MED-S | Clean Store / Medication Room, Sub | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CLN-MED-S | Clean Store / Medication Room, Sub | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 11
CLN-MED-S | Clean Store / Medication Room, Sub | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CLN-MED-S | Clean Store / Medication Room, Sub | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CLN-MED-S | Clean Store / Medication Room, Sub | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 4 | extent dependent on type and height storage solution
CLN-MED-S | Clean Store / Medication Room, Sub | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1 | extent dependent on type and height storage solution
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIJO-140 | CUPBOARD: underbench, single door, adj shelves | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | MMGE-087 | SAFE: dangerous drugs, medium | 1 | size and quantity to be based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 2
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | ITSE-012 | CAMERA: CCTV | 1 | optional, provision and placement dependent on local policies
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | MMGE-036 | FRIDGE: drugs, underbench | 1 | size and quantity to be based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FQSM-046 | SHELVING: storage solution, 600W x 400D x 2100H nom., wire, mobile | 3 | type and quantity of storage options to be determined based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FQCW-061 | BIN: waste, pharmaceutical | 1
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FQSM-048 | SHELVING: storage solution, shelving, 600W x 400D x 2100H nom., wire, mobile | 2 | type and quantity of storage options to be determined based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | FFE | FIDI-052 | DISPENSER: sticker roll | 1 | optional
CLN-MED-S | Clean Store / Medication Room, Sub | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to drug fridge, for temperature monitoring
CLN-MED-S | Clean Store / Medication Room, Sub | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1x optional, for future provision of automated dispensing cabinets
CLN-MED-S | Clean Store / Medication Room, Sub | SE | LIFX-008 | LIGHT: task light, built in | 1 | under wall mounted joinery
CLN-MED-S | Clean Store / Medication Room, Sub | SE | ELBO-015 | SWITCH: light, single | 2 | 1 x general room lighting, 1 x task light
CLN-MED-S | Clean Store / Medication Room, Sub | SE | ELGP-208 | GPO: double, wall mounted | 2
CLN-MED-S | Clean Store / Medication Room, Sub | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | optional, for future provision of automated dispensing cabinets
CLN-MED-S | Clean Store / Medication Room, Sub | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to drug fridge
CLN-MED-S | Clean Store / Medication Room, Sub | SE | ITSE-038 | READER: access control, general | 1
CLRM | Cleaner's Room | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
CLRM | Cleaner's Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
CLRM | Cleaner's Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
CLRM | Cleaner's Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
CLRM | Cleaner's Room | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
CLRM | Cleaner's Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable or secure staff-only access may be provided, hold open hardware may be required, optional vision panel
CLRM | Cleaner's Room | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1
CLRM | Cleaner's Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CLRM | Cleaner's Room | FFE | FQCW-045 | BUCKET: cleaner | 1 | on cleaner's trolley
CLRM | Cleaner's Room | FFE | FIHR-040 | RACK: broom/mop | 1
CLRM | Cleaner's Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CLRM | Cleaner's Room | FFE | FQSM-021 | TROLLEY: cleaner | 1
CLRM | Cleaner's Room | FFE | FIHR-026 | HOOK: coat | 2
CLRM | Cleaner's Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CLRM | Cleaner's Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CLRM | Cleaner's Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CLRM | Cleaner's Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CLRM | Cleaner's Room | FFE | FIDI-021 | DISPENSER: mask | 1 | optional, type of PPE dispensers to be provided to suit service requirements
CLRM | Cleaner's Room | FFE | FQCW-058 | MOP | 1
CLRM | Cleaner's Room | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1 | type and extent of storage to suit service requirements and operational policies for the decanting and storage of chemicals and consumables
CLRM | Cleaner's Room | FFE | HYBA-011 | BASIN: handwash, Type C | 1
CLRM | Cleaner's Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to cleaner's sink
CLRM | Cleaner's Room | FFE | FIDI-010 | DISPENSER: detergent/chemical mixer | 1
CLRM | Cleaner's Room | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 | to basin
CLRM | Cleaner's Room | FFE | HYBA-040 | SINK: cleaner | 1
CLRM | Cleaner's Room | FFE | FIDI-057 | DISPENSER: eye wash bottles | 1 | optional, provide as required depending chemical safety data sheets and WHS policies
CLRM | Cleaner's Room | SE | HYTP-008 | OUTLET: cold water | 1 | optional, provision dependent on detergent/chemical mixer requirements
CLRM | Cleaner's Room | SE | HYDR-004 | DRAIN: floor waste | 1
CLRM | Cleaner's Room | SE | ELBO-015 | SWITCH: light, single | 1
CLRM | Cleaner's Room | SE | ELGP-208 | GPO: double, wall mounted | 1 | quantity to suit equipment charging requirements
CLRM | Cleaner's Room | SE | ITSE-038 | READER: access control, general | 1 | optional, dependent on security requirements
CLUP-7 | Clean-Up Room, 7m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
CLUP-7 | Clean-Up Room, 7m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
CLUP-7 | Clean-Up Room, 7m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
CLUP-7 | Clean-Up Room, 7m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
CLUP-7 | Clean-Up Room, 7m2 | FA | WLWA-005 | WALL FINISH: paint, scrub resistant | 4
CLUP-7 | Clean-Up Room, 7m2 | FA | WLWA-021 | WALL FINISH: vinyl, to 1800 AFFL | 1
CLUP-7 | Clean-Up Room, 7m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
CLUP-7 | Clean-Up Room, 7m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
CLUP-7 | Clean-Up Room, 7m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FQSM-016 | TROLLEY | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FQCW-029 | BIN: waste, recycling, paper, 240L | 1 | optional
CLUP-7 | Clean-Up Room, 7m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | elbow action levers
CLUP-7 | Clean-Up Room, 7m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | 1 to sink, 1 to basin
CLUP-7 | Clean-Up Room, 7m2 | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | hot water
CLUP-7 | Clean-Up Room, 7m2 | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1
CLUP-7 | Clean-Up Room, 7m2 | FFE | FQCW-060 | BIN: waste, cytotoxic, 50L | 1 | optional
CLUP-7 | Clean-Up Room, 7m2 | FFE | MMIC-122 | DISINFECTOR: ultrasound probes | 1 | optional
CLUP-7 | Clean-Up Room, 7m2 | SE | HYDR-004 | DRAIN: floor waste | 1
CLUP-7 | Clean-Up Room, 7m2 | SE | ELBO-015 | SWITCH: light, single | 1
CLUP-7 | Clean-Up Room, 7m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
COMM | Communications Room | FA | FLVY-001 | FLOOR FINISH: vinyl, seamless, coved, anti-static | 1
COMM | Communications Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
COMM | Communications Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
COMM | Communications Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
COMM | Communications Room | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
COMM | Communications Room | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
COMM | Communications Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
COMM | Communications Room | FFE | ITNE-052 | TELEPHONE: handset, wall mount | 1
COMM | Communications Room | FFE | ITNE-005 | COMMS BOARD | 1 | to suit project requirements
COMM | Communications Room | FFE | ITIN-123 | RACK: communications | 1 | to suit project requirements
COMM | Communications Room | FFE | ITIN-128 | RACK: voice, intermediate distribution frame (IDF) | 1 | optional, to suit project requirements
COMM | Communications Room | FFE | ITIN-139 | COMPUTER: mainframe | 1 | to suit project requirements
COMM | Communications Room | FFE | ITNE-011 | COMPUTER: server | 1 | to suit project requirements
COMM | Communications Room | FFE | FQGE-095 | STEP: safety | 1
COMM | Communications Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to suit project requirements
COMM | Communications Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | to suit project requirements
COMM | Communications Room | SE | ELBO-015 | SWITCH: light, single | 1
COMM | Communications Room | SE | ELGP-208 | GPO: double, wall mounted | 3 | to suit project requirements
COMM | Communications Room | SE | ITSE-046 | SENSOR: motion detection, for staff alert | 1
COMM | Communications Room | SE | ITSE-038 | READER: access control, general | 1
COMM | Communications Room | SE | ITSE-020 | CONTROL PANEL: duress | 1 | optional, to suit project requirements
COMM | Communications Room | SE | ITBU-015 | HEAD END: IPTV | 1 | optional, to suit project requirements
COMM | Communications Room | SE | ITBU-016 | HEAD END: MATV | 1 | optional, to suit project requirements
COMM | Communications Room | SE | ELGP-235 | GPO: UPS, double, wall mounted | 4 | to suit project requirements, power may be wall mounted or delivered via ceiling mounted umbilicals for access depending on server selection.
CONS | Consult Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CONS | Consult Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
CONS | Consult Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CONS | Consult Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
CONS | Consult Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
CONS | Consult Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CONS | Consult Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 2 | to exam couch
CONS | Consult Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CONS | Consult Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | 1 1/2 leaf door is also acceptable as required
CONS | Consult Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 1 | to patient/visitor chairs
CONS | Consult Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CONS | Consult Room | FA | DWGL-077 | DOOR: 850mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional, second door for egress
CONS | Consult Room | FFE | MGFP-002 | FLOWMETER: medical air | 1 | optional, provide if medical air required
CONS | Consult Room | FFE | FIDI-003 | DISPENSER: bedroll | 1 | may be provided as an attachment to exam couch
CONS | Consult Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1 | optional, provide if suction required
CONS | Consult Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CONS | Consult Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
CONS | Consult Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CONS | Consult Room | FFE | FIHR-026 | HOOK: coat | 2
CONS | Consult Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
CONS | Consult Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1
CONS | Consult Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CONS | Consult Room | FFE | MMGE-030 | DIAGNOSTIC SET: portable | 1 | may be wall mounted/mobile on stand
CONS | Consult Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CONS | Consult Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CONS | Consult Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CONS | Consult Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CONS | Consult Room | FFE | FIBM-006 | MIRROR: fixed, glass | 1
CONS | Consult Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | optional, provide if oxygen required
CONS | Consult Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
CONS | Consult Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
CONS | Consult Room | FFE | MMGE-002 | ADAPTER: suction | 1 | optional, provide if suction required
CONS | Consult Room | FFE | MMGE-100 | SUCTION BOTTLE | 1 | optional, provide if suction required
CONS | Consult Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
CONS | Consult Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CONS | Consult Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CONS | Consult Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | high resolution monitor for PACS viewing
CONS | Consult Room | FFE | MMBE-023 | COUCH: examination, electric, mobile | 1 | hi/low operation
CONS | Consult Room | FFE | LIFX-026 | LIGHT: examination, wall mounted | 1 | may be ceiling mounted
CONS | Consult Room | FFE | ITNE-023 | PRINTER: networked | 1 | optional
CONS | Consult Room | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
CONS | Consult Room | FFE | FQDW-037 | DESK: adj height, 1500W x 750D x 750H nom. | 1
CONS | Consult Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
CONS | Consult Room | FFE | FQBS-058 | CHAIR: visitor, patient, with arms | 3 | consider weight capacity of chairs
CONS | Consult Room | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | to desk
CONS | Consult Room | SE | ELPR-006 | RCD: residual current device | 3
CONS | Consult Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
CONS | Consult Room | SE | ELBO-015 | SWITCH: light, single | 2 | 1 to exam light
CONS | Consult Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional
CONS | Consult Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional
CONS | Consult Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional
CONS | Consult Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1
CONS | Consult Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
CONS | Consult Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for electric couch
CONS | Consult Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | for exam light
CONS | Consult Room | SE | ELGP-208 | GPO: double, wall mounted | 3 | 2x below desk, 1x above desk
CONS | Consult Room | SE | ITSE-006 | BUTTON: duress, fixed | 1 | in discreet location easily accessible by staff
CONS | Consult Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
CONS | Consult Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
CONS | Consult Room | SE | ELGP-205 | GPO: double, on services panel | 1
CONS | Consult Room | SE | ELGP-222 | GPO: emergency power, double, on services panel | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to hand wash basin 2100mm high
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | DWGL-007 | DOOR: 910mm c/o, single leaf, observation panel, solid core/safety glass, paint | 2
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MGFP-002 | FLOWMETER: medical air | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIHR-019 | BRACKET: for suction bottle | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 2 | consider weight capacity of chair
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIHR-026 | HOOK: coat | 2 | optional
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQGE-010 | CURTAIN: privacy screen | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to hand basin
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIDI-014 | DISPENSER: disposable glove | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to hand basin
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIDI-030 | DISPENSER: soap | 1 | to hand basin
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to hand basin
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMGE-113 | TROLLEY: dressing | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIHR-011 | BRACKET: for monitor, wall mounted | 1 | optional
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MGFP-004 | FLOWMETER: oxygen | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | wall mounted
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQBS-051 | STOOL: mobile, adj height | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMGE-002 | ADAPTER: suction | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMGE-100 | SUCTION BOTTLE | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQSM-003 | PEDESTAL: mobile, wire basket unit, 840H | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | ITNE-009 | COMPUTER: hi performance, for clinical / PACS use | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMHA-005 | MONITOR: patient, cardiac | 1 | optional
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMAH-013 | DEVICE: eye examination, slit lamp | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1 | to desk
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FIJO-010 | BENCH: 450D, open under | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMGE-171 | BOTTLE: eyewash, portable | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMGE-173 | PROJECTOR: visual acuity testing, surface mounted | 1 | project on wall, automated chart sizing
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | MMGE-174 | CHAIR: patient, ENT, electric | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | FFE | ITCL-034 | CAMERA: telemedicine | 1 | optional
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, to cardiac monitor
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | outlet for telephone, PC, telemedicine camera, slit lamp
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELPR-006 | RCD: residual current device | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | + indicator button & light
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, for paediatric use
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, for paediatric use
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-062 | OUTLET: suction, on services panel | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | + indicator button & light
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELGP-223.1 | GPO: emergency power, double, wall mounted (V) | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3 | optional, to cardiac monitor
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ITSE-006 | BUTTON: duress, fixed | 1 | optional
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELBO-012 | SWITCH: light, dimmer | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
CONS-UN | Consult Room - Universal Access | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CONS-UN | Consult Room - Universal Access | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
CONS-UN | Consult Room - Universal Access | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CONS-UN | Consult Room - Universal Access | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
CONS-UN | Consult Room - Universal Access | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
CONS-UN | Consult Room - Universal Access | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
CONS-UN | Consult Room - Universal Access | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 | to exam couch
CONS-UN | Consult Room - Universal Access | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CONS-UN | Consult Room - Universal Access | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional, second door for egress
CONS-UN | Consult Room - Universal Access | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
CONS-UN | Consult Room - Universal Access | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 1 | to patient/visitor chairs
CONS-UN | Consult Room - Universal Access | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CONS-UN | Consult Room - Universal Access | FFE | MGFP-002 | FLOWMETER: medical air | 1 | optional, provide if medical air required
CONS-UN | Consult Room - Universal Access | FFE | FIDI-003 | DISPENSER: bedroll | 1 | may be provided as an attachment to exam couch
CONS-UN | Consult Room - Universal Access | FFE | FIHR-019 | BRACKET: for suction bottle | 1 | optional, provide if suction required
CONS-UN | Consult Room - Universal Access | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CONS-UN | Consult Room - Universal Access | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
CONS-UN | Consult Room - Universal Access | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CONS-UN | Consult Room - Universal Access | FFE | FIHR-026 | HOOK: coat | 2
CONS-UN | Consult Room - Universal Access | FFE | FIRT-031 | TRACK: curtain, privacy | 1
CONS-UN | Consult Room - Universal Access | FFE | FQGE-010 | CURTAIN: privacy screen | 2
CONS-UN | Consult Room - Universal Access | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CONS-UN | Consult Room - Universal Access | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor
CONS-UN | Consult Room - Universal Access | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CONS-UN | Consult Room - Universal Access | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CONS-UN | Consult Room - Universal Access | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CONS-UN | Consult Room - Universal Access | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CONS-UN | Consult Room - Universal Access | FFE | FIBM-007 | MIRROR: fixed, glass, full length | 1
CONS-UN | Consult Room - Universal Access | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | optional, provide if oxygen required
CONS-UN | Consult Room - Universal Access | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
CONS-UN | Consult Room - Universal Access | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
CONS-UN | Consult Room - Universal Access | FFE | MMGE-002 | ADAPTER: suction | 1 | optional, provide if suction required
CONS-UN | Consult Room - Universal Access | FFE | MMGE-100 | SUCTION BOTTLE | 1 | optional, provide if suction required
CONS-UN | Consult Room - Universal Access | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
CONS-UN | Consult Room - Universal Access | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CONS-UN | Consult Room - Universal Access | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CONS-UN | Consult Room - Universal Access | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | high resolution monitor for PACS viewing
CONS-UN | Consult Room - Universal Access | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 | may be portable/mobile on stand
CONS-UN | Consult Room - Universal Access | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | may be wall mounted
CONS-UN | Consult Room - Universal Access | FFE | ITNE-023 | PRINTER: networked | 1 | optional
CONS-UN | Consult Room - Universal Access | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
CONS-UN | Consult Room - Universal Access | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | for patient lifter track
CONS-UN | Consult Room - Universal Access | FFE | FQDW-037 | DESK: adj height, 1500W x 750D x 750H nom. | 1
CONS-UN | Consult Room - Universal Access | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1
CONS-UN | Consult Room - Universal Access | FFE | MMBE-064 | COUCH: examination, electric, mobile, bariatric | 1 | hi/low operation
CONS-UN | Consult Room - Universal Access | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
CONS-UN | Consult Room - Universal Access | FFE | FQBS-058 | CHAIR: visitor, patient, with arms | 3 | consider weight capacity of chairs
CONS-UN | Consult Room - Universal Access | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | to desk
CONS-UN | Consult Room - Universal Access | SE | ELPR-006 | RCD: residual current device | 3
CONS-UN | Consult Room - Universal Access | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for exam light
CONS-UN | Consult Room - Universal Access | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
CONS-UN | Consult Room - Universal Access | SE | ELBO-015 | SWITCH: light, single | 2
CONS-UN | Consult Room - Universal Access | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional
CONS-UN | Consult Room - Universal Access | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional
CONS-UN | Consult Room - Universal Access | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional
CONS-UN | Consult Room - Universal Access | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1
CONS-UN | Consult Room - Universal Access | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
CONS-UN | Consult Room - Universal Access | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for electric couch
CONS-UN | Consult Room - Universal Access | SE | ELGP-208 | GPO: double, wall mounted | 3 | 2x below desk, 1x above desk
CONS-UN | Consult Room - Universal Access | SE | ITSE-006 | BUTTON: duress, fixed | 1 | in discreet location easily accessible by staff
CONS-UN | Consult Room - Universal Access | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
CONS-UN | Consult Room - Universal Access | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
CONS-UN | Consult Room - Universal Access | SE | ELGP-105 | GPO: single, on services panel | 1 | for diagnostic set
CONS-UN | Consult Room - Universal Access | SE | ELGP-205 | GPO: double, on services panel | 1
CONS-UN | Consult Room - Universal Access | SE | ELGP-222 | GPO: emergency power, double, on services panel | 1
CORR | Corridor - Patient Treatment Areas | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CORR | Corridor - Patient Treatment Areas | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 16
CORR | Corridor - Patient Treatment Areas | FA | WLPR-006 | WALL PROTECTION: corner guards | 6 | coordinated with adjacent wall protection
CORR | Corridor - Patient Treatment Areas | FA | FIRT-010 | HANDRAIL | 4 | provided to at least one side of the corridor, to be continuous wherever practical; may be combined with crash rail if provided
CORR | Corridor - Patient Treatment Areas | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
CORR | Corridor - Patient Treatment Areas | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CORR | Corridor - Patient Treatment Areas | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CORR | Corridor - Patient Treatment Areas | FA | WLPR-026 | WALL PROTECTION: rigid wall sheeting | 12 | height dependent on service requirements, crash rails are also acceptable
CORR | Corridor - Patient Treatment Areas | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | quantity to suit layout and infection control policies
CORR | Corridor - Patient Treatment Areas | SE | ITCL-001 | ANNUNCIATOR: nurse call | 1 | ceiling mounted; quantity to suit layout and service requirements
CORR | Corridor - Patient Treatment Areas | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | quantity and location to comply with mandatory requirements.
CTCR | CT Imaging Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CTCR | CT Imaging Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
CTCR | CT Imaging Control Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CTCR | CT Imaging Control Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
CTCR | CT Imaging Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CTCR | CT Imaging Control Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CTCR | CT Imaging Control Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass, to CT imaging room
CTCR | CT Imaging Control Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
CTCR | CT Imaging Control Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1 | to CT imaging room
CTCR | CT Imaging Control Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CTCR | CT Imaging Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
CTCR | CT Imaging Control Room | FFE | DWWD-004 | BLIND: roller | 1
CTCR | CT Imaging Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CTCR | CT Imaging Control Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
CTCR | CT Imaging Control Room | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
CTCR | CT Imaging Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
CTCR | CT Imaging Control Room | FFE | FIHR-044 | RACK: lead apron | 1
CTCR | CT Imaging Control Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
CTCR | CT Imaging Control Room | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1
CTCR | CT Imaging Control Room | FFE | ITNE-023 | PRINTER: networked | 1
CTCR | CT Imaging Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
CTCR | CT Imaging Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1
CTCR | CT Imaging Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 2 | high bench at 900-950mm AFFL is optional
CTCR | CT Imaging Control Room | FFE | MMMI-095 | COMPUTER: tower, ICS, CT | 1
CTCR | CT Imaging Control Room | FFE | MMMI-097 | CONTROL UNIT: c/w display, control box and keyboard, CT | 1 | console for CT scanning equipment
CTCR | CT Imaging Control Room | FFE | FIJO-099 | CAC: cable access cap | 2
CTCR | CT Imaging Control Room | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1
CTCR | CT Imaging Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
CTCR | CT Imaging Control Room | FFE | MMMI-369 | DISPLAY SCREEN: contrast injector | 1
CTCR | CT Imaging Control Room | FFE | FIHR-070 | BRACKET: for display screen, dual, desk mounted | 1
CTCR | CT Imaging Control Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 2
CTCR | CT Imaging Control Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
CTCR | CT Imaging Control Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 2
CTCR | CT Imaging Control Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
CTCR | CT Imaging Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | one outlet for telephone
CTCR | CT Imaging Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1
CTCR | CT Imaging Control Room | SE | ELGP-135 | GPO: UPS, single, wall mounted | 5
CTCR | CT Imaging Control Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | auto on when modality in use
CTCR | CT Imaging Control Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
CTCR | CT Imaging Control Room | SE | ELGP-208 | GPO: double, wall mounted | 2
CTCR | CT Imaging Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3
CTCR | CT Imaging Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CTCR | CT Imaging Control Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
CTCR | CT Imaging Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
CTIR | CT Imaging Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
CTIR | CT Imaging Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 8
CTIR | CT Imaging Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
CTIR | CT Imaging Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
CTIR | CT Imaging Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CTIR | CT Imaging Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2 | to basin
CTIR | CT Imaging Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | at 3000 mm AFFL; sound absorbing plasterboard recommended
CTIR | CT Imaging Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass, to control room
CTIR | CT Imaging Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
CTIR | CT Imaging Room | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
CTIR | CT Imaging Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CTIR | CT Imaging Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 8
CTIR | CT Imaging Room | FFE | MGFP-002 | FLOWMETER: medical air | 1
CTIR | CT Imaging Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2
CTIR | CT Imaging Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CTIR | CT Imaging Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
CTIR | CT Imaging Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CTIR | CT Imaging Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | near door
CTIR | CT Imaging Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CTIR | CT Imaging Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CTIR | CT Imaging Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CTIR | CT Imaging Room | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 1
CTIR | CT Imaging Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CTIR | CT Imaging Room | FFE | MMGE-131 | TROLLEY: monitor | 1
CTIR | CT Imaging Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2
CTIR | CT Imaging Room | FFE | MMBE-042 | SLIDE: patient | 1
CTIR | CT Imaging Room | FFE | MMGE-142 | TROLLEY: sharps bin | 1
CTIR | CT Imaging Room | FFE | MMGE-002 | ADAPTER: suction | 2
CTIR | CT Imaging Room | FFE | MMGE-100 | SUCTION BOTTLE | 2
CTIR | CT Imaging Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
CTIR | CT Imaging Room | FFE | FQSM-003 | PEDESTAL: mobile, wire basket unit, 840H | 2
CTIR | CT Imaging Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CTIR | CT Imaging Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CTIR | CT Imaging Room | FFE | MMBE-010 | BED: patient, electric with mattress | 1
CTIR | CT Imaging Room | FFE | ITCL-012 | CAMERA: observation | 2
CTIR | CT Imaging Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
CTIR | CT Imaging Room | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1
CTIR | CT Imaging Room | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1
CTIR | CT Imaging Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CTIR | CT Imaging Room | FFE | MMMI-099 | DEVICE: imaging, CT | 1
CTIR | CT Imaging Room | FFE | MMMI-105 | TABLE: patient, fixed, CT | 1
CTIR | CT Imaging Room | FFE | MMMI-107 | INJECTOR: contrast, CT, ceiling mounted | 1
CTIR | CT Imaging Room | FFE | FIJO-184 | CUPBOARD: underbench, double door, no shelves, no toeplate, lockable | 1
CTIR | CT Imaging Room | FFE | FIHR-064 | BRACKET: for display screen, arm mounted, rotating | 1
CTIR | CT Imaging Room | FFE | MMSP-035 | PENDANT: single, dual arm, display screen | 1
CTIR | CT Imaging Room | FFE | MMMI-377 | WARMER: contrast | 1
CTIR | CT Imaging Room | FFE | FIHR-078 | BRACKET: for observation camera, wall mounted | 2
CTIR | CT Imaging Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
CTIR | CT Imaging Room | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
CTIR | CT Imaging Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
CTIR | CT Imaging Room | SE | ELBO-001 | BUTTON: emergency stop | 1
CTIR | CT Imaging Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on services panel
CTIR | CT Imaging Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | outside room entry, auto on when modality in use
CTIR | CT Imaging Room | SE | ELBO-015 | SWITCH: light, single | 1
CTIR | CT Imaging Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
CTIR | CT Imaging Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on services panel
CTIR | CT Imaging Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
CTIR | CT Imaging Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
CTIR | CT Imaging Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
CTIR | CT Imaging Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | for clock
CTIR | CT Imaging Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | to walls
CTIR | CT Imaging Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CTIR | CT Imaging Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3 | for foot pedal recharge
CTIR | CT Imaging Room | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
CTIR | CT Imaging Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
CTIR | CT Imaging Room | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors as specified
CTIR | CT Imaging Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
CTIR | CT Imaging Room | SE | ELGP-133 | GPO: UPS, single, on services panel | 2
CTIR | CT Imaging Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 6 | on services panel
CTIR | CT Imaging Room | SE | ELPR-007 | UPS: status indicator | 1 | on services panel
CTPR | CT Planning Room | FA | FLVY-001 | FLOOR FINISH: vinyl, seamless, coved, anti-static | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CTPR | CT Planning Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
CTPR | CT Planning Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
CTPR | CT Planning Room | FA | WLWA-007 | WALL FINISH: splashback | 1
CTPR | CT Planning Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
CTPR | CT Planning Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 7
CTPR | CT Planning Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
CTPR | CT Planning Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass, to control room
CTPR | CT Planning Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1 | to control room
CTPR | CT Planning Room | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
CTPR | CT Planning Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
CTPR | CT Planning Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
CTPR | CT Planning Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
CTPR | CT Planning Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 3
CTPR | CT Planning Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CTPR | CT Planning Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CTPR | CT Planning Room | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 1 | for patient slide
CTPR | CT Planning Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CTPR | CT Planning Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
CTPR | CT Planning Room | FFE | MMBE-042 | SLIDE: patient | 1 | patient transfer devices to be based on operational requirements and WHS policies
CTPR | CT Planning Room | FFE | MMGE-139 | TROLLEY: procedure | 1
CTPR | CT Planning Room | FFE | MMGE-142 | TROLLEY: sharps bin | 1
CTPR | CT Planning Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2
CTPR | CT Planning Room | FFE | MMGE-002 | ADAPTER: suction | 1
CTPR | CT Planning Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
CTPR | CT Planning Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
CTPR | CT Planning Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CTPR | CT Planning Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CTPR | CT Planning Room | FFE | ITCL-012 | CAMERA: observation | 2 | 1 x optional, for patient observation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
CTPR | CT Planning Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
CTPR | CT Planning Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
CTPR | CT Planning Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CTPR | CT Planning Room | FFE | MMMI-105 | TABLE: patient, fixed, CT | 1
CTPR | CT Planning Room | FFE | MMMI-107 | INJECTOR: contrast, CT, ceiling mounted | 1 | may be mobile
CTPR | CT Planning Room | FFE | MMMI-109 | DEVICE: imaging, CT, wide bore | 1
CTPR | CT Planning Room | FFE | FIJO-166 | CUPBOARD: tall, shelving, horizontal patient device storage, radiotherapy | 2
CTPR | CT Planning Room | FFE | FIJO-167 | CUPBOARD: tall, shelving, vertical patient device storage, radiotherapy | 1
CTPR | CT Planning Room | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead is also acceptable
CTPR | CT Planning Room | FFE | MMMI-377 | WARMER: contrast | 1 | may be located in control room
CTPR | CT Planning Room | FFE | FIHR-077 | BRACKET: for observation camera, ceiling mounted | 1
CTPR | CT Planning Room | FFE | FIHR-078 | BRACKET: for observation camera, wall mounted | 1
CTPR | CT Planning Room | FFE | MMRA-008 | DEVICE: surface guided radiation therapy system | 1 | as required for respiratory gating / motion management / surface guidance systems, to suit service requirements
CTPR | CT Planning Room | FFE | MMRA-014 | LASER: radiotherapy, bridge | 1 | wall and ceiling mounted lasers are also acceptable
CTPR | CT Planning Room | FFE | MMRA-020 | OVEN: thermoplastic warming | 1
CTPR | CT Planning Room | FFE | FIHR-092 | HOOK: anchor, patient ladder | 1
CTPR | CT Planning Room | FFE | MMRA-019 | LASER: radiotherapy, couch tracking | 1
CTPR | CT Planning Room | FFE | FIHR-089 | BRACKET: surface guided radiation therapy system, ceiling mounted | 1
CTPR | CT Planning Room | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 2 | 1 x optional, to additional patient observation camera if provided
CTPR | CT Planning Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
CTPR | CT Planning Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
CTPR | CT Planning Room | SE | ELPR-006 | RCD: residual current device | 3
CTPR | CT Planning Room | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | 1 x optional, to additional patient observation camera if provided
CTPR | CT Planning Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
CTPR | CT Planning Room | SE | ELBO-001 | BUTTON: emergency stop | 1
CTPR | CT Planning Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | outside room doors, auto-on when modality in use
CTPR | CT Planning Room | SE | ELBO-015 | SWITCH: light, single | 1
CTPR | CT Planning Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
CTPR | CT Planning Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
CTPR | CT Planning Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
CTPR | CT Planning Room | SE | ELGP-109 | GPO: single, wall mounted | 2 | to clock
CTPR | CT Planning Room | SE | ELGP-208 | GPO: double, wall mounted | 4
CTPR | CT Planning Room | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
CTPR | CT Planning Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
CTPR | CT Planning Room | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors, shielding to be reviewed and confirmed by Radiation Consultant
CTPR | CT Planning Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
CTPR | CT Planning Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
CTPR | CT Planning Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3
CTPR | CT Planning Room | SE | LIFX-038 | LIGHT: backlit feature panels | 2 | desirable
DEN-MLB | Dental Laboratory, Minor | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent under basin and around sink
DEN-MLB | Dental Laboratory, Minor | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9
DEN-MLB | Dental Laboratory, Minor | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DEN-MLB | Dental Laboratory, Minor | FA | WLWA-007 | WALL FINISH: splashback | 1
DEN-MLB | Dental Laboratory, Minor | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DEN-MLB | Dental Laboratory, Minor | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2
DEN-MLB | Dental Laboratory, Minor | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
DEN-MLB | Dental Laboratory, Minor | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
DEN-MLB | Dental Laboratory, Minor | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DEN-MLB | Dental Laboratory, Minor | FFE | ITNE-052 | TELEPHONE: handset, wall mount | 1
DEN-MLB | Dental Laboratory, Minor | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 2
DEN-MLB | Dental Laboratory, Minor | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
DEN-MLB | Dental Laboratory, Minor | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DEN-MLB | Dental Laboratory, Minor | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
DEN-MLB | Dental Laboratory, Minor | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DEN-MLB | Dental Laboratory, Minor | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DEN-MLB | Dental Laboratory, Minor | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 2
DEN-MLB | Dental Laboratory, Minor | FFE | FIJO-197 | SHELF: stainless steel, underbench | 4 | some shelves may be removable or omitted to allow for storage of bulk items on mobile dolly
DEN-MLB | Dental Laboratory, Minor | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 5
DEN-MLB | Dental Laboratory, Minor | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1
DEN-MLB | Dental Laboratory, Minor | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 10 | various sizes
DEN-MLB | Dental Laboratory, Minor | FFE | MMDN-004 | DEVICE: dental, micromotor | 1 | optional
DEN-MLB | Dental Laboratory, Minor | FFE | MMDN-005 | DEVICE: dental, model trimmer | 1 | plumbed to sink
DEN-MLB | Dental Laboratory, Minor | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DEN-MLB | Dental Laboratory, Minor | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DEN-MLB | Dental Laboratory, Minor | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
DEN-MLB | Dental Laboratory, Minor | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | optional; to workstation if provided
DEN-MLB | Dental Laboratory, Minor | FFE | HYDR-008 | TRAP: plaster | 1
DEN-MLB | Dental Laboratory, Minor | FFE | MMDN-009 | LATHE: dental, polishing | 1 | extraction is required if not integral to equipment
DEN-MLB | Dental Laboratory, Minor | FFE | MMDN-013 | MOULDER: dental, forming machine | 1
DEN-MLB | Dental Laboratory, Minor | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1
DEN-MLB | Dental Laboratory, Minor | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 2
DEN-MLB | Dental Laboratory, Minor | FFE | ITNE-003 | BAR CODING: reader | 1 | optional; to workstation if provided
DEN-MLB | Dental Laboratory, Minor | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead is also acceptable
DEN-MLB | Dental Laboratory, Minor | FFE | FQDW-052 | DESK: adj height, 1000W x 600D x 750H nom. | 1 | optional; to workstation if provided
DEN-MLB | Dental Laboratory, Minor | FFE | MMDN-023 | DEVICE: dental extraction unit | 1
DEN-MLB | Dental Laboratory, Minor | FFE | MMDN-024 | DEVICE: dental, mixing vibrator | 1 | a vacuum mixer may also be considered
DEN-MLB | Dental Laboratory, Minor | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
DEN-MLB | Dental Laboratory, Minor | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
DEN-MLB | Dental Laboratory, Minor | SE | HYDR-004 | DRAIN: floor waste | 1
DEN-MLB | Dental Laboratory, Minor | SE | LIFX-008 | LIGHT: task light, built in | 5
DEN-MLB | Dental Laboratory, Minor | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 2 x task light
DEN-MLB | Dental Laboratory, Minor | SE | MGAS-008 | OUTLET: compressed air, wall mounted | 1 | to forming machine
DEN-MLB | Dental Laboratory, Minor | SE | ELGP-109 | GPO: single, wall mounted | 1
DEN-MLB | Dental Laboratory, Minor | SE | ELGP-208 | GPO: double, wall mounted | 8 | 2 x optional; to workstation if provided
DENSR-1 | Dental Surgery, Type 1 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
DENSR-1 | Dental Surgery, Type 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
DENSR-1 | Dental Surgery, Type 1 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DENSR-1 | Dental Surgery, Type 1 | FA | WLWA-007 | WALL FINISH: splashback | 1
DENSR-1 | Dental Surgery, Type 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DENSR-1 | Dental Surgery, Type 1 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | optional
DENSR-1 | Dental Surgery, Type 1 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
DENSR-1 | Dental Surgery, Type 1 | FA | DWWH-005 | WINDOW | 1 | desirable
DENSR-1 | Dental Surgery, Type 1 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
DENSR-1 | Dental Surgery, Type 1 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to external window if provided
DENSR-1 | Dental Surgery, Type 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1 | below sink
DENSR-1 | Dental Surgery, Type 1 | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 2 | optional, extent of storage dependent on service requirements and approach to consumables storage
DENSR-1 | Dental Surgery, Type 1 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DENSR-1 | Dental Surgery, Type 1 | FFE | FIDI-014 | DISPENSER: disposable glove | 2 | 1 x to basin
DENSR-1 | Dental Surgery, Type 1 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DENSR-1 | Dental Surgery, Type 1 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DENSR-1 | Dental Surgery, Type 1 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DENSR-1 | Dental Surgery, Type 1 | FFE | FIDI-021 | DISPENSER: mask | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FQBS-051 | STOOL: mobile, adj height | 2
DENSR-1 | Dental Surgery, Type 1 | FFE | MMGE-002 | ADAPTER: suction | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | MMGE-100 | SUCTION BOTTLE | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | MMDN-016 | TROLLEY: dental | 2
DENSR-1 | Dental Surgery, Type 1 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | optional, to sink if provided
DENSR-1 | Dental Surgery, Type 1 | FFE | MMDN-002 | CHAIR: dental, electric | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | MMDN-018 | X-RAY UNIT: dental, wall mounted | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | MMDN-020 | LIGHT: dental, ceiling mounted | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 2
DENSR-1 | Dental Surgery, Type 1 | FFE | FIJO-099 | CAC: cable access cap | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | FIJO-212 | BULKHEAD: joinery | 2 | optional, over wall mounted joinery if provided; plasterboard bulkhead is also acceptable
DENSR-1 | Dental Surgery, Type 1 | FFE | FIJO-213 | PANEL: joinery carcass end | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | HYBA-079 | SINK: single, dental | 1 | optional
DENSR-1 | Dental Surgery, Type 1 | FFE | FIHR-091 | RACK: lead apron, single | 1 | optional
DENSR-1 | Dental Surgery, Type 1 | FFE | MMDN-022 | CONSOLE: dentist, chair mounted | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | MMDN-021 | CONSOLE: dental assistant, chair mounted | 1
DENSR-1 | Dental Surgery, Type 1 | FFE | MMDN-025 | MONITOR: dentist, chair mounted | 1 | optional
DENSR-1 | Dental Surgery, Type 1 | FFE | FIHR-088 | BRACKET: for monitor, desk mounted, articulated, adj height | 1 | articulated with smooth action, reach to be sufficient for left handed and right handed setup
DENSR-1 | Dental Surgery, Type 1 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
DENSR-1 | Dental Surgery, Type 1 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
DENSR-1 | Dental Surgery, Type 1 | SE | ELPR-006 | RCD: residual current device | 2
DENSR-1 | Dental Surgery, Type 1 | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional
DENSR-1 | Dental Surgery, Type 1 | SE | HYTP-008 | OUTLET: cold water | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | SE | HYDR-001 | DRAIN: special requirements | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | SE | LIFX-008 | LIGHT: task light, built in | 2 | optional, under wall mounted joinery if provided
DENSR-1 | Dental Surgery, Type 1 | SE | ELBO-015 | SWITCH: light, single | 1 | 1 x general room lighting, 2 x optional, to task lighting if provided
DENSR-1 | Dental Surgery, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
DENSR-1 | Dental Surgery, Type 1 | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional
DENSR-1 | Dental Surgery, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1
DENSR-1 | Dental Surgery, Type 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | optional, depending on service requirements
DENSR-1 | Dental Surgery, Type 1 | SE | ELGP-208 | GPO: double, wall mounted | 6
DENSR-1 | Dental Surgery, Type 1 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
DENSR-1 | Dental Surgery, Type 1 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to x-ray unit
DENSR-1 | Dental Surgery, Type 1 | SE | ITSE-006 | BUTTON: duress, fixed | 1
DENSR-1 | Dental Surgery, Type 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
DENSR-1 | Dental Surgery, Type 1 | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
DENSR-1 | Dental Surgery, Type 1 | SE | MGAS-020 | OUTLET: medical air (MA) | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | SE | MGAS-090 | OUTLET: vacuum | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | SE | ITIN-010 | OUTLET: data, single RJ45 | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | SE | ELGE-004 | DIRECT CONNECTION: power, emergency | 1 | to dental chair
DENSR-2 | Dental Surgery, Type 2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
DENSR-2 | Dental Surgery, Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 8
DENSR-2 | Dental Surgery, Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DENSR-2 | Dental Surgery, Type 2 | FA | WLWA-007 | WALL FINISH: splashback | 1
DENSR-2 | Dental Surgery, Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DENSR-2 | Dental Surgery, Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | optional
DENSR-2 | Dental Surgery, Type 2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
DENSR-2 | Dental Surgery, Type 2 | FA | DWWH-005 | WINDOW | 1 | desirable
DENSR-2 | Dental Surgery, Type 2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
DENSR-2 | Dental Surgery, Type 2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to external window if provided
DENSR-2 | Dental Surgery, Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 2 | optional, extent of storage dependent on service requirements and approach to consumables storage
DENSR-2 | Dental Surgery, Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DENSR-2 | Dental Surgery, Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 2 | 1 x to basin
DENSR-2 | Dental Surgery, Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DENSR-2 | Dental Surgery, Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DENSR-2 | Dental Surgery, Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DENSR-2 | Dental Surgery, Type 2 | FFE | FIDI-021 | DISPENSER: mask | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FQBS-051 | STOOL: mobile, adj height | 2
DENSR-2 | Dental Surgery, Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MMDN-016 | TROLLEY: dental | 2
DENSR-2 | Dental Surgery, Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | optional, to sink if provided
DENSR-2 | Dental Surgery, Type 2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MMDN-002 | CHAIR: dental, electric | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MMDN-018 | X-RAY UNIT: dental, wall mounted | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MMDN-020 | LIGHT: dental, ceiling mounted | 1 | may be chair mounted
DENSR-2 | Dental Surgery, Type 2 | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIJO-099 | CAC: cable access cap | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | FIJO-212 | BULKHEAD: joinery | 2 | optional, over wall mounted joinery if provided; plasterboard bulkhead is also acceptable
DENSR-2 | Dental Surgery, Type 2 | FFE | FIJO-213 | PANEL: joinery carcass end | 2
DENSR-2 | Dental Surgery, Type 2 | FFE | HYBA-079 | SINK: single, dental | 1 | optional
DENSR-2 | Dental Surgery, Type 2 | FFE | FIHR-091 | RACK: lead apron, single | 1 | optional
DENSR-2 | Dental Surgery, Type 2 | FFE | MMDN-022 | CONSOLE: dentist, chair mounted | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MMDN-021 | CONSOLE: dental assistant, chair mounted | 1
DENSR-2 | Dental Surgery, Type 2 | FFE | MMDN-025 | MONITOR: dentist, chair mounted | 1 | optional
DENSR-2 | Dental Surgery, Type 2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
DENSR-2 | Dental Surgery, Type 2 | SE | ELPR-006 | RCD: residual current device | 2
DENSR-2 | Dental Surgery, Type 2 | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional
DENSR-2 | Dental Surgery, Type 2 | SE | HYTP-008 | OUTLET: cold water | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | SE | HYDR-001 | DRAIN: special requirements | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | SE | LIFX-008 | LIGHT: task light, built in | 2 | optional, under wall mounted joinery if provided
DENSR-2 | Dental Surgery, Type 2 | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 2 x optional, to task lighting if provided
DENSR-2 | Dental Surgery, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
DENSR-2 | Dental Surgery, Type 2 | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional
DENSR-2 | Dental Surgery, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1
DENSR-2 | Dental Surgery, Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | optional, depending on service requirements
DENSR-2 | Dental Surgery, Type 2 | SE | ELGP-208 | GPO: double, wall mounted | 6
DENSR-2 | Dental Surgery, Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
DENSR-2 | Dental Surgery, Type 2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to x-ray unit
DENSR-2 | Dental Surgery, Type 2 | SE | ITSE-006 | BUTTON: duress, fixed | 2
DENSR-2 | Dental Surgery, Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
DENSR-2 | Dental Surgery, Type 2 | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
DENSR-2 | Dental Surgery, Type 2 | SE | MGAS-020 | OUTLET: medical air (MA) | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | SE | MGAS-090 | OUTLET: vacuum | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | SE | ITIN-010 | OUTLET: data, single RJ45 | 1 | connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | SE | ELGE-004 | DIRECT CONNECTION: power, emergency | 1 | to dental chair
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to Bev. Bay; tiles also acceptable
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | DWWH-005 | WINDOW | 1 | safety glass, desirable
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1 | to Beverage Bay; 910mm clear opening; door hardware to not provide ligature points
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | DWGL-030 | DOOR: 1400mm c/o, 1 1/2 leaf, fully glazed, alum/safety glass, powdercoat/paint | 2 | Entry/Exit doors; 1400mm clear opening; door hardware to not provide ligature points
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1 | optional
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FQGE-002 | ARTWORK | 2 | optional; recessed, not removable
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FQBS-015 | CHAIR: dining | 8 | with space for wheelchair/s
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 2
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 1 | over bench
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | DWWD-003 | BLIND: integral | 2 | to external windows as required
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | under bench
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to sink; plastic; no ligature points; no sharp edges
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to sink; no ligature points; no sharp edges
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1 | lockable
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 1 | 900x900, optional; recessed, not removable
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | DWWH-004 | SHUTTER: roller, manual | 1 | lockable, to Bev Bay; heavy duty
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FQTA-077 | TABLE: square, 800W, dining height | 3
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FQCA-038 | FRIDGE: domestic, underbench, 80L | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | HYGE-008 | BOILING WATER UNIT: 5 Litre | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | HYBA-069 | SINK: single, with drainer, 930mmL | 1 | warm water
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | ITCL-014 | CLOCK: analogue, electric | 1 | recessed
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FQCA-067 | OVEN: microwave, domestic | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 2 | with inset sink
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | FFE | FIJO-207 | CUPBOARD: wall mount, shelf unit, adj shelves for microwave, short | 1 | over bench
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | SE | ELBO-015 | SWITCH: light, single | 2
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | or Duress call
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | SE | ELGP-109 | GPO: single, wall mounted | 4 | BWU, fridge, microwave, clock
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | SE | ELGP-208 | GPO: double, wall mounted | 6 | 2 above bench
DINBEV-25 | Dining Room/Beverage Bay (Mental Health), 25m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
DINR | Dining - Patient | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10/pendulum P3 or agreed equivalent to extend under basin; significant change in colour to be avoided
DINR | Dining - Patient | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
DINR | Dining - Patient | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DINR | Dining - Patient | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
DINR | Dining - Patient | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
DINR | Dining - Patient | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
DINR | Dining - Patient | FA | DWWH-005 | WINDOW | 2 | natural light and external outlook is essential
DINR | Dining - Patient | FA | DWGL-031 | DOOR: 1400mm c/o, 1 1/2 leaf, half glazed, solid core/glass, paint | 1 | with hold open device to support trolley movement as required
DINR | Dining - Patient | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 2 | to meal trolley parking area
DINR | Dining - Patient | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DINR | Dining - Patient | FFE | FQGE-002 | ARTWORK | 1
DINR | Dining - Patient | FFE | FQBS-015 | CHAIR: dining | 16 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
DINR | Dining - Patient | FFE | DWWD-004 | BLIND: roller | 2
DINR | Dining - Patient | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
DINR | Dining - Patient | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DINR | Dining - Patient | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
DINR | Dining - Patient | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DINR | Dining - Patient | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DINR | Dining - Patient | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DINR | Dining - Patient | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 | optional
DINR | Dining - Patient | FFE | FIJO-104 | CUPBOARD: drawer unit, 3 equal | 1
DINR | Dining - Patient | FFE | FQTA-059 | TABLE: square, 1100W, dining height | 4 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
DINR | Dining - Patient | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | size, type and quantity of bins dependent on local waste management policies
DINR | Dining - Patient | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 1 | optional
DINR | Dining - Patient | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DINR | Dining - Patient | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DINR | Dining - Patient | FFE | FQCA-082 | TROLLEY: food delivery, hot/cold | 1 | as required to suit food service model
DINR | Dining - Patient | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
DINR | Dining - Patient | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
DINR | Dining - Patient | FFE | FQCW-062 | BIN: waste, recycling, comingled, 50L | 1 | size, type and quantity of bins dependent on local waste management policies
DINR | Dining - Patient | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to wall mounted telephone
DINR | Dining - Patient | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional, to television, MATV outlet may also be provided depending on local ICT policies
DINR | Dining - Patient | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | with indicator button and light
DINR | Dining - Patient | SE | ELBO-015 | SWITCH: light, single | 1
DINR | Dining - Patient | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
DINR | Dining - Patient | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
DINR | Dining - Patient | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
DINR | Dining - Patient | SE | ELGP-109 | GPO: single, wall mounted | 1 | to meal trolley parking area; power requirements dependent on type of meal trolley
DINR | Dining - Patient | SE | ELGP-208 | GPO: double, wall mounted | 3
DINR | Dining - Patient | SE | ELGP-208 | GPO: double, wall mounted | 1 | optional, to television
DINR | Dining - Patient | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
DISP-10 | Disposal Room, 10m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
DISP-10 | Disposal Room, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
DISP-10 | Disposal Room, 10m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
DISP-10 | Disposal Room, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
DISP-10 | Disposal Room, 10m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
DISP-10 | Disposal Room, 10m2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | lockable or secure staff access, hold open hardware may be required
DISP-10 | Disposal Room, 10m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1
DISP-10 | Disposal Room, 10m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DISP-10 | Disposal Room, 10m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DISP-10 | Disposal Room, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DISP-10 | Disposal Room, 10m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin, locate with alcohol based hand rub if basin is located outside of room
DISP-10 | Disposal Room, 10m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DISP-10 | Disposal Room, 10m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DISP-10 | Disposal Room, 10m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DISP-10 | Disposal Room, 10m2 | FFE | FIJO-194 | SHELF: laminate | 1 | optional, for storage of small sharps bins
DISP-10 | Disposal Room, 10m2 | FFE | MMGE-143 | TROLLEY: soiled linen collection | 1
DISP-10 | Disposal Room, 10m2 | FFE | FQCW-029 | BIN: waste, recycling, paper, 240L | 1 | size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 | size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | FFE | FQCW-022 | BIN: waste, general, skip 660 litre | 1 | size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | may be provided outside of room depending on local infection control policies
DISP-10 | Disposal Room, 10m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DISP-10 | Disposal Room, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
DISP-15 | Disposal Room, 15m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
DISP-15 | Disposal Room, 15m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
DISP-15 | Disposal Room, 15m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4 | 2 optional to optional door
DISP-15 | Disposal Room, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
DISP-15 | Disposal Room, 15m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
DISP-15 | Disposal Room, 15m2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 2 | 1 door optional, lockable or secure staff access, hold open hardware may be required, dual access may be provided depending on overall planning arrangement
DISP-15 | Disposal Room, 15m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1
DISP-15 | Disposal Room, 15m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DISP-15 | Disposal Room, 15m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DISP-15 | Disposal Room, 15m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DISP-15 | Disposal Room, 15m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin, locate with alcohol based hand rub if basin located outside of room
DISP-15 | Disposal Room, 15m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DISP-15 | Disposal Room, 15m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DISP-15 | Disposal Room, 15m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DISP-15 | Disposal Room, 15m2 | FFE | FIJO-194 | SHELF: laminate | 1 | optional, for storage of small sharps bins
DISP-15 | Disposal Room, 15m2 | FFE | MMGE-143 | TROLLEY: soiled linen collection | 1
DISP-15 | Disposal Room, 15m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 1 | size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | FFE | FQCW-029 | BIN: waste, recycling, paper, 240L | 1 | size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 2 | size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | FFE | FQCW-022 | BIN: waste, general, skip 660 litre | 2 | size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | may be provided outside of room depending on local infection control policies
DISP-15 | Disposal Room, 15m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DISP-15 | Disposal Room, 15m2 | SE | ELBO-015 | SWITCH: light, single | 1
DTUR-10 | Dirty Utility, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
DTUR-10 | Dirty Utility, 10m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
DTUR-10 | Dirty Utility, 10m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
DTUR-10 | Dirty Utility, 10m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DTUR-10 | Dirty Utility, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DTUR-10 | Dirty Utility, 10m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
DTUR-10 | Dirty Utility, 10m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | pull handle/push plate, closer
DTUR-10 | Dirty Utility, 10m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 5
DTUR-10 | Dirty Utility, 10m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DTUR-10 | Dirty Utility, 10m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-038 | RACK: bowl/basin | 1 | quantity to be based on service requirements
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DTUR-10 | Dirty Utility, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-029 | HOOK: equipment | 2 | optional, for clean linen bags
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-025 | HOOK: catheter bag | 2 | optional
DTUR-10 | Dirty Utility, 10m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 3
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-053 | RACK: pan & urinal | 1 | quantity to be based on service requirements
DTUR-10 | Dirty Utility, 10m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
DTUR-10 | Dirty Utility, 10m2 | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1
DTUR-10 | Dirty Utility, 10m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1
DTUR-10 | Dirty Utility, 10m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-10 | Dirty Utility, 10m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-10 | Dirty Utility, 10m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DTUR-10 | Dirty Utility, 10m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DTUR-10 | Dirty Utility, 10m2 | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
DTUR-10 | Dirty Utility, 10m2 | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 | combined utensil/pan sanitiser may be provided
DTUR-10 | Dirty Utility, 10m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | hot water
DTUR-10 | Dirty Utility, 10m2 | FFE | MMLA-013 | ANALYSER: urinalysis | 1 | optional
DTUR-10 | Dirty Utility, 10m2 | FFE | MMIC-097 | WASHER SANITISER: utensil washer | 1 | optional, combined utensil/pan sanitiser may be provided
DTUR-10 | Dirty Utility, 10m2 | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1
DTUR-10 | Dirty Utility, 10m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, for urinalysis machine
DTUR-10 | Dirty Utility, 10m2 | SE | ELPR-003 | ISOLATOR: electrical, 1ph+n | 1
DTUR-10 | Dirty Utility, 10m2 | SE | HYTP-013 | OUTLET: hot water | 2 | for washer sanitisers
DTUR-10 | Dirty Utility, 10m2 | SE | HYTP-008 | OUTLET: cold water | 2 | for washer sanitisers
DTUR-10 | Dirty Utility, 10m2 | SE | HYDR-004 | DRAIN: floor waste | 1
DTUR-10 | Dirty Utility, 10m2 | SE | HYDR-006 | DRAIN: tundish | 1 | optional, dependent on machine requirements
DTUR-10 | Dirty Utility, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
DTUR-10 | Dirty Utility, 10m2 | SE | ELGP-106 | GPO: single, special, for equipment | 2 | for washer sanitisers
DTUR-10 | Dirty Utility, 10m2 | SE | ELGP-109.1 | GPO: single, wall mounted (V) | 1 | optional, for urinalysis machine
DTUR-10 | Dirty Utility, 10m2 | SE | HYGE-028 | DEVICE: backflow prevention | 1
DTUR-12 | Dirty Utility, 12m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
DTUR-12 | Dirty Utility, 12m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
DTUR-12 | Dirty Utility, 12m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
DTUR-12 | Dirty Utility, 12m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DTUR-12 | Dirty Utility, 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DTUR-12 | Dirty Utility, 12m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
DTUR-12 | Dirty Utility, 12m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | pull handle/push plate, closer
DTUR-12 | Dirty Utility, 12m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 5
DTUR-12 | Dirty Utility, 12m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-038 | RACK: bowl/basin | 1 | quantity to be based on service requirements
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-029 | HOOK: equipment | 2 | optional, for clean linen bags
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-025 | HOOK: catheter bag | 2 | optional
DTUR-12 | Dirty Utility, 12m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 3
DTUR-12 | Dirty Utility, 12m2 | FFE | FIHR-053 | RACK: pan & urinal | 1 | quantity to be based on service requirements
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-12 | Dirty Utility, 12m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-12 | Dirty Utility, 12m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DTUR-12 | Dirty Utility, 12m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DTUR-12 | Dirty Utility, 12m2 | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
DTUR-12 | Dirty Utility, 12m2 | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 | combined utensil/pan sanitiser may be provided
DTUR-12 | Dirty Utility, 12m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | hot water
DTUR-12 | Dirty Utility, 12m2 | FFE | MMLA-013 | ANALYSER: urinalysis | 1 | optional
DTUR-12 | Dirty Utility, 12m2 | FFE | MMIC-097 | WASHER SANITISER: utensil washer | 1 | combined utensil/pan sanitiser may be provided
DTUR-12 | Dirty Utility, 12m2 | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1
DTUR-12 | Dirty Utility, 12m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, for urinalysis machine
DTUR-12 | Dirty Utility, 12m2 | SE | ELPR-003 | ISOLATOR: electrical, 1ph+n | 1
DTUR-12 | Dirty Utility, 12m2 | SE | HYTP-013 | OUTLET: hot water | 2 | for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | SE | HYTP-008 | OUTLET: cold water | 2 | for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | SE | HYDR-004 | DRAIN: floor waste | 1
DTUR-12 | Dirty Utility, 12m2 | SE | HYDR-006 | DRAIN: tundish | 1 | optional, dependent on machine requirements
DTUR-12 | Dirty Utility, 12m2 | SE | ELBO-015 | SWITCH: light, single | 1
DTUR-12 | Dirty Utility, 12m2 | SE | ELGP-106 | GPO: single, special, for equipment | 2 | for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | SE | ELGP-109.1 | GPO: single, wall mounted (V) | 1 | optional, for urinalysis machine
DTUR-12 | Dirty Utility, 12m2 | SE | HYGE-028 | DEVICE: backflow prevention | 1
DTUR-14 | Dirty Utility, 14m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
DTUR-14 | Dirty Utility, 14m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
DTUR-14 | Dirty Utility, 14m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
DTUR-14 | Dirty Utility, 14m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
DTUR-14 | Dirty Utility, 14m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DTUR-14 | Dirty Utility, 14m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
DTUR-14 | Dirty Utility, 14m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 2 | pull handle/push plate, closer
DTUR-14 | Dirty Utility, 14m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 6
DTUR-14 | Dirty Utility, 14m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DTUR-14 | Dirty Utility, 14m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-038 | RACK: bowl/basin | 1 | quantity to be based on service requirements
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DTUR-14 | Dirty Utility, 14m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-029 | HOOK: equipment | 2 | optional, for clean linen bags
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-025 | HOOK: catheter bag | 2 | optional
DTUR-14 | Dirty Utility, 14m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 3
DTUR-14 | Dirty Utility, 14m2 | FFE | FIHR-053 | RACK: pan & urinal | 1 | quantity to be based on service requirements
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
DTUR-14 | Dirty Utility, 14m2 | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1
DTUR-14 | Dirty Utility, 14m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-14 | Dirty Utility, 14m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-14 | Dirty Utility, 14m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DTUR-14 | Dirty Utility, 14m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DTUR-14 | Dirty Utility, 14m2 | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
DTUR-14 | Dirty Utility, 14m2 | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 | combined utensil/pan sanitiser may be provided
DTUR-14 | Dirty Utility, 14m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | hot water
DTUR-14 | Dirty Utility, 14m2 | FFE | MMLA-013 | ANALYSER: urinalysis | 1 | optional
DTUR-14 | Dirty Utility, 14m2 | FFE | MMIC-097 | WASHER SANITISER: utensil washer | 1 | combined utensil/pan sanitiser may be provided
DTUR-14 | Dirty Utility, 14m2 | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1
DTUR-14 | Dirty Utility, 14m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, for urinalysis machine
DTUR-14 | Dirty Utility, 14m2 | SE | ELPR-003 | ISOLATOR: electrical, 1ph+n | 1
DTUR-14 | Dirty Utility, 14m2 | SE | HYTP-013 | OUTLET: hot water | 2 | for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | SE | HYTP-008 | OUTLET: cold water | 2 | for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | SE | HYDR-004 | DRAIN: floor waste | 1
DTUR-14 | Dirty Utility, 14m2 | SE | HYDR-006 | DRAIN: tundish | 1 | optional, dependent on machine requirements
DTUR-14 | Dirty Utility, 14m2 | SE | ELBO-010 | SWITCH: light, 2-way | 2
DTUR-14 | Dirty Utility, 14m2 | SE | ELGP-106 | GPO: single, special, for equipment | 2 | for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | SE | ELGP-109.1 | GPO: single, wall mounted (V) | 1 | optional, for urinalysis machine
DTUR-14 | Dirty Utility, 14m2 | SE | HYGE-028 | DEVICE: backflow prevention | 1
DTUR-S | Dirty Utility, Sub | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
DTUR-S | Dirty Utility, Sub | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
DTUR-S | Dirty Utility, Sub | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
DTUR-S | Dirty Utility, Sub | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
DTUR-S | Dirty Utility, Sub | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
DTUR-S | Dirty Utility, Sub | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
DTUR-S | Dirty Utility, Sub | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | pull handle/push plate, closer
DTUR-S | Dirty Utility, Sub | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 5
DTUR-S | Dirty Utility, Sub | FA | CLCN-009 | CORNICE: wall trim fixing | 1
DTUR-S | Dirty Utility, Sub | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge
DTUR-S | Dirty Utility, Sub | FFE | FIHR-038 | RACK: bowl/basin | 1 | quantity to be based on service requirements
DTUR-S | Dirty Utility, Sub | FFE | FIHR-016 | BRACKET: for sharps bin | 1
DTUR-S | Dirty Utility, Sub | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
DTUR-S | Dirty Utility, Sub | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
DTUR-S | Dirty Utility, Sub | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
DTUR-S | Dirty Utility, Sub | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
DTUR-S | Dirty Utility, Sub | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
DTUR-S | Dirty Utility, Sub | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
DTUR-S | Dirty Utility, Sub | FFE | FIHR-029 | HOOK: equipment | 2 | optional, for clean linen bags
DTUR-S | Dirty Utility, Sub | FFE | FIHR-025 | HOOK: catheter bag | 2 | optional
DTUR-S | Dirty Utility, Sub | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 2
DTUR-S | Dirty Utility, Sub | FFE | FIHR-053 | RACK: pan & urinal | 1 | quantity to be based on service requirements
DTUR-S | Dirty Utility, Sub | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
DTUR-S | Dirty Utility, Sub | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1
DTUR-S | Dirty Utility, Sub | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1
DTUR-S | Dirty Utility, Sub | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-S | Dirty Utility, Sub | FFE | HYBA-010 | BASIN: handwash, Type B | 1
DTUR-S | Dirty Utility, Sub | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
DTUR-S | Dirty Utility, Sub | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
DTUR-S | Dirty Utility, Sub | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 | combined utensil/pan sanitiser may be provided
DTUR-S | Dirty Utility, Sub | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | hot water
DTUR-S | Dirty Utility, Sub | FFE | MMLA-013 | ANALYSER: urinalysis | 1 | optional
DTUR-S | Dirty Utility, Sub | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1
DTUR-S | Dirty Utility, Sub | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, for urinalysis machine
DTUR-S | Dirty Utility, Sub | SE | HYTP-013 | OUTLET: hot water | 1 | for washer sanitiser
DTUR-S | Dirty Utility, Sub | SE | HYTP-008 | OUTLET: cold water | 1 | for washer sanitiser
DTUR-S | Dirty Utility, Sub | SE | HYDR-004 | DRAIN: floor waste | 1
DTUR-S | Dirty Utility, Sub | SE | ELBO-015 | SWITCH: light, single | 1
DTUR-S | Dirty Utility, Sub | SE | ELGP-106 | GPO: single, special, for equipment | 1 | for washer sanitiser
DTUR-S | Dirty Utility, Sub | SE | ELGP-109.1 | GPO: single, wall mounted (V) | 1 | optional, for urinalysis machine
DTUR-S | Dirty Utility, Sub | SE | HYGE-028 | DEVICE: backflow prevention | 1
ECHO-TOE | Echocardiography - Transoesophageal | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
ECHO-TOE | Echocardiography - Transoesophageal | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
ECHO-TOE | Echocardiography - Transoesophageal | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
ECHO-TOE | Echocardiography - Transoesophageal | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
ECHO-TOE | Echocardiography - Transoesophageal | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
ECHO-TOE | Echocardiography - Transoesophageal | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
ECHO-TOE | Echocardiography - Transoesophageal | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional, to patient wc
ECHO-TOE | Echocardiography - Transoesophageal | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
ECHO-TOE | Echocardiography - Transoesophageal | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ECHO-TOE | Echocardiography - Transoesophageal | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 5
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MGFP-002 | FLOWMETER: medical air | 1 | patient services panel
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIHR-019 | BRACKET: for suction bottle | 2
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIHR-026 | HOOK: coat | 2 | optional
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIJO-131 | CUPBOARD: tall, single door, adj shelves, lockable | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to entry door
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIDI-019 | DISPENSER: gown/apron | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIDI-021 | DISPENSER: mask | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMGE-126 | TROLLEY: intubation | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | patient services panel
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMGE-088 | SAFE: dangerous drugs, small | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQBS-051 | STOOL: mobile, adj height | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMGE-002 | ADAPTER: suction | 2 | patient services panel
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMGE-100 | SUCTION BOTTLE | 2
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQSM-016 | TROLLEY | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FQSM-003 | PEDESTAL: mobile, wire basket unit, 840H | 2
ECHO-TOE | Echocardiography - Transoesophageal | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
ECHO-TOE | Echocardiography - Transoesophageal | FFE | ITCL-014 | CLOCK: analogue, electric | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMHA-002 | DEFIBRILLATOR | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMGE-062 | MONITOR: patient, dynamap | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMMI-325 | DEVICE: imaging, echocardiography machine | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIJO-212 | BULKHEAD: joinery | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMGE-169 | SLING: arm, dynamic, ceiling mounted | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | MMBE-069 | TROLLEY: patient, echocardiography | 1
ECHO-TOE | Echocardiography - Transoesophageal | FFE | ITNE-071 | COMPUTER: desktop, with dual display screens | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 5
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | exam light
ECHO-TOE | Echocardiography - Transoesophageal | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELBO-015 | SWITCH: light, single | 2 | 1 optional, to optional clean up room
ECHO-TOE | Echocardiography - Transoesophageal | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
ECHO-TOE | Echocardiography - Transoesophageal | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
ECHO-TOE | Echocardiography - Transoesophageal | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
ECHO-TOE | Echocardiography - Transoesophageal | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELGP-109 | GPO: single, wall mounted | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELGP-208 | GPO: double, wall mounted | 5
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELBO-012 | SWITCH: light, dimmer | 1
ECHO-TOE | Echocardiography - Transoesophageal | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel
ECL-10 | Equipment Clean-Up, 10m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
ECL-10 | Equipment Clean-Up, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
ECL-10 | Equipment Clean-Up, 10m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn
ECL-10 | Equipment Clean-Up, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
ECL-10 | Equipment Clean-Up, 10m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1
ECL-10 | Equipment Clean-Up, 10m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
ECL-10 | Equipment Clean-Up, 10m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn
ECL-10 | Equipment Clean-Up, 10m2 | FA | DWGL-020 | DOOR: 1100mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | 1100mm clear opening, lockable
ECL-10 | Equipment Clean-Up, 10m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | Wet edge, inset sink
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 2 | to basin and under bench
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | under bench
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1 | over bench
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FQSM-016 | TROLLEY | 2 | optional
ECL-10 | Equipment Clean-Up, 10m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer to BHWS-B (similar)
ECL-10 | Equipment Clean-Up, 10m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 2 | to sinks
ECL-10 | Equipment Clean-Up, 10m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
ECL-10 | Equipment Clean-Up, 10m2 | FFE | HYTP-004 | HOSE: spray | 1 | optional
ECL-10 | Equipment Clean-Up, 10m2 | FFE | HYBA-055 | SINK: single, 500 x 450 x 250D | 2 | hot water
ECL-10 | Equipment Clean-Up, 10m2 | FFE | FIJO-124 | CUPBOARD: tall, triple door, adj shelves, lockable | 1 | optional
ECL-10 | Equipment Clean-Up, 10m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ECL-10 | Equipment Clean-Up, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
ECL-10 | Equipment Clean-Up, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Optional. To be decided at project level.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | DWGL-020 | DOOR: 1100mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | Wet edge and inset sink/s. Length to suit layout, refer RLS or project specific requirements.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | Optional
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-018 | DISPENSER: gown | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 1 | Optional. Number to suit layout.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-008 | DISPENSER: detergent | 1 | To sink.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-022 | DISPENSER: moisturiser | 0 | optional
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | MMGE-119 | TROLLEY: equipment | 1 | Optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIGE-009 | PLATFORM: equipment washing, wall mounted | 1 | Stainless steel, grated, height adjustable, wall mounted.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | At 350mm AFFL or underbench, stainless steel cupboard.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2 | Over bench. Number to suit layout, refer RLS or project specific requirements.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer to BHWS-B (similar). Elbow action levers or handsfree optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin. Elbow action levers or handsfree optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYTP-006 | HOSE: spray, pressure control | 1 | Above sink, optional. Depends on operational/infection control policies.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYTP-003 | HOSE REEL: retractable | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYBA-055 | SINK: single, 500 x 450 x 250D | 1 | hot water
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | HYTP-013 | OUTLET: hot water | 2 | Hose reel and spray hose connection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | HYTP-008 | OUTLET: cold water | 2 | Hose reel and spray hose connection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | HYDR-004 | DRAIN: floor waste | 1 | To wash bay.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | ELBO-015 | SWITCH: light, single | 1
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ECL-14 | Equipment Clean-Up, 14m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
ECL-14 | Equipment Clean-Up, 14m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
ECL-14 | Equipment Clean-Up, 14m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn
ECL-14 | Equipment Clean-Up, 14m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
ECL-14 | Equipment Clean-Up, 14m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1
ECL-14 | Equipment Clean-Up, 14m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
ECL-14 | Equipment Clean-Up, 14m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn
ECL-14 | Equipment Clean-Up, 14m2 | FA | DWGL-020 | DOOR: 1100mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable
ECL-14 | Equipment Clean-Up, 14m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | wet edge, inset sinks
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 2 | optional
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 2 | to basin and under bench
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1
ECL-14 | Equipment Clean-Up, 14m2 | FFE | MMGE-119 | TROLLEY: equipment | 3 | optional
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | under bench
ECL-14 | Equipment Clean-Up, 14m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1 | over bench
ECL-14 | Equipment Clean-Up, 14m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer BHWS-B (similar). Elbow action levers or handsfree optional.
ECL-14 | Equipment Clean-Up, 14m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 2 | to sinks
ECL-14 | Equipment Clean-Up, 14m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin. Elbow action levers or handsfree optional.
ECL-14 | Equipment Clean-Up, 14m2 | FFE | HYTP-004 | HOSE: spray | 1 | optional
ECL-14 | Equipment Clean-Up, 14m2 | FFE | HYBA-055 | SINK: single, 500 x 450 x 250D | 2 | hot water
ECL-14 | Equipment Clean-Up, 14m2 | FFE | MMIC-097 | WASHER SANITISER: utensil washer | 1 | optional
ECL-14 | Equipment Clean-Up, 14m2 | SE | ELPR-003 | ISOLATOR: electrical, 1ph+n | 1
ECL-14 | Equipment Clean-Up, 14m2 | SE | HYTP-013 | OUTLET: hot water | 1
ECL-14 | Equipment Clean-Up, 14m2 | SE | HYTP-008 | OUTLET: cold water | 1
ECL-14 | Equipment Clean-Up, 14m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ECL-14 | Equipment Clean-Up, 14m2 | SE | ELBO-015 | SWITCH: light, single | 1
ECL-14 | Equipment Clean-Up, 14m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
ECL-14 | Equipment Clean-Up, 14m2 | SE | ELGP-106 | GPO: single, special, for equipment | 1 | utensil washer, optional
ECL-8 | Equipment Clean-Up, 8m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
ECL-8 | Equipment Clean-Up, 8m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
ECL-8 | Equipment Clean-Up, 8m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn
ECL-8 | Equipment Clean-Up, 8m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
ECL-8 | Equipment Clean-Up, 8m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1
ECL-8 | Equipment Clean-Up, 8m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
ECL-8 | Equipment Clean-Up, 8m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn
ECL-8 | Equipment Clean-Up, 8m2 | FA | DWGL-020 | DOOR: 1100mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable
ECL-8 | Equipment Clean-Up, 8m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | wet edge, inset sink
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 1 | optional
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | under bench
ECL-8 | Equipment Clean-Up, 8m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1 | over bench
ECL-8 | Equipment Clean-Up, 8m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer BHWS-B (similar)
ECL-8 | Equipment Clean-Up, 8m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 2 | to sinks
ECL-8 | Equipment Clean-Up, 8m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
ECL-8 | Equipment Clean-Up, 8m2 | FFE | HYBA-055 | SINK: single, 500 x 450 x 250D | 2 | hot water
ECL-8 | Equipment Clean-Up, 8m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ECL-8 | Equipment Clean-Up, 8m2 | SE | ELBO-015 | SWITCH: light, single | 1
ECL-8 | Equipment Clean-Up, 8m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
ENS-ACC | Ensuite - Accessible, 7m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-ACC | Ensuite - Accessible, 7m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-ACC | Ensuite - Accessible, 7m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant set plasterboard ceiling also acceptable
ENS-ACC | Ensuite - Accessible, 7m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FA | DWSC-012 | DOOR: 1200mm c/o, 1 1/2 leaf, solid core, paint | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FQGE-011 | CURTAIN: shower | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | optional
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | locate on drop down rail
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | drop down rails to sides of WC
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIGE-001 | BENCH SEAT: fixed, fold up/down, wet area, wall mounted | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-016 | RAIL: towel | 1 | with grab rail strength and fixings
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYBA-005 | BASIN: handwash, accessible | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYWC-001 | TOILET SUITE: accessible | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYTP-020 | SHOWER: hand-held | 1
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYTP-035 | TAPWARE: mixer, basin, accessible | 1
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-ACC | Ensuite - Accessible, 7m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ELBO-015 | SWITCH: light, single | 1
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light; may be located on drop down rail beside toilet
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
ENS-BA | Ensuite - Bariatric, 7m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-BA | Ensuite - Bariatric, 7m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 | for any areas not covered with vinyl/tile
ENS-BA | Ensuite - Bariatric, 7m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-BA | Ensuite - Bariatric, 7m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FA | DWSC-012 | DOOR: 1200mm c/o, 1 1/2 leaf, solid core, paint | 1 | outward opening, privacy latch, emergency release
ENS-BA | Ensuite - Bariatric, 7m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FQGE-011 | CURTAIN: shower | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | MMGE-025 | CHAIR: shower, bariatric | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | optional
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 2 | optional
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-051 | HOLDER: soap/shampoo, recessed, vertical format | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-016 | RAIL: towel | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYWC-002 | TOILET SUITE: bariatric | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYTP-020 | SHOWER: hand-held | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | MMBE-061 | LIFTER: patient, ceiling mounted, track, traverse, bariatric | 1
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-BA | Ensuite - Bariatric, 7m2 | SE | HYDR-004 | DRAIN: floor waste | 2 | 1 near wc/basin, 1 for shower
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ELBO-015 | SWITCH: light, single | 1
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-031 | PENDANT: nurse call, patient to staff | 1 | waterproof
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ENS-BA | Ensuite - Bariatric, 7m2 | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | optional
ENS-BR | Ensuite - Birthing | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | to be tiles for a tiled floor
ENS-BR | Ensuite - Birthing | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
ENS-BR | Ensuite - Birthing | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
ENS-BR | Ensuite - Birthing | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | tiles are also acceptable
ENS-BR | Ensuite - Birthing | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | water resistant ceiling tiles are also acceptable
ENS-BR | Ensuite - Birthing | FA | DWSC-011 | DOOR: 1100mm c/o, single leaf, solid core, paint | 1 | outward opening, with privacy latch and emergency release
ENS-BR | Ensuite - Birthing | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ENS-BR | Ensuite - Birthing | FFE | FIHR-026 | HOOK: coat | 2 | optional
ENS-BR | Ensuite - Birthing | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | optional, dependent on project/service requirements
ENS-BR | Ensuite - Birthing | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, dependent on project/service requirements
ENS-BR | Ensuite - Birthing | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ENS-BR | Ensuite - Birthing | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
ENS-BR | Ensuite - Birthing | FFE | FIDI-030 | DISPENSER: soap | 1
ENS-BR | Ensuite - Birthing | FFE | FIDI-036 | DISPENSER: toilet paper | 1
ENS-BR | Ensuite - Birthing | FFE | FIRT-006 | GRAB RAIL: WC | 1
ENS-BR | Ensuite - Birthing | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 2
ENS-BR | Ensuite - Birthing | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin
ENS-BR | Ensuite - Birthing | FFE | MGFP-004 | FLOWMETER: oxygen | 1
ENS-BR | Ensuite - Birthing | FFE | FQCW-037 | BIN: waste, sanitary | 1
ENS-BR | Ensuite - Birthing | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-BR | Ensuite - Birthing | FFE | FIRT-016 | RAIL: towel | 1 | strength and fixings, including in-wall support, to be equivalent to grab rails
ENS-BR | Ensuite - Birthing | FFE | HYWC-001 | TOILET SUITE: accessible | 1 | accessible suite to assist with mobility and support during labor
ENS-BR | Ensuite - Birthing | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
ENS-BR | Ensuite - Birthing | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2
ENS-BR | Ensuite - Birthing | FFE | HYTP-020 | SHOWER: hand-held | 2
ENS-BR | Ensuite - Birthing | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1
ENS-BR | Ensuite - Birthing | FFE | FIGE-011 | BACKREST: accessible toilet | 1
ENS-BR | Ensuite - Birthing | FFE | MMMA-019 | SUPPORT FIXTURE: birthing, ladder, wall mounted, wet area | 1 | optional; strength and fixings, including in-wall support, to be equivalent to heavy duty grab rails
ENS-BR | Ensuite - Birthing | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1
ENS-BR | Ensuite - Birthing | SE | HYDR-004 | DRAIN: floor waste | 2
ENS-BR | Ensuite - Birthing | SE | ELBO-015 | SWITCH: light, single | 1 | IPX4 rating required, located outside room
ENS-BR | Ensuite - Birthing | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
ENS-BR | Ensuite - Birthing | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1
ENS-BR | Ensuite - Birthing | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | SE | ELGP-208 | GPO: double, wall mounted | 1 | to be classified as a shaver outlet
ENS-BR | Ensuite - Birthing | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles also acceptable
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | tiles also acceptable
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | for High Dependency and intensive care areas, consider plywood or equivalent backing to ceiling finish
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | DWSC-004 | DOOR: 850mm c/o, 180 deg swing, single leaf, solid core, paint | 1 | door swing outward and anti ligature hardware
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIRT-004 | GRAB RAIL: shower, anti ligature | 1 | optional, vertical
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIRT-009 | GRAB RAIL: WC, anti ligature | 1 | optional, vertical
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIHR-027 | HOOK: coat, collapsible, anti ligature | 2 | one at 1200AFFL for wheelchair users; dependent on jurisdictional policy
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIRT-029 | TRACK: curtain, plastic, recessed | 1 | optional, for privacy screen to shower area; dependent on jurisdictional policy. 15kg breaking strength recommended
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, collapsible; anti ligature fabric; dependent on jurisdictional policy
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIDI-051 | HOLDER: soap/shampoo, recessed, vertical format | 1 | to shower
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIDI-038 | DISPENSER: toilet paper, recessed | 1 | recessed or with 15kg breaking strength if wall mounted
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYWC-005 | TOILET SUITE: concealed cistern, floor mounted | 1 | accessible height for patient use
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-019 | SHOWER: fixed rose, anti ligature | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-024 | SPOUT: basin, anti ligature | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-002 | FLUSH BUTTON: toilet suite | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIBM-022 | MIRROR: fixed, safety glass, toughened and laminated, anti ligature | 1 | optional; glued to backing material and screw fixed. some jurisdictions may require material to be polycarbonate
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYBA-078 | BASIN: with integrated shelf | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-046 | TAPWARE: hot and cold taps, shower, anti ligature | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-047 | TAPWARE: hot and cold taps, basin, anti ligature | 1
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | ELBO-015 | SWITCH: light, single | 1 | outside door. may optionally be replaced with light motion sensor deactivation switch
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | optional, + indicator button & light
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | ITSE-045 | SENSOR: motion detection, for lighting control, flush to ceiling | 1 | optional
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | HYDR-010 | DRAIN: floor waste, anti ligature | 2
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | HYDR-011 | DRAIN: clear out, anti ligature | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles also acceptable
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | tiles also acceptable
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | for High Dependency and intensive care areas, consider plywood or equivalent backing to ceiling finish
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | door swing outward and anti ligature hardware
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FIRT-004 | GRAB RAIL: shower, anti ligature | 1 | optional, vertical
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FIRT-009 | GRAB RAIL: WC, anti ligature | 1 | optional, vertical
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FIHR-027 | HOOK: coat, collapsible, anti ligature | 2 | one at 1200AFFL for wheelchair users; dependent on jurisdictional policy
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FIRT-029 | TRACK: curtain, plastic, recessed | 1 | optional, for privacy screen to shower area, 15kg breaking strength recommended
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, collapsible; anti ligature fabric
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FIDI-051 | HOLDER: soap/shampoo, recessed, vertical format | 1 | to shower
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FIDI-038 | DISPENSER: toilet paper, recessed | 1 | recessed or with 15kg breaking strength if wall mounted
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | HYWC-005 | TOILET SUITE: concealed cistern, floor mounted | 1 | accessible height for patient use
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | HYTP-019 | SHOWER: fixed rose, anti ligature | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | HYTP-024 | SPOUT: basin, anti ligature | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | HYTP-002 | FLUSH BUTTON: toilet suite | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | FIBM-022 | MIRROR: fixed, safety glass, toughened and laminated, anti ligature | 1 | optional; glued to backing material and screw fixed. some jurisdictions may require material to be polycarbonate
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | HYBA-078 | BASIN: with integrated shelf | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | HYTP-046 | TAPWARE: hot and cold taps, shower, anti ligature | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | FFE | HYTP-047 | TAPWARE: hot and cold taps, basin, anti ligature | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | SE | ELBO-015 | SWITCH: light, single | 1 | may optionally be replaced with light motion sensor deactivation switch
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | optional, + indicator button & light
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | SE | ITSE-045 | SENSOR: motion detection, for lighting control, flush to ceiling | 1 | optional
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | SE | HYDR-010 | DRAIN: floor waste, anti ligature | 2
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | SE | HYDR-011 | DRAIN: clear out, anti ligature | 1
ENS-MH-B | Ensuite - Mental Health, Inboard Access from Corridor, 5m2 | SE | LIFX-035 | LIGHT: occupancy light | 1 | optional
ENS-SH | Ensuite - Shared, 6m2 | FA | FLVY-005 | FLOOR FINISH: vinyl, seamless, coved, non slip, studded | 1 | Tiles also acceptable
ENS-SH | Ensuite - Shared, 6m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-SH | Ensuite - Shared, 6m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn
ENS-SH | Ensuite - Shared, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
ENS-SH | Ensuite - Shared, 6m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-SH | Ensuite - Shared, 6m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
ENS-SH | Ensuite - Shared, 6m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn
ENS-SH | Ensuite - Shared, 6m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 2 | outward opening, privacy latch; no. to suit layout of room
ENS-SH | Ensuite - Shared, 6m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIJO-181 | JOINERY UNIT: vanity, single basin | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | MMGE-024 | CHAIR: shower | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FQGE-011 | CURTAIN: shower | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | optional
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 | 1 to side
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | drop down rail, optional for standard shared ensuite
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | to both sides of WC in additional access ensuite
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-016 | RAIL: towel | 2 | with grab rail strength and fixings
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYTP-020 | SHOWER: hand-held | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1
ENS-SH | Ensuite - Shared, 6m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-SH | Ensuite - Shared, 6m2 | SE | HYDR-004 | DRAIN: floor waste | 2
ENS-SH | Ensuite - Shared, 6m2 | SE | ELBO-015 | SWITCH: light, single | 2
ENS-SH | Ensuite - Shared, 6m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light
ENS-SH | Ensuite - Shared, 6m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-SH | Ensuite - Shared, 6m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ENS-SP | Ensuite - Special, 6m2 | FA | FLVY-005 | FLOOR FINISH: vinyl, seamless, coved, non slip, studded | 1 | Tiles also acceptable
ENS-SP | Ensuite - Special, 6m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-SP | Ensuite - Special, 6m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1
ENS-SP | Ensuite - Special, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
ENS-SP | Ensuite - Special, 6m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-SP | Ensuite - Special, 6m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
ENS-SP | Ensuite - Special, 6m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ENS-SP | Ensuite - Special, 6m2 | FA | DWSC-013 | DOOR: 1200mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch
ENS-SP | Ensuite - Special, 6m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | MMGE-024 | CHAIR: shower | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FQGE-011 | CURTAIN: shower | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | optional
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | optional
ENS-SP | Ensuite - Special, 6m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-016 | RAIL: towel | 2 | with grab rail strength and fixings
ENS-SP | Ensuite - Special, 6m2 | FFE | HYBA-012 | BASIN: handwash, Type C, with vanity unit | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | HYTP-020 | SHOWER: hand-held | 1
ENS-SP | Ensuite - Special, 6m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1
ENS-SP | Ensuite - Special, 6m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | + indicator button & light
ENS-SP | Ensuite - Special, 6m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ENS-SP | Ensuite - Special, 6m2 | SE | ELBO-015 | SWITCH: light, single | 1
ENS-SP | Ensuite - Special, 6m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
ENS-SP | Ensuite - Special, 6m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-SP | Ensuite - Special, 6m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | Suitable for barefeet. Tiles also acceptable.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant flush set plasterboard ceiling also acceptable
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | MMGE-024 | CHAIR: shower | 1 | Or commode chair or combined shower/commode chair.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIHR-026 | HOOK: coat | 2
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | Optional, depends on Infection Control Policy
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | Optional, depends on Infection Control Policy
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 x basin. 1 x shower (optional).
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | Locate on drop down rail.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 | 1 to side or wrap-around.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | Combined with hand held shower.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | Drop down rails on both sides of WC; 1 x toilet paper dispenser, 1 x patient staff call 1 x NC. Fixings to support bariatric capacity.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIRT-005 | GRAB RAIL: stainless steel | 1 | Behind toilet
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | Over basin
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 | Optional, depends on Waste Management Policy.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | FIRT-016 | RAIL: towel | 1 | With grab rail strength and fixings to support bariatric capacity.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 | Fixture mounted
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 | Tapware: mixer, wall mounted, shower.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1 | With backrest. Concealed cistern, optional.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 | With integral shelf for patient belongings or separate shelf.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light.
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-ST-A1 | Ensuite - Inboard - Alternative 1, 5m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | Suitable for barefeet. Tiles also acceptable.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant flush set plasterboard ceiling also acceptable
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | MMGE-024 | CHAIR: shower | 1 | Or commode chair or combined shower/commode chair.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIHR-026 | HOOK: coat | 2
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | Optional, depends on Infection Control Policy
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | Optional, depends on Infection Control Policy
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 x basin. 1 x shower (optional).
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | Locate on drop down rail.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 | 1 to side or wrap-around.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | Combined with hand held shower.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | Drop down rails on both sides of WC; 1 x toilet paper dispenser, 1 x patient staff call 1 x NC. Fixings to support bariatric capacity.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIRT-005 | GRAB RAIL: stainless steel | 1 | Behind toilet
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | Over basin
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 | Optional, depends on Waste Management Policy.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | FIRT-016 | RAIL: towel | 1 | With grab rail strength and fixings to support bariatric capacity.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 | Fixture mounted
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 | Tapware: mixer, wall mounted, shower.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1 | With backrest. Concealed cistern, optional.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 | With integral shelf for patient belongings or separate shelf.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light.
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-ST-A2 | Ensuite - Inboard - Alternative 2, 5m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | Suitable for barefeet. Tiles also acceptable.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant flush set plasterboard ceiling also acceptable
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | MMGE-024 | CHAIR: shower | 1 | Or commode chair or combined shower/commode chair.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIHR-026 | HOOK: coat | 2
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | Optional, depends on Infection Control Policy
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | Optional, depends on Infection Control Policy
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 x basin. 1 x shower (optional).
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | Locate on drop down rail.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 | 1 to side or wrap-around.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | Combined with hand held shower.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | Drop down rails on both sides of WC; 1 x toilet paper dispenser, 1 x patient staff call 1 x NC. Fixings to support bariatric capacity.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIRT-005 | GRAB RAIL: stainless steel | 1 | Behind toilet
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | Over basin
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 | Optional, depends on Waste Management Policy.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | FIRT-016 | RAIL: towel | 1 | With grab rail strength and fixings to support bariatric capacity.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 | Fixture mounted
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 | Tapware: mixer, wall mounted, shower.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1 | With backrest. Concealed cistern, optional.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 | With integral shelf for patient belongings or separate shelf.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light.
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-ST-A3 | Ensuite - Inboard - Alternative 3, 5m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | Suitable for barefeet. Tiles also acceptable.
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant flush set plasterboard ceiling also acceptable
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch
ENS-ST-B | Ensuite - Outboard, 5m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | MMGE-024 | CHAIR: shower | 1 | Or commode chair or combined shower/commode chair.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIHR-026 | HOOK: coat | 2
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | Optional, depends on Infection Control Policy
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | Optional, depends on Infection Control Policy
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 x basin. 1 x shower (optional).
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | Locate on drop down rail.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 | 1 to side or wrap-around.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | Combined with hand held shower.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | Drop down rails on both sides of WC; 1 x toilet paper dispenser, 1 x patient staff call 1 x NC. Fixings to support bariatric capacity.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIRT-005 | GRAB RAIL: stainless steel | 1 | Behind toilet
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | Over basin
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 | Optional, depends on Waste Management Policy.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | FIRT-016 | RAIL: towel | 1 | With grab rail strength and fixings to support bariatric capacity.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 | Fixture mounted
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 | Tapware: mixer, wall mounted, shower.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1 | With backrest. Concealed cistern, optional.
ENS-ST-B | Ensuite - Outboard, 5m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 | With integral shelf for patient belongings or separate shelf.
ENS-ST-B | Ensuite - Outboard, 5m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ENS-ST-B | Ensuite - Outboard, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light.
ENS-ST-B | Ensuite - Outboard, 5m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-ST-B | Ensuite - Outboard, 5m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | Suitable for barefeet. Tiles also acceptable.
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant flush set plasterboard ceiling also acceptable
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch
ENS-ST-C | Ensuite - Back to Back, 5m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | MMGE-024 | CHAIR: shower | 1 | Or commode chair or combined shower/commode chair.
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIHR-026 | HOOK: coat | 2
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | Optional, depends on Infection Control Policy
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | Optional, depends on Infection Control Policy
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 x basin. 1 x shower (optional).
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 | adjacent to toilet
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | Combined with hand held shower.
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | Optional, can also hold 1 x toilet paper dispenser
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIRT-005 | GRAB RAIL: stainless steel | 1 | behind toilet
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | Over basin
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 | Optional, depends on Waste Management Policy.
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | FIRT-016 | RAIL: towel | 1 | With grab rail strength and fixings to support bariatric capacity.
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 | Fixture mounted
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 | Tapware: mixer, wall mounted, shower.
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1 | With backrest. Concealed cistern, optional.
ENS-ST-C | Ensuite - Back to Back, 5m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 | With integral shelf for patient belongings or separate shelf.
ENS-ST-C | Ensuite - Back to Back, 5m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | SE | HYDR-004 | DRAIN: floor waste | 1
ENS-ST-C | Ensuite - Back to Back, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light.
ENS-ST-C | Ensuite - Back to Back, 5m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ENS-ST-C | Ensuite - Back to Back, 5m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
FLUO | Fluoroscopy Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
FLUO | Fluoroscopy Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 8
FLUO | Fluoroscopy Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
FLUO | Fluoroscopy Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
FLUO | Fluoroscopy Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
FLUO | Fluoroscopy Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2 | to prep. bench, basin & sink
FLUO | Fluoroscopy Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
FLUO | Fluoroscopy Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass, to control room
FLUO | Fluoroscopy Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 2
FLUO | Fluoroscopy Room | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
FLUO | Fluoroscopy Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
FLUO | Fluoroscopy Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 11
FLUO | Fluoroscopy Room | FFE | MGFP-002 | FLOWMETER: medical air | 1 | to services panel
FLUO | Fluoroscopy Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | wall mounted
FLUO | Fluoroscopy Room | FFE | MMGE-019 | CHAIR: patient | 1
FLUO | Fluoroscopy Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
FLUO | Fluoroscopy Room | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 2
FLUO | Fluoroscopy Room | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 2
FLUO | Fluoroscopy Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
FLUO | Fluoroscopy Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
FLUO | Fluoroscopy Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
FLUO | Fluoroscopy Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
FLUO | Fluoroscopy Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
FLUO | Fluoroscopy Room | FFE | MMGE-113 | TROLLEY: dressing | 1
FLUO | Fluoroscopy Room | FFE | FIHR-044 | RACK: lead apron | 1 | wall mounted
FLUO | Fluoroscopy Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
FLUO | Fluoroscopy Room | FFE | FIHR-011 | BRACKET: for monitor, wall mounted | 1
FLUO | Fluoroscopy Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | to services panel
FLUO | Fluoroscopy Room | FFE | MMGE-142 | TROLLEY: sharps bin | 1
FLUO | Fluoroscopy Room | FFE | MMGE-002 | ADAPTER: suction | 2
FLUO | Fluoroscopy Room | FFE | MMGE-100 | SUCTION BOTTLE | 2
FLUO | Fluoroscopy Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
FLUO | Fluoroscopy Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
FLUO | Fluoroscopy Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
FLUO | Fluoroscopy Room | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
FLUO | Fluoroscopy Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
FLUO | Fluoroscopy Room | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
FLUO | Fluoroscopy Room | FFE | MMHA-005 | MONITOR: patient, cardiac | 1 | wall mounted, can optionally be on a trolley
FLUO | Fluoroscopy Room | FFE | HYBA-051 | SINK: single | 1 | warm water
FLUO | Fluoroscopy Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
FLUO | Fluoroscopy Room | FFE | FIJO-060 | BENCH TOP: 600D, joinery under, stainless steel lipped | 1 | wet edge
FLUO | Fluoroscopy Room | FFE | MMMI-283 | BUCKY: wall, general X-Ray | 1 | optional
FLUO | Fluoroscopy Room | FFE | MMMI-121 | INJECTOR: mobile, fluoroscopy/screening | 1 | optional, if angiography procedures are undertaken
FLUO | Fluoroscopy Room | FFE | MMMI-122 | DISPLAY SCREEN: for fluoroscopy/screening | 2 | on articulated arm, ceiling mounted, no. of screens subject to equipment setup
FLUO | Fluoroscopy Room | FFE | MMMI-123 | SHIELD: radiation, upper body, mobile, fluoroscopy/screening | 1
FLUO | Fluoroscopy Room | FFE | MMMI-289 | STAND: ceiling, with traverse bridge, general X-Ray | 1
FLUO | Fluoroscopy Room | FFE | MMMI-124 | STAND: floor, with patient table, fluoroscopy/screening | 1
FLUO | Fluoroscopy Room | FFE | MMMI-128 | CONTROL UNIT: fluoroscopy, mobile | 1
FLUO | Fluoroscopy Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
FLUO | Fluoroscopy Room | FFE | MMSP-036 | PENDANT: single, dual arm, dual display screen | 1
FLUO | Fluoroscopy Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
FLUO | Fluoroscopy Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to prep bench, one outlet for telephone
FLUO | Fluoroscopy Room | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
FLUO | Fluoroscopy Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1
FLUO | Fluoroscopy Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel
FLUO | Fluoroscopy Room | SE | ELBO-001 | BUTTON: emergency stop | 1
FLUO | Fluoroscopy Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on services panel
FLUO | Fluoroscopy Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | number determined by number of doors, auto on when modality is in use
FLUO | Fluoroscopy Room | SE | ELBO-015 | SWITCH: light, single | 2 | to accessible change/wc/shwr.
FLUO | Fluoroscopy Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
FLUO | Fluoroscopy Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on services panel
FLUO | Fluoroscopy Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
FLUO | Fluoroscopy Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
FLUO | Fluoroscopy Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel
FLUO | Fluoroscopy Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | clock
FLUO | Fluoroscopy Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | to prep bench
FLUO | Fluoroscopy Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
FLUO | Fluoroscopy Room | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
FLUO | Fluoroscopy Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | flush mounted
FLUO | Fluoroscopy Room | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors as specified
FLUO | Fluoroscopy Room | SE | ELBO-012 | SWITCH: light, dimmer | 1 | to room
FLUO | Fluoroscopy Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
FLUO | Fluoroscopy Room | SE | ELGP-105 | GPO: single, on services panel | 4
FLUO | Fluoroscopy Room | SE | ELGP-130 | GPO: UPS, single | 1
FLUO | Fluoroscopy Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2
FLUOC | Fluoroscopy Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
FLUOC | Fluoroscopy Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
FLUOC | Fluoroscopy Control Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
FLUOC | Fluoroscopy Control Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
FLUOC | Fluoroscopy Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
FLUOC | Fluoroscopy Control Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
FLUOC | Fluoroscopy Control Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass
FLUOC | Fluoroscopy Control Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
FLUOC | Fluoroscopy Control Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
FLUOC | Fluoroscopy Control Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
FLUOC | Fluoroscopy Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
FLUOC | Fluoroscopy Control Room | FFE | DWWD-004 | BLIND: roller | 1 | to observation window for patient privacy
FLUOC | Fluoroscopy Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
FLUOC | Fluoroscopy Control Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
FLUOC | Fluoroscopy Control Room | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
FLUOC | Fluoroscopy Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
FLUOC | Fluoroscopy Control Room | FFE | FIHR-044 | RACK: lead apron | 1
FLUOC | Fluoroscopy Control Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
FLUOC | Fluoroscopy Control Room | FFE | FQCA-038 | FRIDGE: domestic, underbench, 80L | 1 | optional, with temperature alarm
FLUOC | Fluoroscopy Control Room | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 1
FLUOC | Fluoroscopy Control Room | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1
FLUOC | Fluoroscopy Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
FLUOC | Fluoroscopy Control Room | FFE | MMMI-115 | COMPUTER: CPU, fluoroscopy | 1
FLUOC | Fluoroscopy Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1 | communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
FLUOC | Fluoroscopy Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 2 | high bench at 900-950 AFFL optional
FLUOC | Fluoroscopy Control Room | FFE | MMMI-117 | CONSOLE: control, fluoroscopy/screening | 1
FLUOC | Fluoroscopy Control Room | FFE | FIJO-099 | CAC: cable access cap | 2
FLUOC | Fluoroscopy Control Room | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1
FLUOC | Fluoroscopy Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
FLUOC | Fluoroscopy Control Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 2
FLUOC | Fluoroscopy Control Room | FFE | FIHR-076 | BRACKET: for display screen, triple, desk mounted | 1
FLUOC | Fluoroscopy Control Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
FLUOC | Fluoroscopy Control Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 2
FLUOC | Fluoroscopy Control Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 outlet for slave display screen, one outlet for telephone
FLUOC | Fluoroscopy Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2
FLUOC | Fluoroscopy Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1 | main power emergency stop, consult equipment manufacturer for safety and compatibility with equipment.
FLUOC | Fluoroscopy Control Room | SE | ELGP-135 | GPO: UPS, single, wall mounted | 5
FLUOC | Fluoroscopy Control Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | auto on when modality is in use
FLUOC | Fluoroscopy Control Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
FLUOC | Fluoroscopy Control Room | SE | ELGP-208 | GPO: double, wall mounted | 1
FLUOC | Fluoroscopy Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4
FLUOC | Fluoroscopy Control Room | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 1
FLUOC | Fluoroscopy Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
FLUOC | Fluoroscopy Control Room | SE | WLSH-004 | SHIELDING: lead lining | 1 | to radiation consultant specification
FLUOC | Fluoroscopy Control Room | SE | ITSE-028 | INTERCOM: audiovisual, wall mounted | 1 | to screening room bed entry door
FLUOC | Fluoroscopy Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 2
GENXR | General X-Ray Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
GENXR | General X-Ray Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 14
GENXR | General X-Ray Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
GENXR | General X-Ray Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
GENXR | General X-Ray Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 6
GENXR | General X-Ray Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin; selection of splashback material to comply with AHFG Part D Infection Control
GENXR | General X-Ray Room | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
GENXR | General X-Ray Room | FA | DWGL-006 | DOOR: 910mm c/o, single leaf, observation panel, solid core/lead glass, lead shielding, paint | 1
GENXR | General X-Ray Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
GENXR | General X-Ray Room | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
GENXR | General X-Ray Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 12
GENXR | General X-Ray Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
GENXR | General X-Ray Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
GENXR | General X-Ray Room | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
GENXR | General X-Ray Room | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
GENXR | General X-Ray Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
GENXR | General X-Ray Room | FFE | MMMI-350 | SCREEN: radiation, lead glass | 1 | safety glass
GENXR | General X-Ray Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
GENXR | General X-Ray Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
GENXR | General X-Ray Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
GENXR | General X-Ray Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
GENXR | General X-Ray Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
GENXR | General X-Ray Room | FFE | FIHR-044 | RACK: lead apron | 1
GENXR | General X-Ray Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
GENXR | General X-Ray Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | to services panel
GENXR | General X-Ray Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
GENXR | General X-Ray Room | FFE | MMGE-002 | ADAPTER: suction | 1 | to services panel
GENXR | General X-Ray Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
GENXR | General X-Ray Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
GENXR | General X-Ray Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
GENXR | General X-Ray Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
GENXR | General X-Ray Room | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 1
GENXR | General X-Ray Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
GENXR | General X-Ray Room | FFE | MMBE-010 | BED: patient, electric with mattress | 1
GENXR | General X-Ray Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
GENXR | General X-Ray Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1
GENXR | General X-Ray Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 | to Control
GENXR | General X-Ray Room | FFE | MMMI-285 | CONSOLE: control, general X-Ray | 1
GENXR | General X-Ray Room | FFE | MMMI-293 | TABLE: floating top, general X-Ray | 1 | refer to manufacturer requirements, can optionally be elevating table
GENXR | General X-Ray Room | FFE | MMMI-283 | BUCKY: wall, general X-Ray | 1
GENXR | General X-Ray Room | FFE | MMMI-287 | GENERATOR: cabinet, general X-Ray | 1
GENXR | General X-Ray Room | FFE | MMMI-289 | STAND: ceiling, with traverse bridge, general X-Ray | 1
GENXR | General X-Ray Room | FFE | MMMI-295 | SCREEN: imaging stitching barrier | 1 | optional, may include one per facility
GENXR | General X-Ray Room | FFE | FIJO-029 | BENCH: 750D, open under, X-ray | 1
GENXR | General X-Ray Room | FFE | FIJO-099 | CAC: cable access cap | 2
GENXR | General X-Ray Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
GENXR | General X-Ray Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | to Control
GENXR | General X-Ray Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 1
GENXR | General X-Ray Room | FFE | FIHR-076 | BRACKET: for display screen, triple, desk mounted | 1
GENXR | General X-Ray Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
GENXR | General X-Ray Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 2
GENXR | General X-Ray Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | for phone
GENXR | General X-Ray Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | to radiation consultant's requirements
GENXR | General X-Ray Room | SE | ITSE-029 | INTERCOM: audio, wall mount | 1
GENXR | General X-Ray Room | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
GENXR | General X-Ray Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
GENXR | General X-Ray Room | SE | ELGP-135 | GPO: UPS, single, wall mounted | 3
GENXR | General X-Ray Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 3 | number determined by number of doors, auto on when modality is in use
GENXR | General X-Ray Room | SE | ELBO-015 | SWITCH: light, single | 1
GENXR | General X-Ray Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel; if located within the ED, quantity of services may need to align with acute treatment bays for trauma use
GENXR | General X-Ray Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel; if located within the ED, quantity of services may need to align with acute treatment bays for trauma use
GENXR | General X-Ray Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 2
GENXR | General X-Ray Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | for clock
GENXR | General X-Ray Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | to control
GENXR | General X-Ray Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4
GENXR | General X-Ray Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
GENXR | General X-Ray Room | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
GENXR | General X-Ray Room | SE | ITSE-008 | BUTTON: duress, mobile device | 1
GENXR | General X-Ray Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
GENXR | General X-Ray Room | SE | WLSH-004 | SHIELDING: lead lining | 1
GENXR | General X-Ray Room | SE | ELBO-012 | SWITCH: light, dimmer | 1 | optional
GENXR | General X-Ray Room | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel
GENXR | General X-Ray Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3
GENXR | General X-Ray Room | SE | ELGP-140 | GPO: three phase, single | 1
GYAH-GP | Gymnasium, Group Therapy | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
GYAH-GP | Gymnasium, Group Therapy | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
GYAH-GP | Gymnasium, Group Therapy | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
GYAH-GP | Gymnasium, Group Therapy | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
GYAH-GP | Gymnasium, Group Therapy | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 2
GYAH-GP | Gymnasium, Group Therapy | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
GYAH-GP | Gymnasium, Group Therapy | FA | DWSC-027 | DOOR: 1600mm c/o, 1 1/2 leaf, solid core, paint | 1 | optional, to equipment store
GYAH-GP | Gymnasium, Group Therapy | FA | DWGL-041 | DOOR: 1500mm c/o, 1 1/2 leaf, half glazed, solid core/glass, paint | 1
GYAH-GP | Gymnasium, Group Therapy | FA | CLCN-009 | CORNICE: wall trim fixing | 1
GYAH-GP | Gymnasium, Group Therapy | FA | FLVY-010 | FLOOR FINISH: vinyl, seamless, inset floor markings | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | MMAH-016 | ERGOMETER: arm | 2
GYAH-GP | Gymnasium, Group Therapy | FFE | FQBS-030 | CHAIR: visitor, patient | 2 | to arm ergometer
GYAH-GP | Gymnasium, Group Therapy | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
GYAH-GP | Gymnasium, Group Therapy | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | FQGE-010 | CURTAIN: privacy screen | 2 | to plinth
GYAH-GP | Gymnasium, Group Therapy | FFE | FQSN-007 | BIN: storage bins, wire mesh, stainless steel | 1 | to plinth
GYAH-GP | Gymnasium, Group Therapy | FFE | FIHR-029 | HOOK: equipment | 2 | to plinth
GYAH-GP | Gymnasium, Group Therapy | FFE | MMAH-002 | BICYCLE: exercise | 2
GYAH-GP | Gymnasium, Group Therapy | FFE | MMAH-003 | BICYCLE: exercise, recumbent | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 | to plinth
GYAH-GP | Gymnasium, Group Therapy | FFE | FIRT-017 | STEEL MESH: framed, ceiling mount | 1 | optional, to plinth
GYAH-GP | Gymnasium, Group Therapy | FFE | MMAH-035 | PLINTH: single width | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | FIHR-061 | RACK: weights | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | MMAH-019 | MACHINE: rowing | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | MMAH-020 | MACHINE: stepping | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | MMAH-027 | TREADMILL: automatic | 2
GYAH-GP | Gymnasium, Group Therapy | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 2 | for arm ergometer
GYAH-GP | Gymnasium, Group Therapy | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
GYAH-GP | Gymnasium, Group Therapy | FFE | FIJO-225 | CUPBOARD: tall, pigeon hole shelf unit, gymnasium | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | FIJO-227 | CUPBOARD: tall, double door, gym equipment storage | 1
GYAH-GP | Gymnasium, Group Therapy | FFE | FIRT-047 | TRACK: curtain, privacy, U shaped | 1
GYAH-GP | Gymnasium, Group Therapy | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to telephone
GYAH-GP | Gymnasium, Group Therapy | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to plinth
GYAH-GP | Gymnasium, Group Therapy | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | 1 x to plinth, 1 x at entry door
GYAH-GP | Gymnasium, Group Therapy | SE | ELBO-015 | SWITCH: light, single | 1
GYAH-GP | Gymnasium, Group Therapy | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | optional, to plinth
GYAH-GP | Gymnasium, Group Therapy | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | 1 x to plinth, 1 x at entry door
GYAH-GP | Gymnasium, Group Therapy | SE | ELGP-109 | GPO: single, wall mounted | 1 | to plinth
GYAH-GP | Gymnasium, Group Therapy | SE | ELGP-208 | GPO: double, wall mounted | 9 | quantity to suit equipment requirements
GYAH-GP | Gymnasium, Group Therapy | SE | ELGP-208 | GPO: double, wall mounted | 3 | to plinth
GYAH-GP | Gymnasium, Group Therapy | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
GYAH-ID | Gymnasium, Individual Treatment | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
GYAH-ID | Gymnasium, Individual Treatment | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
GYAH-ID | Gymnasium, Individual Treatment | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
GYAH-ID | Gymnasium, Individual Treatment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
GYAH-ID | Gymnasium, Individual Treatment | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1
GYAH-ID | Gymnasium, Individual Treatment | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
GYAH-ID | Gymnasium, Individual Treatment | FA | DWSC-027 | DOOR: 1600mm c/o, 1 1/2 leaf, solid core, paint | 1 | optional, to equipment store
GYAH-ID | Gymnasium, Individual Treatment | FA | DWGL-041 | DOOR: 1500mm c/o, 1 1/2 leaf, half glazed, solid core/glass, paint | 1
GYAH-ID | Gymnasium, Individual Treatment | FA | CLCN-009 | CORNICE: wall trim fixing | 1
GYAH-ID | Gymnasium, Individual Treatment | FA | FLVY-010 | FLOOR FINISH: vinyl, seamless, inset floor markings | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIBM-010 | MIRROR: fixed, safety glass, full length | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 4
GYAH-ID | Gymnasium, Individual Treatment | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 3
GYAH-ID | Gymnasium, Individual Treatment | FFE | FQGE-010 | CURTAIN: privacy screen | 3 | to plinths
GYAH-ID | Gymnasium, Individual Treatment | FFE | FQSN-007 | BIN: storage bins, wire mesh, stainless steel | 3 | to plinths
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIHR-029 | HOOK: equipment | 6 | to plinths
GYAH-ID | Gymnasium, Individual Treatment | FFE | MMAH-002 | BICYCLE: exercise | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 3 | to plinths
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIRT-017 | STEEL MESH: framed, ceiling mount | 3 | optional, to plinths
GYAH-ID | Gymnasium, Individual Treatment | FFE | MMAH-001 | BARS: parallel | 1 | bariatric capacity to be determine based on service requirements
GYAH-ID | Gymnasium, Individual Treatment | FFE | MMAH-033 | PLINTH: double width | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | MMAH-035 | PLINTH: single width | 2
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIHR-061 | RACK: weights | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 3
GYAH-ID | Gymnasium, Individual Treatment | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | MMAH-027 | TREADMILL: automatic | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 3
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
GYAH-ID | Gymnasium, Individual Treatment | FFE | FIJO-227 | CUPBOARD: tall, double door, gym equipment storage | 1
GYAH-ID | Gymnasium, Individual Treatment | FFE | MMAH-044 | STAIRS: exercise, 90 degree | 1
GYAH-ID | Gymnasium, Individual Treatment | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to telephone
GYAH-ID | Gymnasium, Individual Treatment | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | to plinths
GYAH-ID | Gymnasium, Individual Treatment | SE | ITCL-008 | BUTTON: nurse call, staff assist | 4 | 3 x to plinth, 1 x at entry door
GYAH-ID | Gymnasium, Individual Treatment | SE | ELBO-015 | SWITCH: light, single | 1
GYAH-ID | Gymnasium, Individual Treatment | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 3 | optional, to plinths
GYAH-ID | Gymnasium, Individual Treatment | SE | ITCL-004 | BUTTON: nurse call, emergency | 4 | 3 x to plinth, 1 x at entry door
GYAH-ID | Gymnasium, Individual Treatment | SE | ELGP-109 | GPO: single, wall mounted | 3 | to plinths
GYAH-ID | Gymnasium, Individual Treatment | SE | ELGP-208 | GPO: double, wall mounted | 3 | quantity to suit equipment requirements
GYAH-ID | Gymnasium, Individual Treatment | SE | ELGP-208 | GPO: double, wall mounted | 9 | to plinths
GYAH-ID | Gymnasium, Individual Treatment | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
HYDP | Hydrotherapy Pool | FA | FLGE-010 | FLOOR FINISH: tiles, ceramic, non-slip | 2
HYDP | Hydrotherapy Pool | FA | FLSK-004 | SKIRTING: tiles, coved, to match floor tiles | 12
HYDP | Hydrotherapy Pool | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 6
HYDP | Hydrotherapy Pool | FA | WLWA-011 | WALL FINISH: tiles, ceramic, glazed | 3 | to pool and all walls
HYDP | Hydrotherapy Pool | FA | CLFS-002 | CEILING: fibre cement, flush set, suspended, paint, washable | 1
HYDP | Hydrotherapy Pool | FA | DWWH-005 | WINDOW | 1 | desirable
HYDP | Hydrotherapy Pool | FA | DWOB-007 | OBSERVATION: internal window, alum/safety glass, powdercoat/paint | 4
HYDP | Hydrotherapy Pool | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 6 | to change rooms, cleaner's room, plant areas and alternate exit if required by BCA; lockable
HYDP | Hydrotherapy Pool | FA | DWGL-040 | DOOR: 1500mm c/o ,1 1/2 leaf, fully glazed, alum/safety glass, powdercoat/paint | 2 | to lobby/ waiting; lockable, restricted access
HYDP | Hydrotherapy Pool | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
HYDP | Hydrotherapy Pool | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
HYDP | Hydrotherapy Pool | FFE | MMAH-017 | HOIST: pool, hydraulic | 1 | weight limit requirement to be confirmed dependent on service requirements
HYDP | Hydrotherapy Pool | FFE | MMAH-032 | BLANKET: pool, auto-operated | 1 | optional, power requirements dependent on selected model
HYDP | Hydrotherapy Pool | FFE | ITBU-009 | CONTROL UNIT: public address system | 1 | for announcements and music
HYDP | Hydrotherapy Pool | SE | ITBU-020 | PUBLIC ADDRESS SYSTEM | 1
HYDP | Hydrotherapy Pool | SE | HYTP-008 | OUTLET: cold water | 1 | for washing down concourse
HYDP | Hydrotherapy Pool | SE | HYDR-004 | DRAIN: floor waste | 16 | every 3-4 metres on concourse
HYDP | Hydrotherapy Pool | SE | ELBO-015 | SWITCH: light, single | 1
HYDP | Hydrotherapy Pool | SE | ITCL-004 | BUTTON: nurse call, emergency | 4 | 1 each side of pool
HYDP | Hydrotherapy Pool | SE | ELGP-106 | GPO: single, special, for equipment | 1 | optional, for motorised pool blanket
HYDP | Hydrotherapy Pool | SE | ELGP-113 | GPO: single, wall mounted, waterproof, RCD protected | 4
INTF-MH | Interview Room - Mental Health | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
INTF-MH | Interview Room - Mental Health | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 1
INTF-MH | Interview Room - Mental Health | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional
INTF-MH | Interview Room - Mental Health | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2 | optional
INTF-MH | Interview Room - Mental Health | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
INTF-MH | Interview Room - Mental Health | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
INTF-MH | Interview Room - Mental Health | FA | DWWH-005 | WINDOW | 1 | optional
INTF-MH | Interview Room - Mental Health | FA | DWGL-007 | DOOR: 910mm c/o, single leaf, observation panel, solid core/safety glass, paint | 2 | privacy film to be applied to obs panel in second egress door
INTF-MH | Interview Room - Mental Health | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
INTF-MH | Interview Room - Mental Health | FFE | FQGE-002 | ARTWORK | 1
INTF-MH | Interview Room - Mental Health | FFE | DWWD-002 | BLIND: holland | 1 | optional, roller blind in community areas, integral venetian required for hospital areas
INTF-MH | Interview Room - Mental Health | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
INTF-MH | Interview Room - Mental Health | FFE | FQCW-016 | BIN: waste, general, 20L | 1
INTF-MH | Interview Room - Mental Health | FFE | FIBM-016 | NOTICEBOARD/WHITEBOARD: fixed, combined unit | 1
INTF-MH | Interview Room - Mental Health | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
INTF-MH | Interview Room - Mental Health | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
INTF-MH | Interview Room - Mental Health | FFE | FQBS-054 | STOOL: ottoman | 1
INTF-MH | Interview Room - Mental Health | FFE | FQBS-056 | CHAIR: tub, mental health | 3
INTF-MH | Interview Room - Mental Health | FFE | FQDW-040 | DESK: fixed height, 1200W x 750D x 720H | 1
INTF-MH | Interview Room - Mental Health | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
INTF-MH | Interview Room - Mental Health | SE | ELBO-015 | SWITCH: light, single | 1 | lighting to have controlled switching to create low stimulus environment
INTF-MH | Interview Room - Mental Health | SE | ELGP-208 | GPO: double, wall mounted | 2
INTF-MH | Interview Room - Mental Health | SE | ITSE-006 | BUTTON: duress, fixed | 2 | optional, depends on jurisdictional policy; mobile duress preferred
INTF-MH | Interview Room - Mental Health | SE | ITSE-038 | READER: access control, general | 1 | optional
INTV | Interview Room | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
INTV | Interview Room | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 6
INTV | Interview Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
INTV | Interview Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
INTV | Interview Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
INTV | Interview Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
INTV | Interview Room | FA | DWWH-005 | WINDOW | 1
INTV | Interview Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 2 | second door is optional for egress
INTV | Interview Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
INTV | Interview Room | FFE | FQGE-002 | ARTWORK | 1 | optional
INTV | Interview Room | FFE | DWWD-004 | BLIND: roller | 1
INTV | Interview Room | FFE | FQBS-010 | CHAIR: armchair | 1
INTV | Interview Room | FFE | FQBS-041 | LOUNGE: 2.5 seat | 1
INTV | Interview Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
INTV | Interview Room | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
INTV | Interview Room | FFE | FQTA-075 | TABLE: square, 600W, low height | 2
INTV | Interview Room | FFE | FQBS-058 | CHAIR: visitor, patient, with arms | 4
INTV | Interview Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2
INTV | Interview Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | optional, + indicator button & light
INTV | Interview Room | SE | ELBO-015 | SWITCH: light, single | 1
INTV | Interview Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | optional, + indicator button & light
INTV | Interview Room | SE | ELGP-208 | GPO: double, wall mounted | 2
INTV | Interview Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
INTV | Interview Room | SE | ITSE-038 | READER: access control, general | 1 | optional to second egress door
LAUN-MH | Laundry - Mental Health, 6m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
LAUN-MH | Laundry - Mental Health, 6m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
LAUN-MH | Laundry - Mental Health, 6m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | equal to Acrovyn
LAUN-MH | Laundry - Mental Health, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
LAUN-MH | Laundry - Mental Health, 6m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 | tiles also acceptable
LAUN-MH | Laundry - Mental Health, 6m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
LAUN-MH | Laundry - Mental Health, 6m2 | FA | DWOB-007 | OBSERVATION: internal window, alum/safety glass, powdercoat/paint | 1 | observation window
LAUN-MH | Laundry - Mental Health, 6m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | equal to Acrovyn
LAUN-MH | Laundry - Mental Health, 6m2 | FA | DWGL-007 | DOOR: 910mm c/o, single leaf, observation panel, solid core/safety glass, paint | 1 | lockable; anti ligature door harware
LAUN-MH | Laundry - Mental Health, 6m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FIHR-007 | BRACKET: for dryer | 1 | for dryer
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FQSN-023 | CABINET: ironing board | 1 | lockable, with integral ironing board
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1 | under laundry bench, lockable
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FQSM-030 | TROLLEY: laundry, basket | 1 | under bench
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FIJO-144 | CUPBOARD: wall mount, double door, adj shelves, anti ligature | 2
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FQGE-015 | DRYER: clothes, domestic | 1 | wall mounted
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FQGE-028 | IRON: clothes, electric | 1 | inside cupboard
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | HYBA-064 | SINK: single, laundry | 1 | warm water, with overflow drain
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FQCW-056 | MACHINE: washing, domestic | 1 | provide themostatic mixing valve to hot water or supply warm water
LAUN-MH | Laundry - Mental Health, 6m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | with inset laundry tub
LAUN-MH | Laundry - Mental Health, 6m2 | SE | ELPR-006 | RCD: residual current device | 1
LAUN-MH | Laundry - Mental Health, 6m2 | SE | HYTP-013 | OUTLET: hot water | 1
LAUN-MH | Laundry - Mental Health, 6m2 | SE | HYTP-008 | OUTLET: cold water | 1
LAUN-MH | Laundry - Mental Health, 6m2 | SE | HYDR-004 | DRAIN: floor waste | 1 | tamper proof
LAUN-MH | Laundry - Mental Health, 6m2 | SE | ELBO-015 | SWITCH: light, single | 1
LAUN-MH | Laundry - Mental Health, 6m2 | SE | ELGP-109 | GPO: single, wall mounted | 3 | washer, dryer, ironing cabinet
LAUN-MH | Laundry - Mental Health, 6m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
LAUN-PT | Laundry - Patient, 6m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
LAUN-PT | Laundry - Patient, 6m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | To be decided at project level.
LAUN-PT | Laundry - Patient, 6m2 | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1
LAUN-PT | Laundry - Patient, 6m2 | FA | WLWA-007 | WALL FINISH: splashback | 1 | Selection of material to comply with Part D Infection Prevention and Control AusHFG.
LAUN-PT | Laundry - Patient, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
LAUN-PT | Laundry - Patient, 6m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
LAUN-PT | Laundry - Patient, 6m2 | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | Observation window, optional
LAUN-PT | Laundry - Patient, 6m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
LAUN-PT | Laundry - Patient, 6m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable
LAUN-PT | Laundry - Patient, 6m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIHR-007 | BRACKET: for dryer | 1 | for dryer
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQSN-023 | CABINET: ironing board | 1 | lockable, with integral ironing board
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 2 | Over bench. Number to suit layout, refer RLS or project specific requirements. Some lockable space may be needed.
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQSM-030 | TROLLEY: laundry, basket | 1 | under bench
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQGE-015 | DRYER: clothes, domestic | 1 | wall mounted @ 600mm AFFL on bracket
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQGE-028 | IRON: clothes, electric | 1 | inside cupboard, hardwired.
LAUN-PT | Laundry - Patient, 6m2 | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
LAUN-PT | Laundry - Patient, 6m2 | FFE | HYBA-064 | SINK: single, laundry | 1 | with overflow drain, warm water, sinlge mixer to tub optional
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQCW-056 | MACHINE: washing, domestic | 1 | heavy duty
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | With inset laundry tub, open under part. Length to suit layout, refer RLS or project specific requirements.
LAUN-PT | Laundry - Patient, 6m2 | SE | HYTP-013 | OUTLET: hot water | 1 | to washing machine
LAUN-PT | Laundry - Patient, 6m2 | SE | HYTP-008 | OUTLET: cold water | 1
LAUN-PT | Laundry - Patient, 6m2 | SE | HYDR-004 | DRAIN: floor waste | 1
LAUN-PT | Laundry - Patient, 6m2 | SE | MEEX-002 | EXHAUST: dryer | 1
LAUN-PT | Laundry - Patient, 6m2 | SE | ELBO-015 | SWITCH: light, single | 1
LAUN-PT | Laundry - Patient, 6m2 | SE | ELGP-209 | GPO: double, wall mounted, RCD protected | 1 | 30mA RCD protection, above bench
LAUN-PT | Laundry - Patient, 6m2 | SE | ELGP-111 | GPO: single, wall mounted, RCD protected | 3 | 30mA RCD protection, washer, dryer, ironing cabinet,
LINAC | Linear Accelerator Treatment Room | FA | FLVY-001 | FLOOR FINISH: vinyl, seamless, coved, anti-static | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
LINAC | Linear Accelerator Treatment Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 18
LINAC | Linear Accelerator Treatment Room | FA | WLPR-006 | WALL PROTECTION: corner guards | 9
LINAC | Linear Accelerator Treatment Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
LINAC | Linear Accelerator Treatment Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 14
LINAC | Linear Accelerator Treatment Room | FA | WLWA-022 | WALL FINISH: vinyl, to 900 AFFL | 16
LINAC | Linear Accelerator Treatment Room | FA | CLFS-005 | CEILING: plasterboard, flush set, suspended, paint, scrub resistant | 1
LINAC | Linear Accelerator Treatment Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | inset area above machine as requried
LINAC | Linear Accelerator Treatment Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
LINAC | Linear Accelerator Treatment Room | FFE | DWGE-013 | GATE: single leaf, steel, prefinished | 1
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
LINAC | Linear Accelerator Treatment Room | FFE | FIDI-006 | DISPENSER: cleaning wipes | 1
LINAC | Linear Accelerator Treatment Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 3
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-140 | CUPBOARD: underbench, single door, adj shelves | 1
LINAC | Linear Accelerator Treatment Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 2
LINAC | Linear Accelerator Treatment Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
LINAC | Linear Accelerator Treatment Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
LINAC | Linear Accelerator Treatment Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
LINAC | Linear Accelerator Treatment Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMGE-110 | TROLLEY: clean linen, small | 1
LINAC | Linear Accelerator Treatment Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
LINAC | Linear Accelerator Treatment Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMGE-002 | ADAPTER: suction | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
LINAC | Linear Accelerator Treatment Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
LINAC | Linear Accelerator Treatment Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
LINAC | Linear Accelerator Treatment Room | FFE | ITCL-012 | CAMERA: observation | 6 | 1 x optional, for total body irradiation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
LINAC | Linear Accelerator Treatment Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | workstation on wheels is also acceptable
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-004 | LINEAR ACCELERATOR | 1
LINAC | Linear Accelerator Treatment Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 2 | for patient's own music, individual to each bunker from control room, hearing loop required to speakers
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-058 | BENCH TOP: 600D, joinery under | 3
LINAC | Linear Accelerator Treatment Room | FFE | ITAV-010 | MICROPHONE: ceiling mounted | 2
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-165 | CUPBOARD: tall, applicator storage, radiotherapy | 1 | custom joinery is required for vendor specific electron cones, including sliding rails, shelving to be reinforced for electron shields
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-166 | CUPBOARD: tall, shelving, horizontal patient device storage, radiotherapy | 3 | wide span shelving to be reinforced
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-167 | CUPBOARD: tall, shelving, vertical patient device storage, radiotherapy | 2
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead is also acceptable
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
LINAC | Linear Accelerator Treatment Room | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1
LINAC | Linear Accelerator Treatment Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | to wall mounted computer, may be wireless
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-077 | BRACKET: for observation camera, ceiling mounted | 6 | 1 x optional, to additional patient observation camera if provided
LINAC | Linear Accelerator Treatment Room | FFE | ITNE-073 | DISPLAY SCREEN: patient treatment information | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-006 | ACCESS PANEL: medical physics port | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-013 | DISPLAY SCREEN: radiotherapy, ceiling mounted | 2
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-015 | LASER: radiotherapy, ceiling mounted | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-016 | LASER: radiotherapy, lateral laser | 2
LINAC | Linear Accelerator Treatment Room | FFE | FIJO-231 | CUPBOARD: radiotherapy, laser enclosure | 3
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-017 | LASER: radiotherapy, sagittal laser | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-008 | DEVICE: surface guided radiation therapy system | 3 | as required for respiratory gating / motion management / surface guidance systems, to suit service requirements
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-011 | DEVICE: radiotherapy, daily QA | 1
LINAC | Linear Accelerator Treatment Room | FFE | MMRA-012 | GATE: light gate, radiotherapy bunker | 1
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-093 | BRACKET: keyboard shelf, wall mounted | 1
LINAC | Linear Accelerator Treatment Room | FFE | FIHR-089 | BRACKET: surface guided radiation therapy system, ceiling mounted | 3
LINAC | Linear Accelerator Treatment Room | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 11 | 1 x optional, to additional patient observation camera if provided
LINAC | Linear Accelerator Treatment Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3
LINAC | Linear Accelerator Treatment Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
LINAC | Linear Accelerator Treatment Room | SE | ELPR-006 | RCD: residual current device | 5
LINAC | Linear Accelerator Treatment Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
LINAC | Linear Accelerator Treatment Room | SE | ELBO-001 | BUTTON: emergency stop | 4
LINAC | Linear Accelerator Treatment Room | SE | LIFX-004 | LIGHT: illuminated sign, "Beam On-Beam Off" | 1
LINAC | Linear Accelerator Treatment Room | SE | ELBO-010 | SWITCH: light, 2-way | 2
LINAC | Linear Accelerator Treatment Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
LINAC | Linear Accelerator Treatment Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
LINAC | Linear Accelerator Treatment Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
LINAC | Linear Accelerator Treatment Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4
LINAC | Linear Accelerator Treatment Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2
LINAC | Linear Accelerator Treatment Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
LINAC | Linear Accelerator Treatment Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
LINAC | Linear Accelerator Treatment Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
LINAC | Linear Accelerator Treatment Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3
LINAC | Linear Accelerator Treatment Room | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 12 | 1 x to ceiling mounted laser, 1 x optional, to additional patient observation camera if provided
LINAC | Linear Accelerator Treatment Room | SE | ELGP-220.1 | GPO: emergency power, double (V) | 5 | to wall mounted lasers
LINAC | Linear Accelerator Treatment Room | SE | ELBO-019 | BUTTON: last person out | 1
LINAC | Linear Accelerator Treatment Room | SE | LIFX-038 | LIGHT: backlit feature panels | 2
LINAC-CR | Linear Accelerator Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
LINAC-CR | Linear Accelerator Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9
LINAC-CR | Linear Accelerator Control Room | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1 | optional
LINAC-CR | Linear Accelerator Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
LINAC-CR | Linear Accelerator Control Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
LINAC-CR | Linear Accelerator Control Room | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional
LINAC-CR | Linear Accelerator Control Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
LINAC-CR | Linear Accelerator Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 5
LINAC-CR | Linear Accelerator Control Room | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
LINAC-CR | Linear Accelerator Control Room | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 5
LINAC-CR | Linear Accelerator Control Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
LINAC-CR | Linear Accelerator Control Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1 | may be bench mounted, or integrated with microphone
LINAC-CR | Linear Accelerator Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
LINAC-CR | Linear Accelerator Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1
LINAC-CR | Linear Accelerator Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 2
LINAC-CR | Linear Accelerator Control Room | FFE | FIJO-099 | CAC: cable access cap | 8
LINAC-CR | Linear Accelerator Control Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead is also acceptable
LINAC-CR | Linear Accelerator Control Room | FFE | FIJO-213 | PANEL: joinery carcass end | 2
LINAC-CR | Linear Accelerator Control Room | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 2 | to patient observation monitors
LINAC-CR | Linear Accelerator Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | for patient observation cameras to control pan, tilt and zoom; may be custom control depending on camera system
LINAC-CR | Linear Accelerator Control Room | FFE | FIHR-080 | BRACKET: for bench, 750D, wall mounted | 5 | legs are also acceptable, quantity to be confirmed to achieve required support, ensure location does not impact leg clearance at workstations
LINAC-CR | Linear Accelerator Control Room | FFE | ITNE-071 | COMPUTER: desktop, with dual display screens | 2 | for access to local network including patient records and images for planning and reporting
LINAC-CR | Linear Accelerator Control Room | FFE | MMRA-006 | ACCESS PANEL: medical physics port | 1
LINAC-CR | Linear Accelerator Control Room | FFE | MMRA-009 | COMPUTER: linear accelerator control system PC | 6 | quantity to be confirmed based on vendor and equipment requirements; current provision allows for 1 x linear accelerator control system, 1 x record and verify system, and 2-4 x imaging and patient set up systems (e.g. gating and patient positioning).
LINAC-CR | Linear Accelerator Control Room | FFE | MMRA-010 | CONSOLE: control, linear accelerator | 1
LINAC-CR | Linear Accelerator Control Room | FFE | MMRA-007 | CABINET: linear accelerator computer cabinet | 1 | size, configuration and location to be confirmed by vendor
LINAC-CR | Linear Accelerator Control Room | FFE | ITNE-074 | DISPLAY SCREEN: patient observation | 2
LINAC-CR | Linear Accelerator Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3
LINAC-CR | Linear Accelerator Control Room | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 8 | quantity to suit computer and display screen requirements
LINAC-CR | Linear Accelerator Control Room | SE | ELPR-006 | RCD: residual current device | 3
LINAC-CR | Linear Accelerator Control Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
LINAC-CR | Linear Accelerator Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1 | may be integral to linear accelerator control console
LINAC-CR | Linear Accelerator Control Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
LINAC-CR | Linear Accelerator Control Room | SE | ELGP-208 | GPO: double, wall mounted | 10
LINAC-CR | Linear Accelerator Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 14 | quantity to suit computer and display screen requirements
LINAC-CR | Linear Accelerator Control Room | SE | ELGP-106 | GPO: single, special, for equipment | 1 | to linear accelerator computer cabinet
LINAC-CR | Linear Accelerator Control Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
LINAC-CR | Linear Accelerator Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
LINAC-CR | Linear Accelerator Control Room | SE | ITIN-055 | OUTLET: data, USB, wall mounted | 1 | connection for music to bunker
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | carpet tiles are also acceptable
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | to be feather edge vinyl for carpet tiles
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | DWWH-005 | WINDOW | 1 | natural light and external outlook is essential
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | DWGL-002 | DOOR: 910mm c/o, single leaf, half glazed, solid core/glass, paint | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FFE | FQGE-002 | ARTWORK | 2
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FFE | MMGE-019 | CHAIR: patient | 2 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FFE | DWWD-004 | BLIND: roller | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FFE | FQBS-043 | LOUNGE: 2 seat, 1600 wide | 1 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | FFE | FQTA-075 | TABLE: square, 600W, low height | 2 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to television, MATV outlet may also be provided depending on local ICT policies
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 3 | 1 to television, 2 to room
LNGE-10 | Lounge - Patient / Visitor, 10m2 | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | carpet tiles are also acceptable
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | to be feather edge vinyl for carpet tiles
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | DWGL-061 | DOOR: 1800mm c/o, double leaf, half glazed, solid core/glass, paint | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | DWWH-005 | WINDOW | 1 | natural light and external outlook is essential
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | FQGE-002 | ARTWORK | 2
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | FQBS-039 | LOUNGE: 1 seat | 2 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | MMGE-019 | CHAIR: patient | 2 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | DWWD-004 | BLIND: roller | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | FQBS-043 | LOUNGE: 2 seat, 1600 wide | 2 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | FIHR-045 | RACK: magazine/pamphlet | 1 | optional
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | FFE | FQTA-075 | TABLE: square, 600W, low height | 2 | furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to television, MATV outlet may also be provided depending on local ICT policies
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ELBO-015 | SWITCH: light, single | 1
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 3 | 1 to television, 2 to room
LNGE-20 | Lounge - Patient / Visitor, 20m2 | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
MAMMO | Mammography Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
MAMMO | Mammography Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
MAMMO | Mammography Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
MAMMO | Mammography Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
MAMMO | Mammography Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MAMMO | Mammography Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
MAMMO | Mammography Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiled ceiling also acceptable if interventional procedures are not undertaken
MAMMO | Mammography Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
MAMMO | Mammography Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MAMMO | Mammography Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 6
MAMMO | Mammography Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
MAMMO | Mammography Room | FFE | FIHR-005 | BRACKET: for display screen, PACS, wall mounted | 1
MAMMO | Mammography Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 | to desk
MAMMO | Mammography Room | FFE | MMGE-019 | CHAIR: patient | 1
MAMMO | Mammography Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MAMMO | Mammography Room | FFE | FIHR-026 | HOOK: coat | 2 | optional, for patient changing, 1 @1200H
MAMMO | Mammography Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to entry door
MAMMO | Mammography Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
MAMMO | Mammography Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
MAMMO | Mammography Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
MAMMO | Mammography Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
MAMMO | Mammography Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
MAMMO | Mammography Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
MAMMO | Mammography Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
MAMMO | Mammography Room | FFE | FIHR-055 | RACK: scanhead | 1
MAMMO | Mammography Room | FFE | MMGE-002 | ADAPTER: suction | 1
MAMMO | Mammography Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
MAMMO | Mammography Room | FFE | FQSM-003 | PEDESTAL: mobile, wire basket unit, 840H | 1
MAMMO | Mammography Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
MAMMO | Mammography Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
MAMMO | Mammography Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
MAMMO | Mammography Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | to desk
MAMMO | Mammography Room | FFE | MMMI-159 | DEVICE: imaging, mammography | 1
MAMMO | Mammography Room | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 1
MAMMO | Mammography Room | FFE | MMMI-162 | CONSOLE: control, mammography | 1
MAMMO | Mammography Room | FFE | FIJO-099 | CAC: cable access cap | 1
MAMMO | Mammography Room | FFE | FIRT-040 | TRACK: curtain, privacy, L shaped, angled | 1
MAMMO | Mammography Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
MAMMO | Mammography Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 1
MAMMO | Mammography Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
MAMMO | Mammography Room | FFE | ITNE-070 | DISPLAY SCREEN: PACS | 2
MAMMO | Mammography Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3
MAMMO | Mammography Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to desk, 1 outlet for telephone
MAMMO | Mammography Room | SE | ELPR-006 | RCD: residual current device | 2 | to services panel
MAMMO | Mammography Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on service panel
MAMMO | Mammography Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | auto on when modality is in use
MAMMO | Mammography Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
MAMMO | Mammography Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
MAMMO | Mammography Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
MAMMO | Mammography Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | x-ray viewer
MAMMO | Mammography Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | clock
MAMMO | Mammography Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2
MAMMO | Mammography Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
MAMMO | Mammography Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3 | imaging and control equipment
MAMMO | Mammography Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
MAMMO | Mammography Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
MAMMO | Mammography Room | SE | WLSH-004 | SHIELDING: lead lining | 1
MAMMO | Mammography Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
MAMMO | Mammography Room | SE | ELGP-105 | GPO: single, on services panel | 2
MAMMO | Mammography Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2
MED-14 | Medication Room, 14m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
MED-14 | Medication Room, 14m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9
MED-14 | Medication Room, 14m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
MED-14 | Medication Room, 14m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
MED-14 | Medication Room, 14m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MED-14 | Medication Room, 14m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 4 | extent dependent on type and height storage solution
MED-14 | Medication Room, 14m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
MED-14 | Medication Room, 14m2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
MED-14 | Medication Room, 14m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MED-14 | Medication Room, 14m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1 | extent dependent on type and height storage solution
MED-14 | Medication Room, 14m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
MED-14 | Medication Room, 14m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1
MED-14 | Medication Room, 14m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
MED-14 | Medication Room, 14m2 | FFE | MMGE-087 | SAFE: dangerous drugs, medium | 1 | size and quantity to be based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 5
MED-14 | Medication Room, 14m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
MED-14 | Medication Room, 14m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
MED-14 | Medication Room, 14m2 | FFE | ITSE-012 | CAMERA: CCTV | 1 | optional, provision and placement dependent on local policies
MED-14 | Medication Room, 14m2 | FFE | MMGE-034 | FRIDGE: drugs, large | 1 | size and quantity to be based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
MED-14 | Medication Room, 14m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
MED-14 | Medication Room, 14m2 | FFE | FQSM-046 | SHELVING: storage solution, 600W x 400D x 2100H nom., wire, mobile | 3 | type and quantity of storage options to be determined based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FQCW-061 | BIN: waste, pharmaceutical | 1
MED-14 | Medication Room, 14m2 | FFE | FQSM-048 | SHELVING: storage solution, shelving, 600W x 400D x 2100H nom., wire, mobile | 2 | type and quantity of storage options to be determined based on service requirements
MED-14 | Medication Room, 14m2 | FFE | FIDI-052 | DISPENSER: sticker roll | 1 | optional
MED-14 | Medication Room, 14m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to drug fridge, for temperature monitoring
MED-14 | Medication Room, 14m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 2x optional, for future provision of automated dispensing cabinets
MED-14 | Medication Room, 14m2 | SE | LIFX-008 | LIGHT: task light, built in | 1 | under wall mounted joinery
MED-14 | Medication Room, 14m2 | SE | ELBO-015 | SWITCH: light, single | 2 | 1 x general room lighting, 1 x task light
MED-14 | Medication Room, 14m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
MED-14 | Medication Room, 14m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | optional, for future provision of automated dispensing cabinets
MED-14 | Medication Room, 14m2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to drug fridge
MED-14 | Medication Room, 14m2 | SE | ITSE-038 | READER: access control, general | 1
MEET-15 | Meeting Room, 15m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
MEET-15 | Meeting Room, 15m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
MEET-15 | Meeting Room, 15m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
MEET-15 | Meeting Room, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MEET-15 | Meeting Room, 15m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
MEET-15 | Meeting Room, 15m2 | FA | DWWH-005 | WINDOW | 1 | desirable
MEET-15 | Meeting Room, 15m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional lockable
MEET-15 | Meeting Room, 15m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
MEET-15 | Meeting Room, 15m2 | FFE | DWWD-004 | BLIND: roller | 1
MEET-15 | Meeting Room, 15m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
MEET-15 | Meeting Room, 15m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
MEET-15 | Meeting Room, 15m2 | FFE | FIJO-194 | SHELF: laminate | 1
MEET-15 | Meeting Room, 15m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
MEET-15 | Meeting Room, 15m2 | FFE | ITAV-006 | CONTROL PANEL: AV system, wall mount | 1 | may be wall mounted or on table top
MEET-15 | Meeting Room, 15m2 | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 1
MEET-15 | Meeting Room, 15m2 | FFE | FQBS-059 | CHAIR: meeting rom, stackable | 8
MEET-15 | Meeting Room, 15m2 | FFE | ITAV-062 | CONTROL PANEL: room booking system | 1 | optional
MEET-15 | Meeting Room, 15m2 | FFE | ITAV-063 | COMPUTER: AV system | 1
MEET-15 | Meeting Room, 15m2 | FFE | ITAV-090 | SOUNDBAR: AV system, camera, speaker and microphone | 1 | functions may be provided by individual items dependent on local ICT policies and service requirements
MEET-15 | Meeting Room, 15m2 | FFE | FQTA-086 | TABLE: meeting room, folding | 2 | with services box if floor box provided
MEET-15 | Meeting Room, 15m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | optional, 1 to room booking panel and 1 to video conferencing control panel if provided
MEET-15 | Meeting Room, 15m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
MEET-15 | Meeting Room, 15m2 | SE | ITIN-046 | OUTLET: data, quad RJ45, wall mounted | 1 | optional
MEET-15 | Meeting Room, 15m2 | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 1 | optional
MEET-15 | Meeting Room, 15m2 | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 1 | optional; services may be wall mounted depending on layout and service requirements
MEET-15 | Meeting Room, 15m2 | SE | ELBO-015 | SWITCH: light, single | 1
MEET-15 | Meeting Room, 15m2 | SE | ELGP-208 | GPO: double, wall mounted | 4 | 3 are optional, to suit video conferencing and AV equipment as required
MEET-15 | Meeting Room, 15m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
MEET-15 | Meeting Room, 15m2 | SE | ELGP-203 | GPO: double, in floorbox | 1 | optional
MEET-15 | Meeting Room, 15m2 | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 1 | optional; to table if floor box provided
MEET-20 | Meeting Room, 20m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
MEET-20 | Meeting Room, 20m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
MEET-20 | Meeting Room, 20m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
MEET-20 | Meeting Room, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MEET-20 | Meeting Room, 20m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
MEET-20 | Meeting Room, 20m2 | FA | DWWH-005 | WINDOW | 1 | desirable
MEET-20 | Meeting Room, 20m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional lockable
MEET-20 | Meeting Room, 20m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
MEET-20 | Meeting Room, 20m2 | FFE | DWWD-004 | BLIND: roller | 1
MEET-20 | Meeting Room, 20m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 | optional
MEET-20 | Meeting Room, 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
MEET-20 | Meeting Room, 20m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
MEET-20 | Meeting Room, 20m2 | FFE | FIJO-194 | SHELF: laminate | 1
MEET-20 | Meeting Room, 20m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
MEET-20 | Meeting Room, 20m2 | FFE | ITNE-004 | CAMERA: video conferencing | 1 | optional, multidirectional, may be provided to support camera in soundbar as required
MEET-20 | Meeting Room, 20m2 | FFE | ITAV-006 | CONTROL PANEL: AV system, wall mount | 1 | may be wall mounted or on table top
MEET-20 | Meeting Room, 20m2 | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 1
MEET-20 | Meeting Room, 20m2 | FFE | FQBS-059 | CHAIR: meeting rom, stackable | 12
MEET-20 | Meeting Room, 20m2 | FFE | ITAV-062 | CONTROL PANEL: room booking system | 1 | optional
MEET-20 | Meeting Room, 20m2 | FFE | ITAV-063 | COMPUTER: AV system | 1
MEET-20 | Meeting Room, 20m2 | FFE | ITAV-071 | MICROPHONE: AV system, ceiling mounted, array | 1 | optional, may be recessed in ceiling
MEET-20 | Meeting Room, 20m2 | FFE | ITAV-090 | SOUNDBAR: AV system, camera, speaker and microphone | 1 | functions may be provided by individual items dependent on local ICT policies and service requirements
MEET-20 | Meeting Room, 20m2 | FFE | FQTA-086 | TABLE: meeting room, folding | 2 | with services box if floor box provided
MEET-20 | Meeting Room, 20m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 is optional for booking system if provided
MEET-20 | Meeting Room, 20m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
MEET-20 | Meeting Room, 20m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2
MEET-20 | Meeting Room, 20m2 | SE | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | to microphone array
MEET-20 | Meeting Room, 20m2 | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 1 | optional
MEET-20 | Meeting Room, 20m2 | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 1 | optional; services may be wall mounted depending on layout and service requirements
MEET-20 | Meeting Room, 20m2 | SE | ELBO-015 | SWITCH: light, single | 1
MEET-20 | Meeting Room, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 4
MEET-20 | Meeting Room, 20m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
MEET-20 | Meeting Room, 20m2 | SE | ELGP-203 | GPO: double, in floorbox | 1 | optional
MEET-20 | Meeting Room, 20m2 | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 1 | optional; to table if floor box provided
MEET-30 | Meeting Room, 30m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
MEET-30 | Meeting Room, 30m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
MEET-30 | Meeting Room, 30m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
MEET-30 | Meeting Room, 30m2 | FA | WLWA-001 | WALL FINISH: acoustic panels, prefinished | 12 | optional; to suit acoustic requirements
MEET-30 | Meeting Room, 30m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MEET-30 | Meeting Room, 30m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
MEET-30 | Meeting Room, 30m2 | FA | DWWH-005 | WINDOW | 1 | desirable
MEET-30 | Meeting Room, 30m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional lockable
MEET-30 | Meeting Room, 30m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
MEET-30 | Meeting Room, 30m2 | FFE | DWWD-004 | BLIND: roller | 1
MEET-30 | Meeting Room, 30m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
MEET-30 | Meeting Room, 30m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
MEET-30 | Meeting Room, 30m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
MEET-30 | Meeting Room, 30m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
MEET-30 | Meeting Room, 30m2 | FFE | ITNE-004 | CAMERA: video conferencing | 1 | multidirectional
MEET-30 | Meeting Room, 30m2 | FFE | ITAV-057 | SPEAKER: ceiling recessed | 4 | to replace or support audio from soundbar as required
MEET-30 | Meeting Room, 30m2 | FFE | FIJO-011 | BENCH: 450D, open under, laminate finish | 1
MEET-30 | Meeting Room, 30m2 | FFE | ITAV-006 | CONTROL PANEL: AV system, wall mount | 1 | may be wall mounted or on table top
MEET-30 | Meeting Room, 30m2 | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 1
MEET-30 | Meeting Room, 30m2 | FFE | FIJO-099 | CAC: cable access cap | 1
MEET-30 | Meeting Room, 30m2 | FFE | FIHR-065 | BRACKET: for bench, 450D, wall mounted | 2
MEET-30 | Meeting Room, 30m2 | FFE | FQBS-059 | CHAIR: meeting rom, stackable | 18
MEET-30 | Meeting Room, 30m2 | FFE | ITAV-062 | CONTROL PANEL: room booking system | 1 | optional
MEET-30 | Meeting Room, 30m2 | FFE | ITAV-063 | COMPUTER: AV system | 1
MEET-30 | Meeting Room, 30m2 | FFE | ITAV-071 | MICROPHONE: AV system, ceiling mounted, array | 1 | may be recessed in ceiling
MEET-30 | Meeting Room, 30m2 | FFE | FQTA-086 | TABLE: meeting room, folding | 3 | with services boxes to connect to floor boxes
MEET-30 | Meeting Room, 30m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 is optional for booking system if provided
MEET-30 | Meeting Room, 30m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
MEET-30 | Meeting Room, 30m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2
MEET-30 | Meeting Room, 30m2 | SE | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | to microphone array
MEET-30 | Meeting Room, 30m2 | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 2
MEET-30 | Meeting Room, 30m2 | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 2
MEET-30 | Meeting Room, 30m2 | SE | ELBO-015 | SWITCH: light, single | 1
MEET-30 | Meeting Room, 30m2 | SE | ELGP-208 | GPO: double, wall mounted | 4
MEET-30 | Meeting Room, 30m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
MEET-30 | Meeting Room, 30m2 | SE | ELGP-203 | GPO: double, in floorbox | 2
MEET-30 | Meeting Room, 30m2 | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 2 | to tables to connect to floor boxes
MEET-55 | Meeting Room, 55m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
MEET-55 | Meeting Room, 55m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
MEET-55 | Meeting Room, 55m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 2
MEET-55 | Meeting Room, 55m2 | FA | WLWA-001 | WALL FINISH: acoustic panels, prefinished | 12 | optional; to suit acoustic requirements
MEET-55 | Meeting Room, 55m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MEET-55 | Meeting Room, 55m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
MEET-55 | Meeting Room, 55m2 | FA | DWGL-052 | DOOR: 1600mm c/o, double leaf, observation panel, solid core/glass, paint | 1 | optional lockable
MEET-55 | Meeting Room, 55m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
MEET-55 | Meeting Room, 55m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
MEET-55 | Meeting Room, 55m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
MEET-55 | Meeting Room, 55m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
MEET-55 | Meeting Room, 55m2 | FFE | FQDW-006 | LECTERN: mobile | 1
MEET-55 | Meeting Room, 55m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
MEET-55 | Meeting Room, 55m2 | FFE | ITNE-004 | CAMERA: video conferencing | 1
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-057 | SPEAKER: ceiling recessed | 6
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-006 | CONTROL PANEL: AV system, wall mount | 1
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 1
MEET-55 | Meeting Room, 55m2 | FFE | FQBS-059 | CHAIR: meeting rom, stackable | 42
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-062 | CONTROL PANEL: room booking system | 1 | optional
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-063 | COMPUTER: AV system | 1
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-064 | CAMERA: AV system, ceiling mounted | 1 | optional, multidirectional, to rear of room for view of speaker
MEET-55 | Meeting Room, 55m2 | FFE | ITAV-071 | MICROPHONE: AV system, ceiling mounted, array | 2 | may be recessed in ceiling
MEET-55 | Meeting Room, 55m2 | FFE | FQTA-086 | TABLE: meeting room, folding | 4 | quantity and size/type to suit requirements
MEET-55 | Meeting Room, 55m2 | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | optional, to speaker camera if provided
MEET-55 | Meeting Room, 55m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 is optional for booking system if provided
MEET-55 | Meeting Room, 55m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2
MEET-55 | Meeting Room, 55m2 | SE | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 2 | to microphone array
MEET-55 | Meeting Room, 55m2 | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 3 | 1 to each floorbox if provided
MEET-55 | Meeting Room, 55m2 | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 3 | 1 to lectern, 2 optional to support flexible layout, location to be confirmed to suit service requirements
MEET-55 | Meeting Room, 55m2 | SE | ELBO-015 | SWITCH: light, single | 1
MEET-55 | Meeting Room, 55m2 | SE | ELGP-208 | GPO: double, wall mounted | 4
MEET-55 | Meeting Room, 55m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | as required
MEET-55 | Meeting Room, 55m2 | SE | ELGP-203 | GPO: double, in floorbox | 6 | 2 to each floorbox if provided
MEET-9 | Meeting Room, 9m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
MEET-9 | Meeting Room, 9m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
MEET-9 | Meeting Room, 9m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
MEET-9 | Meeting Room, 9m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
MEET-9 | Meeting Room, 9m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
MEET-9 | Meeting Room, 9m2 | FA | DWWH-005 | WINDOW | 1 | desirable
MEET-9 | Meeting Room, 9m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional lockable
MEET-9 | Meeting Room, 9m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
MEET-9 | Meeting Room, 9m2 | FFE | DWWD-004 | BLIND: roller | 1
MEET-9 | Meeting Room, 9m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
MEET-9 | Meeting Room, 9m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 | optional
MEET-9 | Meeting Room, 9m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
MEET-9 | Meeting Room, 9m2 | FFE | ITAV-006 | CONTROL PANEL: AV system, wall mount | 1 | optional; may be wall mounted or on table top
MEET-9 | Meeting Room, 9m2 | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 1 | optional
MEET-9 | Meeting Room, 9m2 | FFE | FQTA-023 | TABLE: rectangular, 1500L x 900W, work height | 1
MEET-9 | Meeting Room, 9m2 | FFE | FQBS-059 | CHAIR: meeting rom, stackable | 4
MEET-9 | Meeting Room, 9m2 | FFE | ITAV-062 | CONTROL PANEL: room booking system | 1 | optional
MEET-9 | Meeting Room, 9m2 | FFE | ITAV-063 | COMPUTER: AV system | 1 | optional
MEET-9 | Meeting Room, 9m2 | FFE | ITAV-090 | SOUNDBAR: AV system, camera, speaker and microphone | 1 | optional; functions may be provided by individual items dependent on local ICT policies and service requirements
MEET-9 | Meeting Room, 9m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | optional, 1 to room booking panel and 1 to video conferencing control panel if provided
MEET-9 | Meeting Room, 9m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
MEET-9 | Meeting Room, 9m2 | SE | ITIN-046 | OUTLET: data, quad RJ45, wall mounted | 1 | optional, to suit video conferencing and AV equipment as required
MEET-9 | Meeting Room, 9m2 | SE | ELBO-015 | SWITCH: light, single | 1
MEET-9 | Meeting Room, 9m2 | SE | ELGP-208 | GPO: double, wall mounted | 4 | 3 are optional, to suit video conferencing and AV equipment as required
MOR-AU | Mortuary - Autopsy Room | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 | junction with evisceration table to be considered to prevent water ingress
MOR-AU | Mortuary - Autopsy Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
MOR-AU | Mortuary - Autopsy Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
MOR-AU | Mortuary - Autopsy Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
MOR-AU | Mortuary - Autopsy Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MOR-AU | Mortuary - Autopsy Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
MOR-AU | Mortuary - Autopsy Room | FA | DWOB-005 | OBSERVATION: internal window, alum/glass, powdercoat | 1 | to observation area if provided
MOR-AU | Mortuary - Autopsy Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | door seals required
MOR-AU | Mortuary - Autopsy Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | door seals required
MOR-AU | Mortuary - Autopsy Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MOR-AU | Mortuary - Autopsy Room | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 8
MOR-AU | Mortuary - Autopsy Room | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge and integral sink
MOR-AU | Mortuary - Autopsy Room | FFE | FIHR-016 | BRACKET: for sharps bin | 2
MOR-AU | Mortuary - Autopsy Room | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-004 | BIN: waste, clinical, 120L | 1
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 2 | to basin
MOR-AU | Mortuary - Autopsy Room | FFE | FIHR-029 | HOOK: equipment | 1 | optional, for lifter straps/slings
MOR-AU | Mortuary - Autopsy Room | FFE | MMGE-119 | TROLLEY: equipment | 2
MOR-AU | Mortuary - Autopsy Room | FFE | FIRT-005 | GRAB RAIL: stainless steel | 2 | to boot wash
MOR-AU | Mortuary - Autopsy Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
MOR-AU | Mortuary - Autopsy Room | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | optional, dependent on project requirements
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-015 | BIN: waste, general, 120L | 1
MOR-AU | Mortuary - Autopsy Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
MOR-AU | Mortuary - Autopsy Room | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 2
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-023 | SHOWER: safety, eyewash combination | 1
MOR-AU | Mortuary - Autopsy Room | FFE | LIFX-014 | LIGHT: procedure, ceiling mounted | 1 | hardwired, a second light may be provided dependent on service requirements
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-030 | TAPWARE: cold | 1 | to boot wash
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-034 | TAPWARE: laboratory | 1 | to dissection table
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-003 | HOSE REEL: retractable | 1
MOR-AU | Mortuary - Autopsy Room | FFE | HYBA-055 | SINK: single, 500 x 450 x 250D | 1
MOR-AU | Mortuary - Autopsy Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 | suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-028 | SPOUT: bath, wall mounted | 1 | to boot wash
MOR-AU | Mortuary - Autopsy Room | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
MOR-AU | Mortuary - Autopsy Room | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 | suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | FFE | MMBE-070 | LIFTER: patient, ceiling mounted, motor and sling component, mortuary | 1 | optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements; control may be suspended from motor or wall mounted depending on model
MOR-AU | Mortuary - Autopsy Room | FFE | MMLA-086 | TABLE: evisceration, height adjustable | 1 | bariatric capacity to be determined based on service requirements, services on table to be considered: suction capabilities (built-in or provided), power to table, power outlets (if not on table), down draft (optional, built-in to table), water connection (built-in to table)
MOR-AU | Mortuary - Autopsy Room | FFE | MMLA-087 | TABLE: dissection, height adjustable | 1 | with integral sink
MOR-AU | Mortuary - Autopsy Room | FFE | MMGE-185 | SCALES: digital, benchtop | 1
MOR-AU | Mortuary - Autopsy Room | FFE | MMBE-071 | LIFTER: patient, ceiling mounted, track, linear, mortuary | 1 | optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-AU | Mortuary - Autopsy Room | FFE | LIFX-037 | LIGHT: LED strip, ceiling mounted | 1 | task lighting over dissection table, articulated task light is also acceptable dependent on service requirements
MOR-AU | Mortuary - Autopsy Room | FFE | FIRT-046 | GRAB RAIL: stainless steel, freestanding | 1 | to boot wash
MOR-AU | Mortuary - Autopsy Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | SE | HYTP-013 | OUTLET: hot water | 2 | connection only, to evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | SE | HYTP-008 | OUTLET: cold water | 2 | connection only, to evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | SE | HYDR-001 | DRAIN: special requirements | 1 | to evisceration table, confirm requirements at project level
MOR-AU | Mortuary - Autopsy Room | SE | HYDR-004 | DRAIN: floor waste | 1 | to boot wash
MOR-AU | Mortuary - Autopsy Room | SE | HYDR-003 | DRAIN: floor trough | 2
MOR-AU | Mortuary - Autopsy Room | SE | HYTP-012 | OUTLET: hosecock, cold water | 1 | to hose reel
MOR-AU | Mortuary - Autopsy Room | SE | ELBO-015 | SWITCH: light, single | 2 | 1x general room lights, 1x task light over dissection bench. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-106 | GPO: single, special, for equipment | 2 | power to evisceration and dissection tables (if not part of table configuration). Required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-106 | GPO: single, special, for equipment | 8 | 4x outlets on evisceration and dissection tables, dependent on service requirements and vendor specifications. Required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to computer. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | SE | MGAS-060 | OUTLET: suction | 2 | on evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | SE | HYGE-026 | TROUGH: boot wash | 1
MOR-AU | Mortuary - Autopsy Room | SE | MEEX-017 | EXHAUST: downdraft, mortuary | 1 | optional, on evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-BH | Mortuary - Body Holding | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1
MOR-BH | Mortuary - Body Holding | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
MOR-BH | Mortuary - Body Holding | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
MOR-BH | Mortuary - Body Holding | FA | WLPR-021 | WALL PROTECTION: crash rail, at 900 AFFL | 2
MOR-BH | Mortuary - Body Holding | FA | WLPR-006 | WALL PROTECTION: corner guards | 1
MOR-BH | Mortuary - Body Holding | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
MOR-BH | Mortuary - Body Holding | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MOR-BH | Mortuary - Body Holding | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
MOR-BH | Mortuary - Body Holding | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
MOR-BH | Mortuary - Body Holding | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MOR-BH | Mortuary - Body Holding | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 5
MOR-BH | Mortuary - Body Holding | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
MOR-BH | Mortuary - Body Holding | FFE | FIHR-029 | HOOK: equipment | 1 | for lifter straps/slings
MOR-BH | Mortuary - Body Holding | FFE | MMGE-133 | TROLLEY: mortuary, hydraulic | 1 | bariatric capacity to be confirmed based on service requirements
MOR-BH | Mortuary - Body Holding | FFE | HYBA-010 | BASIN: handwash, Type B | 1
MOR-BH | Mortuary - Body Holding | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
MOR-BH | Mortuary - Body Holding | FFE | HYTP-003 | HOSE REEL: retractable | 1
MOR-BH | Mortuary - Body Holding | FFE | MMGE-183 | FRIDGE: body holding, triple tier | 3 | bariatric capacity to be confirmed based on service requirements; power and BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | FFE | MMBE-070 | LIFTER: patient, ceiling mounted, motor and sling component, mortuary | 1 | mobile lifter may be used, bariatric capacity to be confirmed based on service requirements; control may be suspended from motor or wall mounted depending on model
MOR-BH | Mortuary - Body Holding | FFE | MMBE-071 | LIFTER: patient, ceiling mounted, track, linear, mortuary | 1 | mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-BH | Mortuary - Body Holding | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | temperature monitoring, IP rated to suit AS/NZS wet zone requirements, 1 to each refrigerator, BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | SE | ITBU-001 | ALARM: equipment monitoring, temperature | 1 | temperature monitoring, alarm and BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to lifter
MOR-BH | Mortuary - Body Holding | SE | HYDR-004 | DRAIN: floor waste | 1
MOR-BH | Mortuary - Body Holding | SE | HYTP-012 | OUTLET: hosecock, cold water | 1
MOR-BH | Mortuary - Body Holding | SE | ELBO-015 | SWITCH: light, single | 1 | IP rated to suit AS/NZS wet zone requirements
MOR-BH | Mortuary - Body Holding | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | IP rated to suit AS/NZS wet zone requirements
MOR-BH | Mortuary - Body Holding | SE | ELGP-106 | GPO: single, special, for equipment | 3 | 1 to each refrigerator; required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-BR | Mortuary - Body Reception | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
MOR-BR | Mortuary - Body Reception | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 2
MOR-BR | Mortuary - Body Reception | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
MOR-BR | Mortuary - Body Reception | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
MOR-BR | Mortuary - Body Reception | FA | CLCN-009 | CORNICE: wall trim fixing | 1
MOR-BR | Mortuary - Body Reception | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
MOR-BR | Mortuary - Body Reception | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MOR-BR | Mortuary - Body Reception | FFE | FIDI-018 | DISPENSER: gown | 1
MOR-BR | Mortuary - Body Reception | FFE | FIDI-021 | DISPENSER: mask | 1
MOR-BR | Mortuary - Body Reception | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2
MOR-BR | Mortuary - Body Reception | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
MOR-BR | Mortuary - Body Reception | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
MOR-BR | Mortuary - Body Reception | FFE | ITNE-023 | PRINTER: networked | 1
MOR-BR | Mortuary - Body Reception | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
MOR-BR | Mortuary - Body Reception | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
MOR-BR | Mortuary - Body Reception | FFE | FQDW-045 | DESK: adj height, 2400W x 750D x 750H nom. | 1 | length to accommodate A3 landscape mortuary register
MOR-BR | Mortuary - Body Reception | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 outlet for telephone
MOR-BR | Mortuary - Body Reception | SE | LIFX-008 | LIGHT: task light, built in | 2 | to underside of overhead cupboards
MOR-BR | Mortuary - Body Reception | SE | ELBO-015 | SWITCH: light, single | 1 | for task lighting
MOR-BR | Mortuary - Body Reception | SE | ELGP-208 | GPO: double, wall mounted | 3 | emergency power may be provided depending on operational policies and service requirements
MOR-VR | Mortuary - Viewing Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
MOR-VR | Mortuary - Viewing Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
MOR-VR | Mortuary - Viewing Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
MOR-VR | Mortuary - Viewing Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MOR-VR | Mortuary - Viewing Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
MOR-VR | Mortuary - Viewing Room | FA | DWOB-005 | OBSERVATION: internal window, alum/glass, powdercoat | 1
MOR-VR | Mortuary - Viewing Room | FA | DWPR-003 | DOOR PROTECTION: kickplate, to 300 AFFL, vinyl, prefinished | 1
MOR-VR | Mortuary - Viewing Room | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1
MOR-VR | Mortuary - Viewing Room | FA | DWGL-052 | DOOR: 1600mm c/o, double leaf, observation panel, solid core/glass, paint | 1
MOR-VR | Mortuary - Viewing Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MOR-VR | Mortuary - Viewing Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MOR-VR | Mortuary - Viewing Room | FFE | FIRT-031 | TRACK: curtain, privacy | 1
MOR-VR | Mortuary - Viewing Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | heavy/domestic fabric is acceptable
MOR-VR | Mortuary - Viewing Room | FFE | MMGE-186 | TROLLEY: mortuary, transport | 1
MOR-VR | Mortuary - Viewing Room | SE | ELBO-015 | SWITCH: light, single | 1
MOR-W | Mortuary - Waiting | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
MOR-W | Mortuary - Waiting | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 6
MOR-W | Mortuary - Waiting | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
MOR-W | Mortuary - Waiting | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MOR-W | Mortuary - Waiting | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
MOR-W | Mortuary - Waiting | FA | DWOB-005 | OBSERVATION: internal window, alum/glass, powdercoat | 1
MOR-W | Mortuary - Waiting | FA | DWPR-003 | DOOR PROTECTION: kickplate, to 300 AFFL, vinyl, prefinished | 2
MOR-W | Mortuary - Waiting | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | lockable
MOR-W | Mortuary - Waiting | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable
MOR-W | Mortuary - Waiting | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MOR-W | Mortuary - Waiting | FFE | FQGE-002 | ARTWORK | 1
MOR-W | Mortuary - Waiting | FFE | FQBS-032 | CHAIR: waiting | 3
MOR-W | Mortuary - Waiting | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MOR-W | Mortuary - Waiting | FFE | FQCW-016 | BIN: waste, general, 20L | 1
MOR-W | Mortuary - Waiting | FFE | FQBS-043 | LOUNGE: 2 seat, 1600 wide | 1
MOR-W | Mortuary - Waiting | FFE | FQTA-034 | TABLE: rectangular, 900L x 600W, low height | 1
MOR-W | Mortuary - Waiting | SE | ELBO-015 | SWITCH: light, single | 1
MOR-W | Mortuary - Waiting | SE | ELGP-109 | GPO: single, wall mounted | 2
MOR-W | Mortuary - Waiting | SE | ITSE-006 | BUTTON: duress, fixed | 1
MRICR | MRI Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
MRICR | MRI Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 4
MRICR | MRI Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MRICR | MRI Control Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
MRICR | MRI Control Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
MRICR | MRI Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 3
MRICR | MRI Control Room | FFE | DWWD-004 | BLIND: roller | 1
MRICR | MRI Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MRICR | MRI Control Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
MRICR | MRI Control Room | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
MRICR | MRI Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
MRICR | MRI Control Room | FFE | FQSN-050 | LOCKER: 4 tier (quarter size) | 2 | optional
MRICR | MRI Control Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
MRICR | MRI Control Room | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 2 | for RIS/PMS and patient observation
MRICR | MRI Control Room | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1 | wall mounted, on bracket, cardiac/ anaesthetic monitor
MRICR | MRI Control Room | FFE | ITNE-023 | PRINTER: networked | 1 | on benchtop
MRICR | MRI Control Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1
MRICR | MRI Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
MRICR | MRI Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1 | on bench
MRICR | MRI Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 1 | high bench at 900-950 AFFL optional
MRICR | MRI Control Room | FFE | MMMI-171 | BOX: alarm, MRI | 1
MRICR | MRI Control Room | FFE | MMMI-193 | COMPUTER: tower, acquisition, MRI | 1
MRICR | MRI Control Room | FFE | MMMI-195 | WINDOW: radiofrequency, MRI | 1
MRICR | MRI Control Room | FFE | MMMI-197 | BUTTON: quench, MRI | 1
MRICR | MRI Control Room | FFE | MMMI-199 | PANEL: waveguide, MRI | 2
MRICR | MRI Control Room | FFE | MMMI-202 | CONSOLE: control, MRI | 1
MRICR | MRI Control Room | FFE | FIJO-099 | CAC: cable access cap | 2
MRICR | MRI Control Room | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1
MRICR | MRI Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 2
MRICR | MRI Control Room | FFE | MMMI-369 | DISPLAY SCREEN: contrast injector | 1
MRICR | MRI Control Room | FFE | FIHR-070 | BRACKET: for display screen, dual, desk mounted | 2
MRICR | MRI Control Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 2
MRICR | MRI Control Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
MRICR | MRI Control Room | FFE | ITNE-070 | DISPLAY SCREEN: PACS | 2
MRICR | MRI Control Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 outlet for patient slave monitor, one outlet for telephone
MRICR | MRI Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4
MRICR | MRI Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1
MRICR | MRI Control Room | SE | ELGP-135 | GPO: UPS, single, wall mounted | 4
MRICR | MRI Control Room | SE | MGFP-001 | ALARM PANEL: medical gases | 1
MRICR | MRI Control Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
MRICR | MRI Control Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | 1 for printer
MRICR | MRI Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 5
MRICR | MRI Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
MRICR | MRI Control Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
MRICR | MRI Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
MRICR | MRI Control Room | SE | MEGE-014 | ALARM: oxygen depletion | 1
MRICR | MRI Control Room | SE | HYGE-025 | CONTROL PANEL: process cooling water pump | 2
MRICR | MRI Control Room | SE | MEGE-017 | CONTROL PANEL: HVAC | 1
MRIR | MRI Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
MRIR | MRI Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
MRIR | MRI Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
MRIR | MRI Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
MRIR | MRI Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
MRIR | MRI Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiled ceiling also acceptable; ceiling treatment to enhance patient experience to be considered
MRIR | MRI Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MRIR | MRI Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 9
MRIR | MRI Room | FFE | MGFP-002 | FLOWMETER: medical air | 1 | MRI compatible
MRIR | MRI Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | MRI compatible
MRIR | MRI Room | FFE | FIJO-116 | CUPBOARD: tall, double door, adj shelves | 3 | for coils
MRIR | MRI Room | FFE | FQBS-037 | FOOTSTOOL | 1 | MRI compatible
MRIR | MRI Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | MRI compatible
MRIR | MRI Room | FFE | MMGE-002 | ADAPTER: suction | 2 | MRI compatible
MRIR | MRI Room | FFE | MMGE-100 | SUCTION BOTTLE | 2 | MRI compatible
MRIR | MRI Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
MRIR | MRI Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1
MRIR | MRI Room | FFE | MMMI-175 | CABIN: radio frequency, faraday cage, MRI | 1 | 3 dimensions
MRIR | MRI Room | FFE | MMMI-180 | DEVICE: imaging, magnet, MRI | 1 | refer to manufacturer's requirements for quench pipes and other associated equipment
MRIR | MRI Room | FFE | MMMI-181 | DOOR: radio frequency, MRI | 1 | 1200mm clear opening; with door protection to 900mm AFFL
MRIR | MRI Room | FFE | MMMI-185 | PIPE: quench, MRI | 1 | installed to manufacturer's specifications with minimal bends
MRIR | MRI Room | FFE | MMMI-183 | INJECTOR: contrast, MRI | 1
MRIR | MRI Room | FFE | MMMI-188 | CAMERA: observation, MRI | 2 | with direct view of patient
MRIR | MRI Room | FFE | MMMI-191 | TABLE: patient, MRI | 1 | detachable table also acceptable; use of detachable table may also negate need for MRI compatible patient transport trolley
MRIR | MRI Room | FFE | MMMI-195 | WINDOW: radiofrequency, MRI | 1 | 1 to control, 1 to anaesthetic preparation
MRIR | MRI Room | FFE | MMMI-198 | MACHINE: anaesthetic, MRI Safe | 1
MRIR | MRI Room | FFE | MMMI-199 | PANEL: waveguide, MRI | 4
MRIR | MRI Room | FFE | MMMI-200 | TROLLEY: patient, transport, MRI Safe | 1
MRIR | MRI Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | to cupboards
MRIR | MRI Room | FFE | MMMI-368 | LASER: positioning lights, MRI | 1 | optional, for radiotherapy planning
MRIR | MRI Room | FFE | FIHR-082 | BRACKET: for observation camera, MRI Safe, wall mounted | 2
MRIR | MRI Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
MRIR | MRI Room | SE | ELPR-006 | RCD: residual current device | 2 | 1 for each UPS & emergency power circuits
MRIR | MRI Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | 1-laser positioning light if required
MRIR | MRI Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
MRIR | MRI Room | SE | ELBO-001 | BUTTON: emergency stop | 1
MRIR | MRI Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1
MRIR | MRI Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2
MRIR | MRI Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1
MRIR | MRI Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
MRIR | MRI Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2
MRIR | MRI Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
MRIR | MRI Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | 1-clock
MRIR | MRI Room | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 2
MRIR | MRI Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
MRIR | MRI Room | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
MRIR | MRI Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | MRI compatible
MRIR | MRI Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
MRIR | MRI Room | SE | MMMI-201 | PANEL: penetration, MRI | 1
MRIR | MRI Room | SE | ELGP-133 | GPO: UPS, single, on services panel | 2
MRIR | MRI Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
MRIR | MRI Room | SE | ELPR-007 | UPS: status indicator | 1
MRIR | MRI Room | SE | MEGE-016 | SENSOR: oxygen depletion | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | low VOC vinyl, consider acoustic options
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | consider acoustic properties
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 3
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MGFP-002 | FLOWMETER: medical air | 2 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIHR-019 | BRACKET: for suction bottle | 4
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | mounted on trolley FQSM-035
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2 | shared
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1 | mounted on trolley FQSM-035
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIJO-194 | SHELF: laminate | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMGE-002 | ADAPTER: suction | 4 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMGE-100 | SUCTION BOTTLE | 4
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQSM-035 | TROLLEY: small | 2
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIBM-018 | WHITEBOARD: fixed | 1 | may be optionally replaced with a care board
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQCA-086 | WARMER: bottle, mobile | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMGE-076 | PUMP: breast | 1 | on trolley/stand
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | on trolley
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMMA-007 | INCUBATOR: infant, humidicrib | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMGE-065 | MONITOR: patient, neonatal | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMSP-018 | PENDANT: single, wet and dry combination (fixed or adjustable height) | 1 | optional; would replace wall mounted service panel MMSP-026
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMHA-024 | VENTILATOR: continuous positive airway pressure (CPAP) | 1 | optional; provide bracket
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMHA-025 | VENTILATOR: neonatal | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQBS-055 | CHAIR: overnight fold out | 1 | compatible with kangaroo care, breastfeeding
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQSM-044 | CUPBOARD: mobile, double door, adjustable shelves | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FQGE-091 | FRIDGE: milk, small | 1 | optional
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | ITCL-036 | CAMERA: neonatal | 1 | optional; must be able to be turned off within the bay; storage and use of images to be considered
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | MMMA-018 | MIXER: oxygen and air | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIHR-083 | BRACKET: for neonatal camera, crib mounted | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIHR-084 | BRACKET: for oxygen and air mixer | 1 | optional
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIHR-085 | BRACKET: for neonatal monitor, crib mounted | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | FFE | FIHR-086 | BRACKET: for CPAP ventilator, wall mounted | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELGP-101 | GPO: single, ceiling mounted | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | LIFX-017 | LIGHT: night light | 1 | switch to be located at cubicle or staff station
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 4 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 4 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | MGAS-062 | OUTLET: suction, on services panel | 4 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on wall; for parent/carer use
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on wall; for parent/carer use
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELGP-208 | GPO: double, wall mounted | 1 | to parent/carer area; may include optional USB charging point
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELPR-004 | MONITOR: line isolation | 1 | 1 required for UPS
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | MMSP-026 | SERVICES PANEL: wall mounted | 3 | flush mounted
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELBO-012 | SWITCH: light, dimmer | 2
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ITIN-035 | OUTLET: data, triple RJ45, on services panel | 2 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELGP-133 | GPO: UPS, single, on services panel | 4 | on services panel
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELGP-122 | GPO: emergency power, single, on services panel | 12
NBIC-HD | Neonatal Bay - Intensive Care/ High Dependency Care | SE | ELPR-007 | UPS: status indicator | 1 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | low VOC vinyl, consider acoustic options
NBLD | Neonatal Bay - Low Dependency Care | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
NBLD | Neonatal Bay - Low Dependency Care | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
NBLD | Neonatal Bay - Low Dependency Care | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
NBLD | Neonatal Bay - Low Dependency Care | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | consider acoustic properties
NBLD | Neonatal Bay - Low Dependency Care | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
NBLD | Neonatal Bay - Low Dependency Care | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 3
NBLD | Neonatal Bay - Low Dependency Care | FFE | MGFP-002 | FLOWMETER: medical air | 2 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIHR-019 | BRACKET: for suction bottle | 3
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | mounted on trolley FQSM-035
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | optional
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2 | shared
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1 | mounted on trolley FQSM-035
NBLD | Neonatal Bay - Low Dependency Care | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIJO-194 | SHELF: laminate | 1 | optional; for small milk fridge FQGE-091
NBLD | Neonatal Bay - Low Dependency Care | FFE | MMGE-002 | ADAPTER: suction | 3 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | FFE | MMGE-100 | SUCTION BOTTLE | 3
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQSM-035 | TROLLEY: small | 2
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIBM-018 | WHITEBOARD: fixed | 1 | may be optionally replaced with a care board
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQCA-086 | WARMER: bottle, mobile | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | MMGE-076 | PUMP: breast | 1 | on trolley/stand
NBLD | Neonatal Bay - Low Dependency Care | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | optional; on trolley
NBLD | Neonatal Bay - Low Dependency Care | FFE | MMMA-007 | INCUBATOR: infant, humidicrib | 1 | or bassinette
NBLD | Neonatal Bay - Low Dependency Care | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQBS-055 | CHAIR: overnight fold out | 1 | compatible with kangaroo care, breastfeeding
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQSM-044 | CUPBOARD: mobile, double door, adjustable shelves | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | FQGE-091 | FRIDGE: milk, small | 1 | optional
NBLD | Neonatal Bay - Low Dependency Care | FFE | ITCL-036 | CAMERA: neonatal | 1 | optional; must be able to be turned off in the bay; storage and use of images to be considered
NBLD | Neonatal Bay - Low Dependency Care | FFE | MMMA-018 | MIXER: oxygen and air | 1
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIHR-083 | BRACKET: for neonatal camera, crib mounted | 1 | optional
NBLD | Neonatal Bay - Low Dependency Care | FFE | FIHR-084 | BRACKET: for oxygen and air mixer | 1
NBLD | Neonatal Bay - Low Dependency Care | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
NBLD | Neonatal Bay - Low Dependency Care | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
NBLD | Neonatal Bay - Low Dependency Care | SE | ELPR-006 | RCD: residual current device | 2 | on services panel; Line Isolation Monitor may be provided for UPS
NBLD | Neonatal Bay - Low Dependency Care | SE | ELGP-101 | GPO: single, ceiling mounted | 1
NBLD | Neonatal Bay - Low Dependency Care | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | SE | LIFX-017 | LIGHT: night light | 1 | switch to be located at cubicle or staff station
NBLD | Neonatal Bay - Low Dependency Care | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 3 | on services panel, 1 no. optional
NBLD | Neonatal Bay - Low Dependency Care | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 3 | on services panel, 1 no. optional
NBLD | Neonatal Bay - Low Dependency Care | SE | MGAS-062 | OUTLET: suction, on services panel | 3 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on wall, for parent/carer use
NBLD | Neonatal Bay - Low Dependency Care | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on wall, for parent/carer use
NBLD | Neonatal Bay - Low Dependency Care | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | SE | ELGP-208 | GPO: double, wall mounted | 1 | to parent/carer area; may include optional USB charging point
NBLD | Neonatal Bay - Low Dependency Care | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4
NBLD | Neonatal Bay - Low Dependency Care | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
NBLD | Neonatal Bay - Low Dependency Care | SE | ELPR-004 | MONITOR: line isolation | 1
NBLD | Neonatal Bay - Low Dependency Care | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2
NBLD | Neonatal Bay - Low Dependency Care | SE | MMSP-026 | SERVICES PANEL: wall mounted | 3 | flush mounted
NBLD | Neonatal Bay - Low Dependency Care | SE | ELBO-012 | SWITCH: light, dimmer | 1
NBLD | Neonatal Bay - Low Dependency Care | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | SE | ELGP-133 | GPO: UPS, single, on services panel | 2 | on services panel
NBLD | Neonatal Bay - Low Dependency Care | SE | ELGP-122 | GPO: emergency power, single, on services panel | 6
NBLD | Neonatal Bay - Low Dependency Care | SE | ELPR-007 | UPS: status indicator | 1 | on services panel
OFF-1P-12 | Office - 1 Person, 12m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 2
OFF-1P-12 | Office - 1 Person, 12m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
OFF-1P-12 | Office - 1 Person, 12m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
OFF-1P-12 | Office - 1 Person, 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
OFF-1P-12 | Office - 1 Person, 12m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
OFF-1P-12 | Office - 1 Person, 12m2 | FA | DWWH-005 | WINDOW | 1 | desirable
OFF-1P-12 | Office - 1 Person, 12m2 | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | with privacy film
OFF-1P-12 | Office - 1 Person, 12m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | lockable
OFF-1P-12 | Office - 1 Person, 12m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FQBS-029 | CHAIR: visitor, office areas | 3
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | DWWD-004 | BLIND: roller | 1 | to window if provided
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FIHR-026 | HOOK: coat | 2 | optional, prioritize lower hook for wheelchair users if only one hook provided
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1 | lockable
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | dual screens may be provided to suit service requirements
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FQTA-057 | TABLE: round, 900 diam, work height | 1
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FQSN-135 | CABINET: single door, tambour, adj shelves, lockable, 1200H | 1 | lockable, size to suit service requirements
OFF-1P-12 | Office - 1 Person, 12m2 | FFE | FQDW-054 | WORKSTATION: straight, adj height, 1600W x 750D x 750H nom. | 1
OFF-1P-12 | Office - 1 Person, 12m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1
OFF-1P-12 | Office - 1 Person, 12m2 | SE | ELBO-015 | SWITCH: light, single | 1
OFF-1P-12 | Office - 1 Person, 12m2 | SE | ELGP-208 | GPO: double, wall mounted | 4 | extent of emergency power to be determined based on service requirements
OFF-1P-12 | Office - 1 Person, 12m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | inclusion dependent on location, not required if room located in staff only area
OFF-1P-9 | Office - 1 Person, 9m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
OFF-1P-9 | Office - 1 Person, 9m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
OFF-1P-9 | Office - 1 Person, 9m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
OFF-1P-9 | Office - 1 Person, 9m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
OFF-1P-9 | Office - 1 Person, 9m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
OFF-1P-9 | Office - 1 Person, 9m2 | FA | DWWH-005 | WINDOW | 1 | desirable
OFF-1P-9 | Office - 1 Person, 9m2 | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | with privacy film
OFF-1P-9 | Office - 1 Person, 9m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | lockable
OFF-1P-9 | Office - 1 Person, 9m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FQBS-029 | CHAIR: visitor, office areas | 2
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | DWWD-004 | BLIND: roller | 1 | to window if provided
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FIHR-026 | HOOK: coat | 2 | optional, prioritize lower hook for wheelchair users if only one hook provided
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1 | lockable
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | dual screens may be provided to suit service requirements
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FQSN-135 | CABINET: single door, tambour, adj shelves, lockable, 1200H | 1 | lockable, size to suit service requirements
OFF-1P-9 | Office - 1 Person, 9m2 | FFE | FQDW-054 | WORKSTATION: straight, adj height, 1600W x 750D x 750H nom. | 1
OFF-1P-9 | Office - 1 Person, 9m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1
OFF-1P-9 | Office - 1 Person, 9m2 | SE | ELBO-015 | SWITCH: light, single | 1
OFF-1P-9 | Office - 1 Person, 9m2 | SE | ELGP-208 | GPO: double, wall mounted | 3 | extent of emergency power to be determined based on service requirements
OFF-1P-9 | Office - 1 Person, 9m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | inclusion dependent on location, not required if room located in staff only area
OFF-2P | Office - 2 Person | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
OFF-2P | Office - 2 Person | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5
OFF-2P | Office - 2 Person | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
OFF-2P | Office - 2 Person | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
OFF-2P | Office - 2 Person | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
OFF-2P | Office - 2 Person | FA | DWWH-005 | WINDOW | 1 | desirable
OFF-2P | Office - 2 Person | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | with privacy film
OFF-2P | Office - 2 Person | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | lockable
OFF-2P | Office - 2 Person | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OFF-2P | Office - 2 Person | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
OFF-2P | Office - 2 Person | FFE | FQBS-029 | CHAIR: visitor, office areas | 2
OFF-2P | Office - 2 Person | FFE | DWWD-004 | BLIND: roller | 1 | to window if provided
OFF-2P | Office - 2 Person | FFE | FIHR-026 | HOOK: coat | 2 | optional, prioritize lower hook for wheelchair users if only one hook provided
OFF-2P | Office - 2 Person | FFE | FQCW-016 | BIN: waste, general, 20L | 1
OFF-2P | Office - 2 Person | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 2 | lockable
OFF-2P | Office - 2 Person | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | optional
OFF-2P | Office - 2 Person | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2 | dual screens may be provided to suit service requirements
OFF-2P | Office - 2 Person | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
OFF-2P | Office - 2 Person | FFE | FQDW-054 | WORKSTATION: straight, adj height, 1600W x 750D x 750H nom. | 2
OFF-2P | Office - 2 Person | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2
OFF-2P | Office - 2 Person | SE | ELBO-015 | SWITCH: light, single | 1
OFF-2P | Office - 2 Person | SE | ELGP-208 | GPO: double, wall mounted | 6 | extent of emergency power to be determined based on service requirements
OFF-2P | Office - 2 Person | SE | ITSE-006 | BUTTON: duress, fixed | 1 | inclusion dependent on location, not required if room located in staff only area
OFF-CLN | Office - Clinical Workroom | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | carpet tiles are also acceptable
OFF-CLN | Office - Clinical Workroom | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
OFF-CLN | Office - Clinical Workroom | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
OFF-CLN | Office - Clinical Workroom | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
OFF-CLN | Office - Clinical Workroom | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
OFF-CLN | Office - Clinical Workroom | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | optional
OFF-CLN | Office - Clinical Workroom | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
OFF-CLN | Office - Clinical Workroom | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OFF-CLN | Office - Clinical Workroom | FFE | FQBS-018 | CHAIR: office, ergonomic | 4
OFF-CLN | Office - Clinical Workroom | FFE | FQCW-016 | BIN: waste, general, 20L | 1
OFF-CLN | Office - Clinical Workroom | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 | to patient flow monitor
OFF-CLN | Office - Clinical Workroom | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 6 | overhead joinery may be configured to include pigeon holes for record storage as required
OFF-CLN | Office - Clinical Workroom | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
OFF-CLN | Office - Clinical Workroom | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional, above bench
OFF-CLN | Office - Clinical Workroom | FFE | ITBU-013 | DISPLAY SCREEN: patient flow system | 1
OFF-CLN | Office - Clinical Workroom | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 4
OFF-CLN | Office - Clinical Workroom | FFE | ITNE-023 | PRINTER: networked | 1
OFF-CLN | Office - Clinical Workroom | FFE | ITNE-049 | TELEPHONE: handset, desktop | 4
OFF-CLN | Office - Clinical Workroom | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 1
OFF-CLN | Office - Clinical Workroom | FFE | FIJO-099 | CAC: cable access cap | 4
OFF-CLN | Office - Clinical Workroom | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead is also acceptable
OFF-CLN | Office - Clinical Workroom | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | to patient flow monitor
OFF-CLN | Office - Clinical Workroom | FFE | FIHR-080 | BRACKET: for bench, 750D, wall mounted | 3 | legs are also acceptable, quantity to be confirmed to achieve required support, ensure location does not impact leg clearance at workstations
OFF-CLN | Office - Clinical Workroom | FFE | ITCL-037 | CHARGER: wireless duress devices | 2 | optional
OFF-CLN | Office - Clinical Workroom | FFE | FIHR-093 | BRACKET: keyboard shelf, wall mounted | 1 | to patient flow monitor
OFF-CLN | Office - Clinical Workroom | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 x to patient flow monitor, 1 x to printer
OFF-CLN | Office - Clinical Workroom | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | location of outlets to meet local operational/WHS requirements
OFF-CLN | Office - Clinical Workroom | SE | LIFX-008 | LIGHT: task light, built in | 6 | under wall mounted joinery
OFF-CLN | Office - Clinical Workroom | SE | ELBO-015 | SWITCH: light, single | 2 | 1 x general room lighting, 1 x task light
OFF-CLN | Office - Clinical Workroom | SE | ELGP-208 | GPO: double, wall mounted | 7 | location of outlets to meet local operational/WHS requirements
OFF-CLN | Office - Clinical Workroom | SE | ELGP-208 | GPO: double, wall mounted | 3 | for BYO devices, to be located above desk for easy access
OFF-CLN | Office - Clinical Workroom | SE | ELGP-208 | GPO: double, wall mounted | 1 | optional, for duress charging station if provided
OFF-CLN | Office - Clinical Workroom | SE | ITSE-006 | BUTTON: duress, fixed | 1 | below desk, wall mounted is also acceptable
OFF-CLN | Office - Clinical Workroom | SE | ELGP-130 | GPO: UPS, single | 1 | to printer; UPS to be provided if downtime computer required
OFF-CLN | Office - Clinical Workroom | SE | ELGP-235 | GPO: UPS, double, wall mounted | 2 | UPS to be provided if downtime computer required. location of outlets to meet local operational/WHS requirements
OFF-WI-5 | Office - Write-up, 5m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
OFF-WI-5 | Office - Write-up, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
OFF-WI-5 | Office - Write-up, 5m2 | FA | WLPR-010 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | Align heights of corner guards with other corridor elements
OFF-WI-5 | Office - Write-up, 5m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
OFF-WI-5 | Office - Write-up, 5m2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | Between above bench joinery and ceiling
OFF-WI-5 | Office - Write-up, 5m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
OFF-WI-5 | Office - Write-up, 5m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OFF-WI-5 | Office - Write-up, 5m2 | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1 | Standing or seating height, refer RLS or project specific requirements
OFF-WI-5 | Office - Write-up, 5m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 2 | For standing height bench, use ergonomic high chair for standring height
OFF-WI-5 | Office - Write-up, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
OFF-WI-5 | Office - Write-up, 5m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 4 | Above bench, number to suit layout. Refer to RLS or project specific requirements
OFF-WI-5 | Office - Write-up, 5m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | Between bench and overbench joinery
OFF-WI-5 | Office - Write-up, 5m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2 | Consider location of harddrive, if below bench add bracket
OFF-WI-5 | Office - Write-up, 5m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
OFF-WI-5 | Office - Write-up, 5m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | Number of outlets per faceplate as per ICT policy. 1 per workspace
OFF-WI-5 | Office - Write-up, 5m2 | SE | LIFX-008 | LIGHT: task light, built in | 2 | For above bench joinery
OFF-WI-5 | Office - Write-up, 5m2 | SE | ELBO-015 | SWITCH: light, single | 2 | Pelmet lighting
OFF-WI-5 | Office - Write-up, 5m2 | SE | ITCL-001 | ANNUNCIATOR: nurse call | 1 | Located in corridor adjacent, number to suit design
OFF-WI-5 | Office - Write-up, 5m2 | SE | ELGP-208 | GPO: double, wall mounted | 4 | 2 per workspace
OFF-WS | Office - Workstation | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 2
OFF-WS | Office - Workstation | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
OFF-WS | Office - Workstation | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
OFF-WS | Office - Workstation | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OFF-WS | Office - Workstation | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
OFF-WS | Office - Workstation | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | optional; to be rationalised between multiple workstations
OFF-WS | Office - Workstation | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1
OFF-WS | Office - Workstation | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | dual screens may be provided to suit service requirements
OFF-WS | Office - Workstation | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | optional
OFF-WS | Office - Workstation | FFE | FQDW-043 | PARTITION: workstation system, acoustic | 1 | a modesty panel may been to be required depending on layout, this may be an extension of the acoustic panel or a separate panel depending on selected system.
OFF-WS | Office - Workstation | FFE | FQDW-054 | WORKSTATION: straight, adj height, 1600W x 750D x 750H nom. | 1
OFF-WS | Office - Workstation | FFE | FQDW-075 | WORKSTATION SYSTEM: cable tray, soft wired power and data | 1 | separation of power and data cables may be required
OFF-WS | Office - Workstation | SE | ITIN-029 | OUTLET: data, double RJ45, desk box | 1
OFF-WS | Office - Workstation | SE | ELGP-212 | GPO: double, desk box | 3
OFF-WS | Office - Workstation | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 1
OPG | OPG Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
OPG | OPG Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9
OPG | OPG Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
OPG | OPG Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
OPG | OPG Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 7
OPG | OPG Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
OPG | OPG Room | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
OPG | OPG Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass
OPG | OPG Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
OPG | OPG Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OPG | OPG Room | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
OPG | OPG Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
OPG | OPG Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
OPG | OPG Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
OPG | OPG Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
OPG | OPG Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
OPG | OPG Room | FFE | FIDI-030 | DISPENSER: soap | 1
OPG | OPG Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1
OPG | OPG Room | FFE | FIJO-142 | CUPBOARD: underbench, single, adj shelves, with single drawer | 1
OPG | OPG Room | FFE | FQSM-016 | TROLLEY | 1
OPG | OPG Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
OPG | OPG Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
OPG | OPG Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
OPG | OPG Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
OPG | OPG Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
OPG | OPG Room | FFE | MMMI-324 | DEVICE: imaging, dental imaging unit (OPG/CEPH/CONE BEAM CT) | 1 | may be mounted to pole or a wall plate
OPG | OPG Room | FFE | FIJO-069 | BENCH TOP: 750D, joinery under, laminate finish | 1
OPG | OPG Room | FFE | FIJO-099 | CAC: cable access cap | 2
OPG | OPG Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
OPG | OPG Room | FFE | MMMI-371 | BUTTON: dental imaging unit, remote activation | 1 | locate outside room
OPG | OPG Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 1
OPG | OPG Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
OPG | OPG Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 1
OPG | OPG Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | for BUTTON:OPG, to connect to outlet adjacent to OPG
OPG | OPG Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | computer, PACS screen
OPG | OPG Room | SE | ELPR-006 | RCD: residual current device | 1
OPG | OPG Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
OPG | OPG Room | SE | ELBO-001 | BUTTON: emergency stop | 2 | main power emergency stop, consult equipment manufacturer for safety and compatibility with equipment.
OPG | OPG Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | outside room entry, auto on when modality is in use
OPG | OPG Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
OPG | OPG Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | clock
OPG | OPG Room | SE | ELGP-223.1 | GPO: emergency power, double, wall mounted (V) | 5
OPG | OPG Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
OPG | OPG Room | SE | WLSH-004 | SHIELDING: lead lining | 1
OPG | OPG Room | SE | ELBO-012 | SWITCH: light, dimmer | 2
OVBR | Overnight Stay - Bedroom | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
OVBR | Overnight Stay - Bedroom | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 8
OVBR | Overnight Stay - Bedroom | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
OVBR | Overnight Stay - Bedroom | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1 | optional
OVBR | Overnight Stay - Bedroom | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
OVBR | Overnight Stay - Bedroom | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
OVBR | Overnight Stay - Bedroom | FA | DWWH-005 | WINDOW | 1 | essential
OVBR | Overnight Stay - Bedroom | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | lockable
OVBR | Overnight Stay - Bedroom | FA | CLCN-009 | CORNICE: wall trim fixing | 1
OVBR | Overnight Stay - Bedroom | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 | optional
OVBR | Overnight Stay - Bedroom | FFE | DWWD-004 | BLIND: roller | 1 | blackout fabric
OVBR | Overnight Stay - Bedroom | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1
OVBR | Overnight Stay - Bedroom | FFE | FQCW-016 | BIN: waste, general, 20L | 1
OVBR | Overnight Stay - Bedroom | FFE | FQBS-004 | BED: domestic, single with mattress | 1
OVBR | Overnight Stay - Bedroom | FFE | FQTA-001 | TABLE: bedside | 1
OVBR | Overnight Stay - Bedroom | FFE | FQCA-030 | FRIDGE: domestic, 120L | 1 | optional, dependent on project requirements
OVBR | Overnight Stay - Bedroom | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | may be wall mounted
OVBR | Overnight Stay - Bedroom | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead is also acceptable
OVBR | Overnight Stay - Bedroom | FFE | FQDW-053 | DESK: fixed height, 1000W x 600D x 720H | 1 | optional
OVBR | Overnight Stay - Bedroom | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 x optional, to desk if provided
OVBR | Overnight Stay - Bedroom | SE | LIFX-011 | LIGHT: reading light | 1
OVBR | Overnight Stay - Bedroom | SE | ELBO-015 | SWITCH: light, single | 2 | 1 x general room lighting, 1 x reading light
OVBR | Overnight Stay - Bedroom | SE | ELGP-109 | GPO: single, wall mounted | 1 | optional, to fridge if provided
OVBR | Overnight Stay - Bedroom | SE | ELGP-208 | GPO: double, wall mounted | 1
OVBR | Overnight Stay - Bedroom | SE | ITSE-038 | READER: access control, general | 1 | optional
OVBR | Overnight Stay - Bedroom | SE | ELGP-208.1 | GPO: double, wall mounted (V) | 1
OVES | Overnight Stay - Ensuite | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
OVES | Overnight Stay - Ensuite | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
OVES | Overnight Stay - Ensuite | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
OVES | Overnight Stay - Ensuite | FA | WLWA-019 | WALL FINISH: vinyl, full height | 6 | tiles are also acceptable
OVES | Overnight Stay - Ensuite | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
OVES | Overnight Stay - Ensuite | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | with privacy latch, inward opening door to have emergency release
OVES | Overnight Stay - Ensuite | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
OVES | Overnight Stay - Ensuite | FFE | FIHR-026 | HOOK: coat | 2
OVES | Overnight Stay - Ensuite | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1
OVES | Overnight Stay - Ensuite | FFE | FQGE-011 | CURTAIN: shower | 1
OVES | Overnight Stay - Ensuite | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
OVES | Overnight Stay - Ensuite | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
OVES | Overnight Stay - Ensuite | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 - to basin, 1 - to shower
OVES | Overnight Stay - Ensuite | FFE | FIDI-036 | DISPENSER: toilet paper | 1
OVES | Overnight Stay - Ensuite | FFE | FIBM-006 | MIRROR: fixed, glass | 1
OVES | Overnight Stay - Ensuite | FFE | FQCW-037 | BIN: waste, sanitary | 1
OVES | Overnight Stay - Ensuite | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 | optional
OVES | Overnight Stay - Ensuite | FFE | FIRT-016 | RAIL: towel | 1
OVES | Overnight Stay - Ensuite | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
OVES | Overnight Stay - Ensuite | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
OVES | Overnight Stay - Ensuite | FFE | HYTP-018 | SHOWER: fixed rose | 1
OVES | Overnight Stay - Ensuite | FFE | HYWC-008 | TOILET SUITE: standard | 1 | with 100mm clearout access point
OVES | Overnight Stay - Ensuite | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1
OVES | Overnight Stay - Ensuite | SE | HYDR-004 | DRAIN: floor waste | 1
OVES | Overnight Stay - Ensuite | SE | ELBO-015 | SWITCH: light, single | 1
OVES | Overnight Stay - Ensuite | SE | ELGP-208 | GPO: double, wall mounted | 1
PAR | Parenting Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
PAR | Parenting Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
PAR | Parenting Room | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | tiles are also acceptable
PAR | Parenting Room | FA | WLWA-007 | WALL FINISH: splashback | 1
PAR | Parenting Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PAR | Parenting Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 4
PAR | Parenting Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PAR | Parenting Room | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | with privacy latch, emergency release to be provided on inward opening door
PAR | Parenting Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PAR | Parenting Room | FFE | FQBS-035 | CHANGE TABLE: baby | 1
PAR | Parenting Room | FFE | FIHR-026 | HOOK: coat | 2
PAR | Parenting Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PAR | Parenting Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to sink
PAR | Parenting Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to sink
PAR | Parenting Room | FFE | FQBS-010 | CHAIR: armchair | 1 | to be suitable for breastfeeding
PAR | Parenting Room | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | for nappies, sanitary waste stream may be required dependent on operational policies
PAR | Parenting Room | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
PAR | Parenting Room | FFE | HYBA-051 | SINK: single | 1 | depth to meet accessible requirements; integrated solid surface sink into solid surface bench is also acceptable
PAR | Parenting Room | FFE | FQTA-049 | TABLE: round, 500 diam, low height | 1
PAR | Parenting Room | FFE | FIJO-213 | PANEL: joinery carcass end | 1
PAR | Parenting Room | FFE | FIJO-228 | JOINERY UNIT: sink shroud, accessible | 1 | to sink
PAR | Parenting Room | FFE | FIJO-232 | BENCH TOP: 650D, joinery under, laminate finish | 1 | solid surface is also acceptable, dependent on requirements
PAR | Parenting Room | SE | ELBO-015 | SWITCH: light, single | 1
PAR | Parenting Room | SE | ELGP-208 | GPO: double, wall mounted | 1
PAR | Parenting Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | default = set plasterboard; drop in tile ceiling also acceptable
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MMGE-142 | TROLLEY: sharps bin | 1 | shared
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MMGE-002 | ADAPTER: suction | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MMGE-100 | SUCTION BOTTLE | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1 | shared
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELPR-006 | RCD: residual current device | 1 | on service panel
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | LIFX-030 | LIGHT: downlight, recessed, compact fluorescent | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel for examination downlight
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | shared between a group of beds
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITSE-006 | BUTTON: duress, fixed | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | flush mounted
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2 | on services panel
PBIC | Patient Bay - Intensive Care | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
PBIC | Patient Bay - Intensive Care | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
PBIC | Patient Bay - Intensive Care | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PBIC | Patient Bay - Intensive Care | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
PBIC | Patient Bay - Intensive Care | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 4
PBIC | Patient Bay - Intensive Care | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBIC | Patient Bay - Intensive Care | FA | DWWH-005 | WINDOW | 1
PBIC | Patient Bay - Intensive Care | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBIC | Patient Bay - Intensive Care | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 5
PBIC | Patient Bay - Intensive Care | FFE | MGFP-002 | FLOWMETER: medical air | 3 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to window
PBIC | Patient Bay - Intensive Care | FFE | FIHR-019 | BRACKET: for suction bottle | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | for staff
PBIC | Patient Bay - Intensive Care | FFE | MMGE-019 | CHAIR: patient | 1
PBIC | Patient Bay - Intensive Care | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBIC | Patient Bay - Intensive Care | FFE | FQCW-035 | BIN: waste, recycling, plastics, 50L | 1
PBIC | Patient Bay - Intensive Care | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBIC | Patient Bay - Intensive Care | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBIC | Patient Bay - Intensive Care | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PBIC | Patient Bay - Intensive Care | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
PBIC | Patient Bay - Intensive Care | FFE | FQCW-004 | BIN: waste, clinical, 120L | 1
PBIC | Patient Bay - Intensive Care | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | near entry
PBIC | Patient Bay - Intensive Care | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PBIC | Patient Bay - Intensive Care | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PBIC | Patient Bay - Intensive Care | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PBIC | Patient Bay - Intensive Care | FFE | MMOP-027 | IV POLE: on pendant | 1
PBIC | Patient Bay - Intensive Care | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
PBIC | Patient Bay - Intensive Care | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBIC | Patient Bay - Intensive Care | FFE | FQTA-013 | TABLE: overbed | 1
PBIC | Patient Bay - Intensive Care | FFE | MGFP-004 | FLOWMETER: oxygen | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | MMGE-142 | TROLLEY: sharps bin | 1
PBIC | Patient Bay - Intensive Care | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3 | wire basket bins
PBIC | Patient Bay - Intensive Care | FFE | MMGE-002 | ADAPTER: suction | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | MMGE-100 | SUCTION BOTTLE | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
PBIC | Patient Bay - Intensive Care | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
PBIC | Patient Bay - Intensive Care | FFE | MMBE-013 | BED: patient, ICU, electric | 1
PBIC | Patient Bay - Intensive Care | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
PBIC | Patient Bay - Intensive Care | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
PBIC | Patient Bay - Intensive Care | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | optional
PBIC | Patient Bay - Intensive Care | FFE | MMSP-020 | PENDANT: tandem, wet and dry combination (fixed or adjustable height) | 1 | with drawer for patient property
PBIC | Patient Bay - Intensive Care | FFE | ITCL-014 | CLOCK: analogue, electric | 1
PBIC | Patient Bay - Intensive Care | FFE | MMGE-049 | MACHINE: dialysis | 1 | optional, if mobile dialysis required
PBIC | Patient Bay - Intensive Care | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
PBIC | Patient Bay - Intensive Care | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
PBIC | Patient Bay - Intensive Care | FFE | MMHA-023 | VENTILATOR | 1 | on pendant 1-A
PBIC | Patient Bay - Intensive Care | FFE | ITBU-006 | CONTROL PANEL: patient entertainment, handset | 1 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 1
PBIC | Patient Bay - Intensive Care | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | optional
PBIC | Patient Bay - Intensive Care | FFE | MMHA-030 | MONITOR: patient, cardiac, pendant mounted | 1 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FQBS-055 | CHAIR: overnight fold out | 1 | can optionally be a visitor chair
PBIC | Patient Bay - Intensive Care | FFE | FIJO-213 | PANEL: joinery carcass end | 1
PBIC | Patient Bay - Intensive Care | FFE | FQSM-043 | TROLLEY: nested, set of 3, underbench | 1
PBIC | Patient Bay - Intensive Care | FFE | MMBE-068 | LIFTER: patient, pendant mounted | 1 | optional
PBIC | Patient Bay - Intensive Care | FFE | MMGE-178 | PROCESSOR: reverse osmosis RO water, mobile | 1 | optional if mobile dialysis required
PBIC | Patient Bay - Intensive Care | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
PBIC | Patient Bay - Intensive Care | SE | ELPR-006 | RCD: residual current device | 2 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | display screen, clock
PBIC | Patient Bay - Intensive Care | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on tandem pendant, + indicator button & light
PBIC | Patient Bay - Intensive Care | SE | HYTP-008 | OUTLET: cold water | 1 | optional, for mobile reverse osmosis water unit
PBIC | Patient Bay - Intensive Care | SE | LIFX-017 | LIGHT: night light | 1 | wall washers
PBIC | Patient Bay - Intensive Care | SE | ELBO-015 | SWITCH: light, single | 1
PBIC | Patient Bay - Intensive Care | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on tandem pendant, + indicator button & light
PBIC | Patient Bay - Intensive Care | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on tandem pendant, call button on the handset
PBIC | Patient Bay - Intensive Care | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | on tandem pendant, + indicator button & light
PBIC | Patient Bay - Intensive Care | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3 | optional, if mobile dialysis station required
PBIC | Patient Bay - Intensive Care | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
PBIC | Patient Bay - Intensive Care | SE | ELPR-004 | MONITOR: line isolation | 1
PBIC | Patient Bay - Intensive Care | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
PBIC | Patient Bay - Intensive Care | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
PBIC | Patient Bay - Intensive Care | SE | ELBO-012 | SWITCH: light, dimmer | 2 | one on pendant, one to wall
PBIC | Patient Bay - Intensive Care | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 6 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | optionally can be a data outlet for patient entertainment system
PBIC | Patient Bay - Intensive Care | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 3 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-121 | GPO: emergency power, single, on pendant | 16 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
PBIC | Patient Bay - Intensive Care | SE | ELPR-007 | UPS: status indicator | 2 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | HYDR-015 | DRAIN: tundish unit, integral drainage outlets | 1 | optional, if mobile dialysis required
PBIC | Patient Bay - Intensive Care | SE | HYDR-016 | DRAIN: floor waste, sealed | 1
PBSC | Patient Bay - Specimen Collection | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBSC | Patient Bay - Specimen Collection | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
PBSC | Patient Bay - Specimen Collection | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
PBSC | Patient Bay - Specimen Collection | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
PBSC | Patient Bay - Specimen Collection | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 3
PBSC | Patient Bay - Specimen Collection | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PBSC | Patient Bay - Specimen Collection | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PBSC | Patient Bay - Specimen Collection | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | on trolley
PBSC | Patient Bay - Specimen Collection | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 | optional
PBSC | Patient Bay - Specimen Collection | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBSC | Patient Bay - Specimen Collection | FFE | FIHR-026 | HOOK: coat | 2 | optional, prioritize lower hook for wheelchair users if only one hook provided
PBSC | Patient Bay - Specimen Collection | FFE | FIRT-031 | TRACK: curtain, privacy | 1
PBSC | Patient Bay - Specimen Collection | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PBSC | Patient Bay - Specimen Collection | FFE | FQSN-007 | BIN: storage bins, wire mesh, stainless steel | 1 | extent and type of storage to be based on service requirements and local infection control policies
PBSC | Patient Bay - Specimen Collection | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PBSC | Patient Bay - Specimen Collection | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBSC | Patient Bay - Specimen Collection | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBSC | Patient Bay - Specimen Collection | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | on trolley; may be wall mounted or mobile
PBSC | Patient Bay - Specimen Collection | FFE | FQBS-051 | STOOL: mobile, adj height | 1
PBSC | Patient Bay - Specimen Collection | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1
PBSC | Patient Bay - Specimen Collection | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | optional
PBSC | Patient Bay - Specimen Collection | FFE | FQGE-056 | PRINTER: desktop, labels | 1 | optional, on WOW
PBSC | Patient Bay - Specimen Collection | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | a desk may be provided depending on operational model
PBSC | Patient Bay - Specimen Collection | FFE | MMGE-189 | TROLLEY: phlebotomy 600W x 490D x 900H nominal | 1 | with drop down shelf
PBSC | Patient Bay - Specimen Collection | FFE | MMBE-094 | CHAIR: recliner, clinical, phlebotomy | 1 | electric, height adjustable and able to lie flat, electric examination couch may also be provided
PBSC | Patient Bay - Specimen Collection | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
PBSC | Patient Bay - Specimen Collection | SE | ELPR-006 | RCD: residual current device | 1
PBSC | Patient Bay - Specimen Collection | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | optional, to exam light
PBSC | Patient Bay - Specimen Collection | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
PBSC | Patient Bay - Specimen Collection | SE | ELBO-015 | SWITCH: light, single | 1 | optional, to exam light
PBSC | Patient Bay - Specimen Collection | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
PBSC | Patient Bay - Specimen Collection | SE | ELGP-109 | GPO: single, wall mounted | 1 | to chair
PBSC | Patient Bay - Specimen Collection | SE | ELGP-208 | GPO: double, wall mounted | 1
PBSC | Patient Bay - Specimen Collection | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
PBSC | Patient Bay - Specimen Collection | SE | ITSE-006 | BUTTON: duress, fixed | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 | high pressure laminate concealed fixing
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 3 | as required
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MGFP-002 | FLOWMETER: medical air | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-019 | BRACKET: for suction bottle | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQTA-013 | TABLE: overbed | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MGFP-004 | FLOWMETER: oxygen | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3 | wire basket bins
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-002 | ADAPTER: suction | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-100 | SUCTION BOTTLE | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMBE-011 | BED: patient, emergency, electric | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 | optional, or workstation on wheels
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | optional
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-081 | BRACKET: for all-in-one computer, with keyboard shelf, wall mounted, articulated | 1 | optional
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | optional, for cardiac monitor and wall mounted PC, if required
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELPR-006 | RCD: residual current device | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELBO-015 | SWITCH: light, single | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel, + indicator button & light
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | for WOW/ computer
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | shared between a group of beds
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3 | optional, for cardiac monitor and wall mounted PC, if required
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MMSP-026 | SERVICES PANEL: wall mounted | 3
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 | to bedhead wall
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | DWGL-032 | DOOR: 1400mm c/o, 1 1/2 leaf, half glazed, solid core/safety glass, paint | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 2 | optional
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 6
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MGFP-002 | FLOWMETER: medical air | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to internal window
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIHR-019 | BRACKET: for suction bottle | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIDI-030 | DISPENSER: soap | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FQTA-013 | TABLE: overbed | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MGFP-004 | FLOWMETER: oxygen | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MMGE-002 | ADAPTER: suction | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MMGE-100 | SUCTION BOTTLE | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | HYBA-010 | BASIN: handwash, Type B | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MMBE-011 | BED: patient, emergency, electric | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIRT-041 | TRACK: curtain, privacy, U shaped, angled | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIHR-063 | BRACKET: for all-in-one computer, with keyboard shelf, wall mounted | 1 | optional
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 | optional, or workstation on wheels
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | optional
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | for patient monitor and wall mounted PC, if required
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ELPR-006 | RCD: residual current device | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MEEX-008 | EXHAUST: low level | 1 | optional, for negative pressure room
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MGAS-062 | OUTLET: suction, on services panel | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel, + indicator button & light
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3 | for monitor, if required
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MMSP-026 | SERVICES PANEL: wall mounted | 3
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ELBO-012 | SWITCH: light, dimmer | 2 | dimmable to allow paediatric patients to sleep
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | WLWA-021 | WALL FINISH: vinyl, to 1800 AFFL | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MGFP-002 | FLOWMETER: medical air | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIHR-019 | BRACKET: for suction bottle | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIHR-026 | HOOK: coat | 2 | optional
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | shared
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-142 | TROLLEY: sharps bin | 1 | shared
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-002 | ADAPTER: suction | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-100 | SUCTION BOTTLE | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMBE-023 | COUCH: examination, electric, mobile | 1 | optional, may be replaced with a patient chair or recliner
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELPR-006 | RCD: residual current device | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELBO-015 | SWITCH: light, single | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-062 | OUTLET: suction, on services panel | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | shared between a group of beds
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
PBTR-MD | Patient Bay - Medical Day Treatment | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FA | DWWH-005 | WINDOW | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | MGFP-002 | FLOWMETER: medical air | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FIHR-019 | BRACKET: for suction bottle | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | DWWD-004 | BLIND: roller | 1 | dependent on local infection control policies and service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FQGE-010 | CURTAIN: privacy screen | 2
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | MMGE-119 | TROLLEY: equipment | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FQTA-013 | TABLE: overbed | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | quantity to be rationalised across the unit to suit number of staff
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | MMGE-002 | ADAPTER: suction | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | MMGE-100 | SUCTION BOTTLE | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | MMGE-023 | CHAIR: recliner, clinical, electric | 1 | or bed
PBTR-MD | Patient Bay - Medical Day Treatment | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | optional, dependent on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ELPR-006 | RCD: residual current device | 2
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | to patient entertainment screen
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
PBTR-MD | Patient Bay - Medical Day Treatment | SE | LIFX-011 | LIGHT: reading light | 1 | hardwired
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ELBO-015 | SWITCH: light, single | 1 | to exam light
PBTR-MD | Patient Bay - Medical Day Treatment | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset, reading light control
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ELGP-109 | GPO: single, wall mounted | 2 | low level, for bed/recliner
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ELGP-206 | GPO: double, on services panel, RCD protected | 1
PBTR-MD | Patient Bay - Medical Day Treatment | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2 | 1 panel for medical gases may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ELGP-105 | GPO: single, on services panel | 2
PBTR-MD | Patient Bay - Medical Day Treatment | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 3
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 3
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | MGFP-002 | FLOWMETER: medical air | 1 | to services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIHR-026 | HOOK: coat | 2 | optional
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | to services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | MMGE-002 | ADAPTER: suction | 1 | to services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | MMGE-100 | SUCTION BOTTLE | 1 | on bracket
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | MMBE-011 | BED: patient, emergency, electric | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | MMHA-005 | MONITOR: patient, cardiac | 1 | optional
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1 | optional
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional, for monitor
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ELPR-006 | RCD: residual current device | 2
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ELGP-101 | GPO: single, ceiling mounted | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | LIFX-011 | LIGHT: reading light | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | LIFX-017 | LIGHT: night light | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ELBO-015 | SWITCH: light, single | 2 | to services panel for bay light control and to wall for night light
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | shared between a group of beds
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2 | optional, for monitor
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | MMSP-026 | SERVICES PANEL: wall mounted | 3
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ITIN-071 | OUTLET: MATV, ceiling mounted | 1
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on service panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | WLPR-019 | WALL PROTECTION: crash rail, at 900 AFFL, prefinished PVC | 1 | as required
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 3 | as required
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 5
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MGFP-002 | FLOWMETER: medical air | 1 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQGE-010 | CURTAIN: privacy screen | 2
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 | optional, for slave display screen
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIDI-021 | DISPENSER: mask | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 | optional, for slave display screen
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-126 | TROLLEY: intubation | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-039 | HANGER: IV, for ceiling track | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIRT-020 | TRACK: ceiling mounted, IV | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MGFP-004 | FLOWMETER: oxygen | 3 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMHA-027 | TROLLEY: resuscitation, adult | 1 | where more than one resuscitation bay may be centrally located
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-088 | SAFE: dangerous drugs, small | 1 | optional, where more than one resuscitation bay may be centrally located
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-002 | ADAPTER: suction | 3 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-100 | SUCTION BOTTLE | 3 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQSM-039 | TROLLEY: waste bag | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQSM-003 | PEDESTAL: mobile, wire basket unit, 840H | 2
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 1 | for patient management system
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1 | refer BHWS-A (similar)
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMBE-011 | BED: patient, emergency, electric | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITCL-012 | CAMERA: observation | 2 | optional, for telemedecine
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMHA-002 | DEFIBRILLATOR | 1 | on resuscitation trolley
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 2 | optional, one to wall, one to ceiling
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-036 | FRIDGE: drugs, underbench | 1 | optional, where more than one resuscitation bay may be centrally located
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMSP-018 | PENDANT: single, wet and dry combination (fixed or adjustable height) | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | to bench
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMHA-023 | VENTILATOR | 1 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | open under part
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITCL-020 | CLOCK: clock system slave, dual digital / elapsed time | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIJO-099 | CAC: cable access cap | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMHA-030 | MONITOR: patient, cardiac, pendant mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIJO-216 | CUPBOARD: pigeon holes, under bench | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FQSM-043 | TROLLEY: nested, set of 3, underbench | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIHR-076 | BRACKET: for display screen, triple, desk mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-175 | DIAGNOSTIC SET: pendant mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-176 | PUMP: infusion, pendant mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | FIHR-077 | BRACKET: for observation camera, ceiling mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMGE-177 | PUMP: syringe, pendant mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | ITNE-070 | DISPLAY SCREEN: PACS | 2
PBTR-R | Patient Bay, Emergency - Resuscitation | FFE | MMSP-037 | LIGHT: operating, single, 550 diam nom. pendant mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 4 | optional, where supplying data to drug fridge and slave display screens
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELPR-006 | RCD: residual current device | 2
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on pendant + indicator button & light
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELBO-015 | SWITCH: light, single | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on pendant + indicator button & light
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on pendant + indicator button & light
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 5 | one to resus. trolley
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 1 | optional, for optional drug fridge
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 2
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 5
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITCL-023 | CONTROL PANEL: master clock system | 1
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ITIN-034 | OUTLET: data, triple RJ45, on pendant | 2
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | optional, on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 3 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | optional, on pendant, if N2O provided
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELGP-132 | GPO: UPS, single, on pendant | 4
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELGP-121 | GPO: emergency power, single, on pendant | 8 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | ELPR-007 | UPS: status indicator | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent; a higher slip rating may be required depending on local WHS policies
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | optional, to side walls if provided
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 2 | optional, to side walls if provided
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | DWWH-005 | WINDOW | 1 | access to natural light and external outlook essential
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | DWWD-004 | BLIND: roller | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQGE-010 | CURTAIN: privacy screen | 2
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQTA-013 | TABLE: overbed | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-002 | ADAPTER: suction | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-100 | SUCTION BOTTLE | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-023 | CHAIR: recliner, clinical, electric | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-049 | MACHINE: dialysis | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | MMGE-096 | STATION: combination dialysis connection point and waste water tundish | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | optional
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | FFE | HYDR-019 | ACCESS PANEL: waterless trap | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELPR-006 | RCD: residual current device | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment system, may be replaced with data outlet depending on ICT policy
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to patient entertainment system
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | HYDR-004 | DRAIN: floor waste | 1 | in case of spills, to be consolidated between multiple bays
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | LIFX-011 | LIGHT: reading light | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELBO-015 | SWITCH: light, single | 1 | optional
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button and reading light switch on handset
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | low level, to recliner
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | SE | ELGP-222 | GPO: emergency power, double, on services panel | 3
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent; a higher slip rating may be required depending on local WHS policies
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | optional, to side walls if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 2 | optional, to side walls if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | DWWH-005 | WINDOW | 1 | access to natural light and external outlook essential
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | DWWD-004 | BLIND: roller | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FQGE-010 | CURTAIN: privacy screen | 2
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FQTA-013 | TABLE: overbed | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | MMGE-002 | ADAPTER: suction | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | MMGE-100 | SUCTION BOTTLE | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | MMBE-009 | BED: patient, electric | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | MMGE-049 | MACHINE: dialysis | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | MMGE-096 | STATION: combination dialysis connection point and waste water tundish | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | optional
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | FFE | HYDR-019 | ACCESS PANEL: waterless trap | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ELPR-006 | RCD: residual current device | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment system, may be replaced with data outlet depending on ICT policy
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to patient entertainment system
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | HYDR-004 | DRAIN: floor waste | 1 | in case of spills, to be consolidated between multiple bays
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | LIFX-011 | LIGHT: reading light | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ELBO-015 | SWITCH: light, single | 1 | optional
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button and reading light switch on handset
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | low level, to bed
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | SE | ELGP-222 | GPO: emergency power, double, on services panel | 3
PET-CT | PET-CT Imaging Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
PET-CT | PET-CT Imaging Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
PET-CT | PET-CT Imaging Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
PET-CT | PET-CT Imaging Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
PET-CT | PET-CT Imaging Room | FA | WLWA-007 | WALL FINISH: splashback | 1
PET-CT | PET-CT Imaging Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PET-CT | PET-CT Imaging Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 6
PET-CT | PET-CT Imaging Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PET-CT | PET-CT Imaging Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1 | automated
PET-CT | PET-CT Imaging Room | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1 | automated
PET-CT | PET-CT Imaging Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PET-CT | PET-CT Imaging Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 1
PET-CT | PET-CT Imaging Room | FFE | MGFP-002 | FLOWMETER: medical air | 1 | on services panel
PET-CT | PET-CT Imaging Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2
PET-CT | PET-CT Imaging Room | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PET-CT | PET-CT Imaging Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PET-CT | PET-CT Imaging Room | FFE | FIJO-141 | CUPBOARD: underbench, single door, adj shelves, lockable | 1
PET-CT | PET-CT Imaging Room | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 3
PET-CT | PET-CT Imaging Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
PET-CT | PET-CT Imaging Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | near door
PET-CT | PET-CT Imaging Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PET-CT | PET-CT Imaging Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PET-CT | PET-CT Imaging Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PET-CT | PET-CT Imaging Room | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 1
PET-CT | PET-CT Imaging Room | FFE | MMGE-045 | IV STAND: mobile | 1 | may be ceiling mounted
PET-CT | PET-CT Imaging Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
PET-CT | PET-CT Imaging Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | on services panel
PET-CT | PET-CT Imaging Room | FFE | MMBE-042 | SLIDE: patient | 1
PET-CT | PET-CT Imaging Room | FFE | MMGE-142 | TROLLEY: sharps bin | 1
PET-CT | PET-CT Imaging Room | FFE | MMGE-091 | SPHYGMOMANOMETER: portable | 1
PET-CT | PET-CT Imaging Room | FFE | MMGE-002 | ADAPTER: suction | 2 | on services panel
PET-CT | PET-CT Imaging Room | FFE | MMGE-100 | SUCTION BOTTLE | 2
PET-CT | PET-CT Imaging Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
PET-CT | PET-CT Imaging Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
PET-CT | PET-CT Imaging Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
PET-CT | PET-CT Imaging Room | FFE | ITCL-012 | CAMERA: observation | 3
PET-CT | PET-CT Imaging Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
PET-CT | PET-CT Imaging Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
PET-CT | PET-CT Imaging Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
PET-CT | PET-CT Imaging Room | FFE | MMMI-207 | DEVICE: imaging, PET/CT | 1
PET-CT | PET-CT Imaging Room | FFE | MMMI-209 | PHANTOM: PET/CT | 1 | stored within shielded custom joinery
PET-CT | PET-CT Imaging Room | FFE | MMMI-217 | TABLE: patient, fixed, PET/CT | 1
PET-CT | PET-CT Imaging Room | FFE | MMMI-107 | INJECTOR: contrast, CT, ceiling mounted | 1 | also may be mobile or wall mounted
PET-CT | PET-CT Imaging Room | FFE | MMMI-218 | LASER: positioning lights, PET/CT | 1
PET-CT | PET-CT Imaging Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
PET-CT | PET-CT Imaging Room | FFE | MMMI-377 | WARMER: contrast | 1 | optional
PET-CT | PET-CT Imaging Room | FFE | FIJO-218 | CUPBOARD: tall, double door, adj shelves, lockable, heavy duty | 1
PET-CT | PET-CT Imaging Room | FFE | FIHR-077 | BRACKET: for observation camera, ceiling mounted | 2
PET-CT | PET-CT Imaging Room | FFE | FIHR-078 | BRACKET: for observation camera, wall mounted | 1
PET-CT | PET-CT Imaging Room | FFE | FIHR-092 | HOOK: anchor, patient ladder | 1
PET-CT | PET-CT Imaging Room | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 2
PET-CT | PET-CT Imaging Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3
PET-CT | PET-CT Imaging Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | on wall near PET-CT unit
PET-CT | PET-CT Imaging Room | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | handsfree to control room
PET-CT | PET-CT Imaging Room | SE | ELPR-006 | RCD: residual current device | 1 | on services panel
PET-CT | PET-CT Imaging Room | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 2
PET-CT | PET-CT Imaging Room | SE | ELGP-101 | GPO: single, ceiling mounted | 3 | 1-laser positioning light
PET-CT | PET-CT Imaging Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
PET-CT | PET-CT Imaging Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, on services panel
PET-CT | PET-CT Imaging Room | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | alarm for temperature range
PET-CT | PET-CT Imaging Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | to outside of all doors to room, auto on when modality is in use, vendor to provide signal wiring to light
PET-CT | PET-CT Imaging Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
PET-CT | PET-CT Imaging Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, on services panel
PET-CT | PET-CT Imaging Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
PET-CT | PET-CT Imaging Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
PET-CT | PET-CT Imaging Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light
PET-CT | PET-CT Imaging Room | SE | ELGP-109 | GPO: single, wall mounted | 2 | 1-clock
PET-CT | PET-CT Imaging Room | SE | ELGP-208 | GPO: double, wall mounted | 3
PET-CT | PET-CT Imaging Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | to walls
PET-CT | PET-CT Imaging Room | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 1
PET-CT | PET-CT Imaging Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
PET-CT | PET-CT Imaging Room | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
PET-CT | PET-CT Imaging Room | SE | ELGP-203 | GPO: double, in floorbox | 4
PET-CT | PET-CT Imaging Room | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
PET-CT | PET-CT Imaging Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | patient services
PET-CT | PET-CT Imaging Room | SE | WLSH-004 | SHIELDING: lead lining | 1 | to room doors, walls, (ceiling) as required by radiation consultant design and specification
PET-CT | PET-CT Imaging Room | SE | ELBO-012 | SWITCH: light, dimmer | 1 | number determined by number of doors
PET-CT | PET-CT Imaging Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PET-CT | PET-CT Imaging Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on service panel
PET-CT | PET-CT Imaging Room | SE | ELPR-007 | UPS: status indicator | 1 | on service panel
PET-CT | PET-CT Imaging Room | SE | LIFX-038 | LIGHT: backlit feature panels | 2
PHA-CO | Pharmacy - Counter | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1 | vinyl is also acceptable
PHA-CO | Pharmacy - Counter | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 12 | seamless coved vinyl skirting if vinyl flooring provided
PHA-CO | Pharmacy - Counter | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 7
PHA-CO | Pharmacy - Counter | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PHA-CO | Pharmacy - Counter | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PHA-CO | Pharmacy - Counter | FFE | FQSN-028 | CABINET: pass through | 1 | lockable, under bench, for transfer of large items
PHA-CO | Pharmacy - Counter | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
PHA-CO | Pharmacy - Counter | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
PHA-CO | Pharmacy - Counter | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2
PHA-CO | Pharmacy - Counter | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | quantity and type of bins to be based on local waste management policies
PHA-CO | Pharmacy - Counter | FFE | FIJO-114 | CUPBOARD: drawer unit, lockable | 1
PHA-CO | Pharmacy - Counter | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2
PHA-CO | Pharmacy - Counter | FFE | ITNE-023 | PRINTER: networked | 1 | optional
PHA-CO | Pharmacy - Counter | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
PHA-CO | Pharmacy - Counter | FFE | FIJO-058 | BENCH TOP: 600D, joinery under | 2
PHA-CO | Pharmacy - Counter | FFE | FIJO-051 | BENCH TOP: 450D, joinery under | 1
PHA-CO | Pharmacy - Counter | FFE | FIJO-099 | CAC: cable access cap | 2
PHA-CO | Pharmacy - Counter | FFE | FIJO-213 | PANEL: joinery carcass end | 1
PHA-CO | Pharmacy - Counter | FFE | FQCW-064 | BIN: waste, paper, secure, 20L | 1 | quantity and type of bins to be based on local waste management policies
PHA-CO | Pharmacy - Counter | FFE | FIJO-229 | JOINERY UNIT: reception counter, pharmacy | 1
PHA-CO | Pharmacy - Counter | FFE | FIJO-230 | JOINERY UNIT: reception counter, pharmacy, accessible | 1
PHA-CO | Pharmacy - Counter | FFE | WLPT-015 | SCREEN: security, safety glass, with communication slot and pass through | 2
PHA-CO | Pharmacy - Counter | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3
PHA-CO | Pharmacy - Counter | SE | ELBO-015 | SWITCH: light, single | 1
PHA-CO | Pharmacy - Counter | SE | ELGP-208 | GPO: double, wall mounted | 3
PHA-CO | Pharmacy - Counter | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | extent of emergency power to be determined based on service requirements
PHA-CO | Pharmacy - Counter | SE | ITSE-006 | BUTTON: duress, fixed | 1 | shared, below desk
PHA-DB | Pharmacy - Distribution Workstation | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PHA-DB | Pharmacy - Distribution Workstation | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
PHA-DB | Pharmacy - Distribution Workstation | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PHA-DB | Pharmacy - Distribution Workstation | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PHA-DB | Pharmacy - Distribution Workstation | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PHA-DB | Pharmacy - Distribution Workstation | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
PHA-DB | Pharmacy - Distribution Workstation | FFE | FQDW-002 | DESK: adj height, 1800W x 750D x 750H nom. | 1
PHA-DB | Pharmacy - Distribution Workstation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
PHA-DB | Pharmacy - Distribution Workstation | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 1
PHA-DB | Pharmacy - Distribution Workstation | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | may be on wall or desk mounted bracket, an additional screen may be provided depending on project ICT requirements
PHA-DB | Pharmacy - Distribution Workstation | FFE | ITNE-003 | BAR CODING: reader | 1
PHA-DB | Pharmacy - Distribution Workstation | FFE | FIJO-069 | BENCH TOP: 750D, joinery under, laminate finish | 1
PHA-DB | Pharmacy - Distribution Workstation | FFE | ITNE-072 | BAR CODING: PDE dock | 1 | may be shared between multiple workstations
PHA-DB | Pharmacy - Distribution Workstation | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
PHA-DB | Pharmacy - Distribution Workstation | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | extent of emergency power to be determined based on service requirements
PHA-DS | Pharmacy - Dispensing Workstation | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PHA-DS | Pharmacy - Dispensing Workstation | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PHA-DS | Pharmacy - Dispensing Workstation | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PHA-DS | Pharmacy - Dispensing Workstation | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
PHA-DS | Pharmacy - Dispensing Workstation | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | quantity and type of bins to be based on local waste management policies
PHA-DS | Pharmacy - Dispensing Workstation | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 1 | optional, depending on project ICT requirements; may be on desk mounted bracket
PHA-DS | Pharmacy - Dispensing Workstation | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | may be on desk mounted bracket
PHA-DS | Pharmacy - Dispensing Workstation | FFE | ITNE-003 | BAR CODING: reader | 1
PHA-DS | Pharmacy - Dispensing Workstation | FFE | FQDW-046 | WORKSTATION: pharmacy,straight, adj height, 1800W x 750D x 900H nom. | 1
PHA-DS | Pharmacy - Dispensing Workstation | FFE | FQDW-047 | WORKSTATION: pharmacy, services spine bench | 1 | services spine may be shared between multiple workstations
PHA-DS | Pharmacy - Dispensing Workstation | FFE | FQDW-048 | WORKSTATION: pharmacy, services spine shelves | 1 | services spine may be shared between multiple workstations
PHA-DS | Pharmacy - Dispensing Workstation | FFE | FQCW-064 | BIN: waste, paper, secure, 20L | 1 | quantity and type of bins to be based on local waste management policies
PHA-DS | Pharmacy - Dispensing Workstation | FFE | FQGE-093 | PRINTER: desktop, labels, pharmacy | 1
PHA-DS | Pharmacy - Dispensing Workstation | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2
PHA-DS | Pharmacy - Dispensing Workstation | SE | ELGP-208 | GPO: double, wall mounted | 1
PHA-DS | Pharmacy - Dispensing Workstation | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | extent of emergency power to be determined based on service requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent to extend under basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 11
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 6
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 4
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1 | may be height adjustable item depending on service requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-141 | CUPBOARD: underbench, single door, adj shelves, lockable | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 3
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-148 | CUPBOARD: wall mount, double door, glazed, adj shelves, lockable | 3
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-159 | CUPBOARD: wall mount, single door, glazed, adj shelves, lockable | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQSM-016 | TROLLEY | 1 | optional
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYBA-010 | BASIN: handwash, Type B | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYBA-069 | SINK: single, with drainer, 930mmL | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | MEEX-013 | FUME CUPBOARD | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 2
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FIJO-212 | BULKHEAD: joinery | 2
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | MMGE-185 | SCALES: digital, benchtop | 2
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | FFE | FQCW-065 | BIN: waste, pharmaceutical 50L | 1 | quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | SE | LIFX-008 | LIGHT: task light, built in | 2 | under wall mounted joinery
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 2 x task lights
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | SE | ELGP-208 | GPO: double, wall mounted | 4 | provision of emergency power to be determined based on service requirements
PHA-RE | Pharmacy - Returns Workstation | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PHA-RE | Pharmacy - Returns Workstation | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PHA-RE | Pharmacy - Returns Workstation | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PHA-RE | Pharmacy - Returns Workstation | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PHA-RE | Pharmacy - Returns Workstation | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PHA-RE | Pharmacy - Returns Workstation | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
PHA-RE | Pharmacy - Returns Workstation | FFE | FQDW-002 | DESK: adj height, 1800W x 750D x 750H nom. | 1
PHA-RE | Pharmacy - Returns Workstation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
PHA-RE | Pharmacy - Returns Workstation | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | may be on wall or desk mounted bracket, an additional screen may be provided depending on project ICT requirements
PHA-RE | Pharmacy - Returns Workstation | FFE | ITNE-003 | BAR CODING: reader | 1
PHA-RE | Pharmacy - Returns Workstation | FFE | FQSM-045 | SHELVING: storage solution, 400W x 600D x 2100H nom., wire, mobile | 2
PHA-RE | Pharmacy - Returns Workstation | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
PHA-RE | Pharmacy - Returns Workstation | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | extent of emergency power to be determined based on service requirements
PLAY | Play Area - Paediatric | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PLAY | Play Area - Paediatric | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
PLAY | Play Area - Paediatric | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
PLAY | Play Area - Paediatric | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PLAY | Play Area - Paediatric | FA | DWWH-005 | WINDOW | 1 | desirable
PLAY | Play Area - Paediatric | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PLAY | Play Area - Paediatric | FFE | FQGE-002 | ARTWORK | 1
PLAY | Play Area - Paediatric | FFE | FQBS-012 | CHAIR: child | 2
PLAY | Play Area - Paediatric | FFE | FQBS-032 | CHAIR: waiting | 2
PLAY | Play Area - Paediatric | FFE | DWWD-004 | BLIND: roller | 1
PLAY | Play Area - Paediatric | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PLAY | Play Area - Paediatric | FFE | FQTA-003 | TABLE: children's play | 1
PLAY | Play Area - Paediatric | FFE | FQTA-075 | TABLE: square, 600W, low height | 1
PLAY | Play Area - Paediatric | SE | ELGP-208 | GPO: double, wall mounted | 1
PLNT-WT | Plant - Water Treatment | FA | FLGE-003 | FLOOR FINISH: concrete, sealed, trowel | 1
PLNT-WT | Plant - Water Treatment | FA | FLSK-002 | SKIRTING: concrete, coved to 150 AFFL, sealed | 6
PLNT-WT | Plant - Water Treatment | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
PLNT-WT | Plant - Water Treatment | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
PLNT-WT | Plant - Water Treatment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PLNT-WT | Plant - Water Treatment | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1
PLNT-WT | Plant - Water Treatment | FA | DWSC-027 | DOOR: 1600mm c/o, 1 1/2 leaf, solid core, paint | 1 | lockable
PLNT-WT | Plant - Water Treatment | FA | DWSC-027 | DOOR: 1600mm c/o, 1 1/2 leaf, solid core, paint | 1 | optional secondary access door, lockable
PLNT-WT | Plant - Water Treatment | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PLNT-WT | Plant - Water Treatment | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | optional
PLNT-WT | Plant - Water Treatment | FFE | MEGE-010 | HEAT EXCHANGER: supplied by mechanical chilled water | 1 | as required; may be necessary to cool feed water where high temperatures are expected, refer to technical expert for required outlet temperature (generally <25°C)
PLNT-WT | Plant - Water Treatment | FFE | HYGE-016 | PUMP: pressure booster | 2 | to suit water pressure drop through pre-filtration train where building water pressure and flow is inadequate
PLNT-WT | Plant - Water Treatment | FFE | HYGE-012 | WATER TREATMENT: reverse osmosis plant | 1 | details according to manufacturer's specifications
PLNT-WT | Plant - Water Treatment | FFE | FQSN-138 | PALLET: half size | 1
PLNT-WT | Plant - Water Treatment | FFE | HYGE-027 | DEVICE: UV irradiator | 1
PLNT-WT | Plant - Water Treatment | FFE | FQDW-051 | DESK: adj height, 1500W x 600D x 900H nom. | 1 | optional
PLNT-WT | Plant - Water Treatment | SE | ITBU-002 | ALARM: equipment monitoring, water treatment malfunction | 1 | connected to BMS and staff station in unit
PLNT-WT | Plant - Water Treatment | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
PLNT-WT | Plant - Water Treatment | SE | HYTP-008 | OUTLET: cold water | 1
PLNT-WT | Plant - Water Treatment | SE | HYDR-004 | DRAIN: floor waste | 1 | floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | SE | HYDR-006 | DRAIN: tundish | 2
PLNT-WT | Plant - Water Treatment | SE | ELBO-015 | SWITCH: light, single | 1
PLNT-WT | Plant - Water Treatment | SE | ELBO-010 | SWITCH: light, 2-way | 1 | optional
PLNT-WT | Plant - Water Treatment | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 8 | for water treatment equipment, high level (power tools to be on a separate circuit)
PLNT-WT | Plant - Water Treatment | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | optional, dependent on equipment
PLNT-WT | Plant - Water Treatment | SE | HYGE-020 | WATER TREATMENT: carbon filter | 3 | 1 is optional; size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-019 | WATER TREATMENT: brine tank | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-024 | WATER TREATMENT: softener tank | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-021 | WATER TREATMENT: multimedia tank | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-023 | WATER TREATMENT: particle filter, 5 microns | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYGE-022 | WATER TREATMENT: particle filter, 1 micron | 1 | size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | SE | HYDR-017 | DRAIN: floor waste, 300 x 300 | 1 | floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | SE | ITBU-024 | ALARM: chlorine meter | 1 | optional, dependent on local operational policies
PLNT-WT | Plant - Water Treatment | SE | HYGE-028 | DEVICE: backflow prevention | 1
PLNT-WT | Plant - Water Treatment | SE | HYDR-018 | DRAIN: tundish, floor drain | 1 | tundish must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLST | Plaster Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PLST | Plaster Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PLST | Plaster Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
PLST | Plaster Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
PLST | Plaster Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
PLST | Plaster Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PLST | Plaster Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1
PLST | Plaster Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PLST | Plaster Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
PLST | Plaster Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PLST | Plaster Room | FFE | MGFP-002 | FLOWMETER: medical air | 1
PLST | Plaster Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | quantity to suit number of suction outlets
PLST | Plaster Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PLST | Plaster Room | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 3
PLST | Plaster Room | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 3
PLST | Plaster Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PLST | Plaster Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
PLST | Plaster Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
PLST | Plaster Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PLST | Plaster Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PLST | Plaster Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PLST | Plaster Room | FFE | MMBE-043 | TROLLEY: patient, examination | 1 | or plinth/examination couch
PLST | Plaster Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | quantity to suit number of oxygen outlets
PLST | Plaster Room | FFE | MMMA-011 | MIXER: oxygen and nitrous oxide | 1 | optional, may be mobile, on trolley or wall mounted
PLST | Plaster Room | FFE | MMAH-028 | TROLLEY: plaster | 1
PLST | Plaster Room | FFE | MMGE-002 | ADAPTER: suction | 2 | quantity to suit number of suction outlets
PLST | Plaster Room | FFE | MMGE-100 | SUCTION BOTTLE | 2 | quantity to suit number of suction outlets
PLST | Plaster Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
PLST | Plaster Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
PLST | Plaster Room | FFE | HYTP-038 | TAPWARE: mixer, elbow levers, long | 1 | to sink
PLST | Plaster Room | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PLST | Plaster Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
PLST | Plaster Room | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 | optional, may be portable/mobile on stand
PLST | Plaster Room | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
PLST | Plaster Room | FFE | HYDR-008 | TRAP: plaster | 1 | to be easily accessible for cleaning and maintenance
PLST | Plaster Room | FFE | MMAH-023 | SAW: plaster | 1 | integral/localised dust extraction required
PLST | Plaster Room | FFE | HYBA-053 | SINK: single, 450 x 350 x 300D | 1 | hot water
PLST | Plaster Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
PLST | Plaster Room | FFE | FIJO-060 | BENCH TOP: 600D, joinery under, stainless steel lipped | 1 | with sink and wet edge
PLST | Plaster Room | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1 | optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
PLST | Plaster Room | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PLST | Plaster Room | FFE | MMGE-001 | ADAPTER: scavenge | 1
PLST | Plaster Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
PLST | Plaster Room | FFE | FIRT-039 | TRACK: curtain, privacy, Z shaped, angled | 1
PLST | Plaster Room | FFE | MMAH-045 | VACUUM: plaster saw | 1 | or independent dust extraction system
PLST | Plaster Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to telephone
PLST | Plaster Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
PLST | Plaster Room | SE | ELPR-006 | RCD: residual current device | 4
PLST | Plaster Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to exam light
PLST | Plaster Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
PLST | Plaster Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1
PLST | Plaster Room | SE | LIFX-008 | LIGHT: task light, built in | 3
PLST | Plaster Room | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 1 x task light, 1 x examination light
PLST | Plaster Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 is optional, quantity dependent on service requirements
PLST | Plaster Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1
PLST | Plaster Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PLST | Plaster Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 is optional, quantity dependent on service requirements
PLST | Plaster Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
PLST | Plaster Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
PLST | Plaster Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
PLST | Plaster Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for patient trolley
PLST | Plaster Room | SE | ELGP-208 | GPO: double, wall mounted | 4
PLST | Plaster Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
PLST | Plaster Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
PLST | Plaster Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PLST | Plaster Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PLST | Plaster Room | SE | ELGP-105 | GPO: single, on services panel | 3
PLST | Plaster Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3
PROC | Procedure Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PROC | Procedure Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
PROC | Procedure Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
PROC | Procedure Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
PROC | Procedure Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PROC | Procedure Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 4
PROC | Procedure Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PROC | Procedure Room | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 2
PROC | Procedure Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
PROC | Procedure Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PROC | Procedure Room | FFE | MGFP-002 | FLOWMETER: medical air | 1
PROC | Procedure Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | quantity to suit number of suction outlets
PROC | Procedure Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PROC | Procedure Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PROC | Procedure Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
PROC | Procedure Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
PROC | Procedure Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
PROC | Procedure Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PROC | Procedure Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
PROC | Procedure Room | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
PROC | Procedure Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
PROC | Procedure Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PROC | Procedure Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PROC | Procedure Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PROC | Procedure Room | FFE | MMGE-119 | TROLLEY: equipment | 1
PROC | Procedure Room | FFE | MMBE-043 | TROLLEY: patient, examination | 1
PROC | Procedure Room | FFE | FIHR-011 | BRACKET: for monitor, wall mounted | 1 | optional, for cardiac/vital signs monitor
PROC | Procedure Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | quantity to suit number of oxygen outlets
PROC | Procedure Room | FFE | MMMA-011 | MIXER: oxygen and nitrous oxide | 1 | optional, may be mobile, on trolley or wall mounted
PROC | Procedure Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
PROC | Procedure Room | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1
PROC | Procedure Room | FFE | MMGE-002 | ADAPTER: suction | 2 | quantity to suit number of suction outlets
PROC | Procedure Room | FFE | MMGE-100 | SUCTION BOTTLE | 2 | quantity to suit number of suction outlets
PROC | Procedure Room | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
PROC | Procedure Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
PROC | Procedure Room | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PROC | Procedure Room | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PROC | Procedure Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
PROC | Procedure Room | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 | optional, may be portable/mobile on stand
PROC | Procedure Room | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1 | optional
PROC | Procedure Room | FFE | ITNE-023 | PRINTER: networked | 1 | optional
PROC | Procedure Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
PROC | Procedure Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
PROC | Procedure Room | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1 | optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
PROC | Procedure Room | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PROC | Procedure Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
PROC | Procedure Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 to telephone, 1 - optional, for cardiac/vital signs monitor
PROC | Procedure Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2
PROC | Procedure Room | SE | ELPR-006 | RCD: residual current device | 4
PROC | Procedure Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to procedure light
PROC | Procedure Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
PROC | Procedure Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, dependent on service requirements, provide if nitrous oxide required
PROC | Procedure Room | SE | LIFX-008 | LIGHT: task light, built in | 1
PROC | Procedure Room | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 1 x task light, 1 x examination light
PROC | Procedure Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, dependent on service requirements
PROC | Procedure Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PROC | Procedure Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
PROC | Procedure Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
PROC | Procedure Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
PROC | Procedure Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for patient trolley
PROC | Procedure Room | SE | ELGP-208 | GPO: double, wall mounted | 2
PROC | Procedure Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
PROC | Procedure Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | optional, for cardiac/vital signs monitor
PROC | Procedure Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
PROC | Procedure Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PROC | Procedure Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PROC | Procedure Room | SE | ELGP-105 | GPO: single, on services panel | 3
PROC | Procedure Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3
PT-HOLD-A | Patient Bay - Holding, Chair | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | acoustic tiles are also acceptable
PT-HOLD-A | Patient Bay - Holding, Chair | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | MGFP-002 | FLOWMETER: medical air | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FQBS-030 | CHAIR: visitor, patient | 1 | optional
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 | type and extent of storage dependant on operational policies for stock centralisation/decanting and infection prevention and control policies
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 4 | type and size of bins dependant on items to be stored
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | MMGE-002 | ADAPTER: suction | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | MMGE-100 | SUCTION BOTTLE | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | shared between multiple bays
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | shared between multiple bays
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | FIRT-047 | TRACK: curtain, privacy, U shaped | 1
PT-HOLD-A | Patient Bay - Holding, Chair | FFE | MMBE-091 | CHAIR: recliner, clinical, electric | 1
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional, for patient monitoring
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
PT-HOLD-A | Patient Bay - Holding, Chair | SE | LIFX-032 | LIGHT: downlight, examination, ceiling mounted | 1 | optional, provision dependant on service requirements; articulated examination light is also acceptable
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, with indicator button and light
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ELBO-015 | SWITCH: light, single | 1 | optional, to services panel, for examination downlight if provided
PT-HOLD-A | Patient Bay - Holding, Chair | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PT-HOLD-A | Patient Bay - Holding, Chair | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PT-HOLD-A | Patient Bay - Holding, Chair | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, with indicator button and light
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ELGP-109 | GPO: single, wall mounted | 1 | low, for patient recliner
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ELGP-208 | GPO: double, wall mounted | 1 | for patient's own devices
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | optional, for patient monitoring
PT-HOLD-A | Patient Bay - Holding, Chair | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | quantity to suit service requirements
PT-HOLD-A | Patient Bay - Holding, Chair | SE | ELGP-122 | GPO: emergency power, single, on services panel | 5 | type and quantity to suit service requirements
PT-HOLD-B | Patient Bay - Holding, Bed | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | acoustic tiles are also acceptable
PT-HOLD-B | Patient Bay - Holding, Bed | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | MGFP-002 | FLOWMETER: medical air | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FQBS-030 | CHAIR: visitor, patient | 1 | optional
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 | type and extent of storage dependant on operational policies for stock centralisation/decanting and infection prevention and control policies
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 4 | type and size of bins dependant on items to be stored
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | MMGE-002 | ADAPTER: suction | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | MMGE-100 | SUCTION BOTTLE | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | MMBE-007 | BED: patient, day procedure, electric | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | shared between multiple bays
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | shared between multiple bays
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FIHR-068 | BRACKET: for alcohol based hand rub, attached to bed | 1
PT-HOLD-B | Patient Bay - Holding, Bed | FFE | FIRT-047 | TRACK: curtain, privacy, U shaped | 1
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional, for patient monitoring
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ELPR-006 | RCD: residual current device | 2 | to services panel
PT-HOLD-B | Patient Bay - Holding, Bed | SE | LIFX-032 | LIGHT: downlight, examination, ceiling mounted | 1 | optional, provision dependant on service requirements; articulated examination light is also acceptable
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ELBO-015 | SWITCH: light, single | 1 | optional, to services panel, for examination downlight if provided
PT-HOLD-B | Patient Bay - Holding, Bed | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PT-HOLD-B | Patient Bay - Holding, Bed | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PT-HOLD-B | Patient Bay - Holding, Bed | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ELGP-109 | GPO: single, wall mounted | 1 | low, for patient bed
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ELGP-208 | GPO: double, wall mounted | 1 | for patient's own devices
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | optional, for patient monitoring
PT-HOLD-B | Patient Bay - Holding, Bed | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | quantity to suit service requirements
PT-HOLD-B | Patient Bay - Holding, Bed | SE | ELGP-122 | GPO: emergency power, single, on services panel | 5 | type and quantity to suit service requirements
PT-RS1 | Patient Bay - Recovery, Stage 1 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MGFP-002 | FLOWMETER: medical air | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FQGE-010 | CURTAIN: privacy screen | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FIHR-029 | HOOK: equipment | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMGE-119 | TROLLEY: equipment | 1 | shared between multiple bays
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMGE-045 | IV STAND: mobile | 1 | bed mounted IV pole or ceiling mounted IV track are also acceptable
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 | type and extent of storage dependant on operational policies for stock centralisation/decanting and infection prevention and control policies
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMGE-142 | TROLLEY: sharps bin | 1 | shared between multiple bays
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 4 | type and size of bins dependant on items to be stored
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMGE-002 | ADAPTER: suction | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMGE-100 | SUCTION BOTTLE | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMBE-007 | BED: patient, day procedure, electric | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | shared between multiple bays
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1 | may be located on left or right side of bedhead depending on monitor functionality and staff workflows; appropriate wall support required for mounting bracket
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | shared between multiple bays
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1 | may be located on left or right side of bedhead depending on monitor functionality and staff workflows; appropriate wall support required
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FIHR-068 | BRACKET: for alcohol based hand rub, attached to bed | 1 | may be wall mounted depending on bedhead arrangment
PT-RS1 | Patient Bay - Recovery, Stage 1 | FFE | FIRT-047 | TRACK: curtain, privacy, U shaped | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to patient monitor
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | LIFX-032 | LIGHT: downlight, examination, ceiling mounted | 1 | articulated examination light is also acceptable
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, with indicator button and light
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel, for examination downlight
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 2
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, with indicator button and light
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ELGP-208 | GPO: double, wall mounted | 1 | low, for patient bed and pressure mattress
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | to patient monitor
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | quantity to suit service requirements
PT-RS1 | Patient Bay - Recovery, Stage 1 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 7 | type and quantity to suit service requirements
PTRY | Pantry | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PTRY | Pantry | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
PTRY | Pantry | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | floor finish must be minimum slip rating R10/pendulum P3 or agreed equivalent
PTRY | Pantry | FA | WLWA-007 | WALL FINISH: splashback | 4 | to bench with sink, to basin
PTRY | Pantry | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PTRY | Pantry | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
PTRY | Pantry | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | with hold open device to support trolley movement as required
PTRY | Pantry | FA | CLCN-009 | CORNICE: wall trim fixing | 1
PTRY | Pantry | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
PTRY | Pantry | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 1
PTRY | Pantry | FFE | FIJO-156 | CUPBOARD: wall mount, single door, adj shelves | 1
PTRY | Pantry | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
PTRY | Pantry | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
PTRY | Pantry | FFE | FIDI-025 | DISPENSER: paper/hand towel | 2 | 1 to basin, 1 to sink
PTRY | Pantry | FFE | FIDI-030 | DISPENSER: soap | 2 | 1 to basin, 1 to sink
PTRY | Pantry | FFE | FIJO-104 | CUPBOARD: drawer unit, 3 equal | 1
PTRY | Pantry | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | size, type and quantity of bins dependent on local waste management policies
PTRY | Pantry | FFE | HYBA-011 | BASIN: handwash, Type C | 1
PTRY | Pantry | FFE | HYGE-003 | BOILING/CHILLED WATER UNIT: Combination | 1 | ensure adequate ventilation in joinery
PTRY | Pantry | FFE | HYTP-029 | TAPWARE: boiling/chilled water unit (comb) | 1 | instant hot/cold water tap to sink; high/gooseneck tap may be required where large kettles are to be filled for tea service
PTRY | Pantry | FFE | HYBA-069 | SINK: single, with drainer, 930mmL | 1
PTRY | Pantry | FFE | FQCA-015 | DISPENSER: ice, potable | 1 | optional; item to comply with infection control requirements
PTRY | Pantry | FFE | FQCA-067 | OVEN: microwave, domestic | 1
PTRY | Pantry | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
PTRY | Pantry | FFE | FQCA-027 | FRIDGE: commercial, floor standing, single door | 1 | Clear area for fridge to allow for adequate ventilation and full opening of door. May be connected to BMS for temperature monitoring depending on service requirements,
PTRY | Pantry | FFE | FIJO-069 | BENCH TOP: 750D, joinery under, laminate finish | 1 | minimum depth 600mm; where an ice machine is provided the depth may need to increase to accommodate appliance
PTRY | Pantry | FFE | FIJO-163 | CUPBOARD: tall, single microwave | 1
PTRY | Pantry | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead is also acceptable
PTRY | Pantry | FFE | FQCW-062 | BIN: waste, recycling, comingled, 50L | 1 | size, type and quantity of bins dependent on local waste management policies
PTRY | Pantry | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional, to fridge, for temperature monitoring as required
PTRY | Pantry | SE | HYTP-008 | OUTLET: cold water | 1 | to boiling/ chilled water unit
PTRY | Pantry | SE | ELBO-015 | SWITCH: light, single | 1
PTRY | Pantry | SE | ELGP-109 | GPO: single, wall mounted | 3 | 1 to fridge, 1 to microwave, 1 to boiling/ chilled water unit
PTRY | Pantry | SE | ELGP-208 | GPO: double, wall mounted | 2 | over bench
PTRY | Pantry | SE | ITSE-038 | READER: access control, general | 1 | optional, dependent on security requirements and location of room
REC-E | Reception, Emergency | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
REC-E | Reception, Emergency | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 11
REC-E | Reception, Emergency | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
REC-E | Reception, Emergency | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
REC-E | Reception, Emergency | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
REC-E | Reception, Emergency | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 2
REC-E | Reception, Emergency | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 2 | to waiting area
REC-E | Reception, Emergency | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional, to triage room
REC-E | Reception, Emergency | FA | DWOB-016 | OBSERVATION: internal window, alum/safety glass, one way, powdercoat | 2 | optional
REC-E | Reception, Emergency | FA | CLCN-009 | CORNICE: wall trim fixing | 1
REC-E | Reception, Emergency | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
REC-E | Reception, Emergency | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
REC-E | Reception, Emergency | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
REC-E | Reception, Emergency | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
REC-E | Reception, Emergency | FFE | FIJO-131 | CUPBOARD: tall, single door, adj shelves, lockable | 1
REC-E | Reception, Emergency | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 1
REC-E | Reception, Emergency | FFE | FIJO-102 | CUPBOARD: drawer unit | 1
REC-E | Reception, Emergency | FFE | FQCW-016 | BIN: waste, general, 20L | 1
REC-E | Reception, Emergency | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 4
REC-E | Reception, Emergency | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 3
REC-E | Reception, Emergency | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 1 | above upstand of benches
REC-E | Reception, Emergency | FFE | FQSN-062 | SAFE: small | 1
REC-E | Reception, Emergency | FFE | MMBE-045 | WHEELCHAIR | 1
REC-E | Reception, Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
REC-E | Reception, Emergency | FFE | ITBU-013 | DISPLAY SCREEN: patient flow system | 1
REC-E | Reception, Emergency | FFE | FQGE-037 | MACHINE: cash register | 1
REC-E | Reception, Emergency | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 3
REC-E | Reception, Emergency | FFE | FQGE-038 | MACHINE: electronic funds transfer at point of sale (EFTPOS) | 1
REC-E | Reception, Emergency | FFE | ITSE-048 | DISPLAY SCREEN: CCTV system | 1 | observe amulance bay and other zones as required
REC-E | Reception, Emergency | FFE | FQGE-056 | PRINTER: desktop, labels | 2
REC-E | Reception, Emergency | FFE | ITNE-049 | TELEPHONE: handset, desktop | 3
REC-E | Reception, Emergency | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 3 | behind reception desk, open under part
REC-E | Reception, Emergency | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1 | to waiting area speaker
REC-E | Reception, Emergency | FFE | ITNE-021 | MULTIFUNCTION DEVICE: floorstanding | 1
REC-E | Reception, Emergency | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 3
REC-E | Reception, Emergency | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 3
REC-E | Reception, Emergency | FFE | FIJO-185 | JOINERY UNIT: counter top and screen under, emergency reception | 2
REC-E | Reception, Emergency | FFE | FIJO-186 | JOINERY UNIT: counter top and screen under, accessible, emergency reception | 1
REC-E | Reception, Emergency | FFE | WLPT-012 | SCREEN: security, safety glass, with communication slot | 3 | optional, subject to a risk assessment to determine whether required
REC-E | Reception, Emergency | FFE | FIJO-212 | BULKHEAD: joinery | 1
REC-E | Reception, Emergency | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1 | for CCTV
REC-E | Reception, Emergency | FFE | FIJO-216 | CUPBOARD: pigeon holes, under bench | 2
REC-E | Reception, Emergency | FFE | FIGE-010 | PASSTHROUGH: to bench | 3
REC-E | Reception, Emergency | FFE | WLPT-014 | SCREEN: acoustic, privacy, safety glass | 4 | optional, subject to a risk assessment to determine whether required
REC-E | Reception, Emergency | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 5
REC-E | Reception, Emergency | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | to workstation bench, 1 outet on each panel for telephone
REC-E | Reception, Emergency | SE | ELBO-015 | SWITCH: light, single | 2
REC-E | Reception, Emergency | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 5
REC-E | Reception, Emergency | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 5
REC-E | Reception, Emergency | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
REC-E | Reception, Emergency | SE | ITSE-006 | BUTTON: duress, fixed | 3 | to workstation bench
REC-E | Reception, Emergency | SE | ITSE-038 | READER: access control, general | 2
REC-E | Reception, Emergency | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 3 | to each work station
REC-E | Reception, Emergency | SE | ITSE-028 | INTERCOM: audiovisual, wall mounted | 1 | to ambulance bay and ED entry as required
REC-E | Reception, Emergency | SE | ITIN-029 | OUTLET: data, double RJ45, desk box | 3
REC-E | Reception, Emergency | SE | ELGP-224 | GPO: emergency power, double, desk box | 6
REC-E | Reception, Emergency | SE | ELBO-018 | BUTTON: security, perimeter lockdown | 1 | optional
REC-E | Reception, Emergency | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 3
RECP-10 | Reception, 10m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | carpet tiles are also acceptable
RECP-10 | Reception, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 18
RECP-10 | Reception, 10m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
RECP-10 | Reception, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
RECP-10 | Reception, 10m2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 3
RECP-10 | Reception, 10m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
RECP-10 | Reception, 10m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
RECP-10 | Reception, 10m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
RECP-10 | Reception, 10m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
RECP-10 | Reception, 10m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
RECP-10 | Reception, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
RECP-10 | Reception, 10m2 | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1
RECP-10 | Reception, 10m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1
RECP-10 | Reception, 10m2 | FFE | FIJO-182 | JOINERY UNIT: reception desk | 1
RECP-10 | Reception, 10m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
RECP-10 | Reception, 10m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | dual screens may be provided to suit service requirements
RECP-10 | Reception, 10m2 | FFE | ITNE-023 | PRINTER: networked | 1 | optional
RECP-10 | Reception, 10m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
RECP-10 | Reception, 10m2 | FFE | FIJO-051 | BENCH TOP: 450D, joinery under | 1
RECP-10 | Reception, 10m2 | FFE | FIJO-099 | CAC: cable access cap | 1
RECP-10 | Reception, 10m2 | FFE | WLPT-014 | SCREEN: acoustic, privacy, safety glass | 3 | optional
RECP-10 | Reception, 10m2 | FFE | WLPT-015 | SCREEN: security, safety glass, with communication slot and pass through | 2 | optional
RECP-10 | Reception, 10m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
RECP-10 | Reception, 10m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | location of outlets to meet local operational/WHS requirements
RECP-10 | Reception, 10m2 | SE | ELBO-003 | CONTROL PANEL: lighting | 1 | optional
RECP-10 | Reception, 10m2 | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | optional
RECP-10 | Reception, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
RECP-10 | Reception, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 3 | 1 x for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
RECP-10 | Reception, 10m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | extent of emergency power to be determined based on service requirements, location of outlets to meet local operational/WHS requirements
RECP-10 | Reception, 10m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1
RECP-10 | Reception, 10m2 | SE | ITSE-038 | READER: access control, general | 1 | optional
RECP-10 | Reception, 10m2 | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1 | optional, to external entry and/or unit entry as required
RECP-15 | Reception, 15m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | carpet tiles are also acceptable
RECP-15 | Reception, 15m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 18
RECP-15 | Reception, 15m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
RECP-15 | Reception, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
RECP-15 | Reception, 15m2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 3
RECP-15 | Reception, 15m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
RECP-15 | Reception, 15m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
RECP-15 | Reception, 15m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
RECP-15 | Reception, 15m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
RECP-15 | Reception, 15m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2
RECP-15 | Reception, 15m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
RECP-15 | Reception, 15m2 | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 2
RECP-15 | Reception, 15m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 2
RECP-15 | Reception, 15m2 | FFE | FIJO-182 | JOINERY UNIT: reception desk | 1
RECP-15 | Reception, 15m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
RECP-15 | Reception, 15m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2 | dual screens may be provided to suit service requirements
RECP-15 | Reception, 15m2 | FFE | ITNE-023 | PRINTER: networked | 1 | optional
RECP-15 | Reception, 15m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
RECP-15 | Reception, 15m2 | FFE | FIJO-051 | BENCH TOP: 450D, joinery under | 1
RECP-15 | Reception, 15m2 | FFE | FIJO-099 | CAC: cable access cap | 2
RECP-15 | Reception, 15m2 | FFE | WLPT-014 | SCREEN: acoustic, privacy, safety glass | 3 | optional
RECP-15 | Reception, 15m2 | FFE | WLPT-015 | SCREEN: security, safety glass, with communication slot and pass through | 3 | optional
RECP-15 | Reception, 15m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
RECP-15 | Reception, 15m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | location of outlets to meet local operational/WHS requirements
RECP-15 | Reception, 15m2 | SE | ELBO-003 | CONTROL PANEL: lighting | 1 | optional
RECP-15 | Reception, 15m2 | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | optional
RECP-15 | Reception, 15m2 | SE | ELBO-015 | SWITCH: light, single | 1
RECP-15 | Reception, 15m2 | SE | ELGP-208 | GPO: double, wall mounted | 5 | 2 x for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
RECP-15 | Reception, 15m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | extent of emergency power to be determined based on service requirements, location of outlets to meet local operational/WHS requirements
RECP-15 | Reception, 15m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1
RECP-15 | Reception, 15m2 | SE | ITSE-038 | READER: access control, general | 1 | optional
RECP-15 | Reception, 15m2 | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1 | optional, to external entry and/or unit entry as required
RECP-20 | Reception, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | carpet tiles are also acceptable
RECP-20 | Reception, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 18
RECP-20 | Reception, 20m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
RECP-20 | Reception, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
RECP-20 | Reception, 20m2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 3
RECP-20 | Reception, 20m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
RECP-20 | Reception, 20m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
RECP-20 | Reception, 20m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
RECP-20 | Reception, 20m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 3
RECP-20 | Reception, 20m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2
RECP-20 | Reception, 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 2
RECP-20 | Reception, 20m2 | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 2
RECP-20 | Reception, 20m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 2
RECP-20 | Reception, 20m2 | FFE | FIJO-182 | JOINERY UNIT: reception desk | 1
RECP-20 | Reception, 20m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
RECP-20 | Reception, 20m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 3 | dual screens may be provided to suit service requirements
RECP-20 | Reception, 20m2 | FFE | ITNE-023 | PRINTER: networked | 1 | optional
RECP-20 | Reception, 20m2 | FFE | FQGE-056 | PRINTER: desktop, labels | 1 | optional
RECP-20 | Reception, 20m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 3
RECP-20 | Reception, 20m2 | FFE | FIJO-051 | BENCH TOP: 450D, joinery under | 1
RECP-20 | Reception, 20m2 | FFE | FIJO-099 | CAC: cable access cap | 3
RECP-20 | Reception, 20m2 | FFE | WLPT-014 | SCREEN: acoustic, privacy, safety glass | 3 | optional
RECP-20 | Reception, 20m2 | FFE | WLPT-015 | SCREEN: security, safety glass, with communication slot and pass through | 4 | optional
RECP-20 | Reception, 20m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional for label printer
RECP-20 | Reception, 20m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
RECP-20 | Reception, 20m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 3 | location of outlets to meet local operational/WHS requirements
RECP-20 | Reception, 20m2 | SE | ELBO-003 | CONTROL PANEL: lighting | 1 | optional
RECP-20 | Reception, 20m2 | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | optional
RECP-20 | Reception, 20m2 | SE | ELBO-015 | SWITCH: light, single | 1
RECP-20 | Reception, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 8 | 3 x for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements, 1 x optional for label printer
RECP-20 | Reception, 20m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3 | extent of emergency power to be determined based on service requirements, location of outlets to meet local operational/WHS requirements
RECP-20 | Reception, 20m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1
RECP-20 | Reception, 20m2 | SE | ITSE-038 | READER: access control, general | 1 | optional
RECP-20 | Reception, 20m2 | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1 | optional, to external entry and/or unit entry as required
REPR | Reporting Room | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
REPR | Reporting Room | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 5 | or floor vinyl coved skirting
REPR | Reporting Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
REPR | Reporting Room | FA | WLWA-001 | WALL FINISH: acoustic panels, prefinished | 3
REPR | Reporting Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1 | both sides
REPR | Reporting Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
REPR | Reporting Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
REPR | Reporting Room | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1
REPR | Reporting Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
REPR | Reporting Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 3 | 1 per workstation
REPR | Reporting Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
REPR | Reporting Room | FFE | FQCW-016 | BIN: waste, general, 20L | 2
REPR | Reporting Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
REPR | Reporting Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
REPR | Reporting Room | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 4 | RIS/PMS monitor per workstation
REPR | Reporting Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
REPR | Reporting Room | FFE | MMGE-152 | VIEWER: X-ray, 2 screen | 2 | 1 per workstation
REPR | Reporting Room | FFE | FIJO-099 | CAC: cable access cap | 2
REPR | Reporting Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
REPR | Reporting Room | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 2 | optional, for wall mounted display screen, 1 per workstation
REPR | Reporting Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 2
REPR | Reporting Room | FFE | FIHR-070 | BRACKET: for display screen, dual, desk mounted | 4
REPR | Reporting Room | FFE | FQDW-043 | PARTITION: workstation system, acoustic | 1
REPR | Reporting Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 2
REPR | Reporting Room | FFE | FQDW-044 | WORKSTATION: straight, adj height, 1800W x 800D x 750H nom. | 2 | adjustable sit to standing height workstation optional
REPR | Reporting Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 2
REPR | Reporting Room | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 4
REPR | Reporting Room | FFE | ITNE-070 | DISPLAY SCREEN: PACS | 2 | optional, wall mounted for viewing by teams, 1 per workstation
REPR | Reporting Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 2 to each workstation for deskbox soft wired deskbox connection
REPR | Reporting Room | SE | LIFX-011 | LIGHT: reading light | 2 | 1 per w/s - task light
REPR | Reporting Room | SE | ELGP-109 | GPO: single, wall mounted | 2 | 1 to each workstation for deskbox soft wired deskbox connection
REPR | Reporting Room | SE | ELGP-109 | GPO: single, wall mounted | 2 | optional, for use with wall mounted display screen, 1 per workstation
REPR | Reporting Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | to bench, x-ray viewer
REPR | Reporting Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
REPR | Reporting Room | SE | ELBO-012 | SWITCH: light, dimmer | 3 | to room
REPR | Reporting Room | SE | ITIN-066 | OUTLET: HDMI, wall mounted | 2 | 1 to each workstation for deskbox soft wired deskbox connection
REPR | Reporting Room | SE | ITIN-066 | OUTLET: HDMI, wall mounted | 2 | optional, for use with wall mounted display screen, 1 per workstation
REPR | Reporting Room | SE | ITIN-029 | OUTLET: data, double RJ45, desk box | 4
REPR | Reporting Room | SE | ITIN-067 | OUTLET: HDMI, desk box | 2 | optional, 1 per workstation
REPR | Reporting Room | SE | ELGP-212 | GPO: double, desk box | 8
REPR | Reporting Room | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 2
REPW | Reporting Workstation | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
REPW | Reporting Workstation | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 1 | or floor vinyl coved skirting
REPW | Reporting Workstation | FA | WLWA-001 | WALL FINISH: acoustic panels, prefinished | 1 | to long edge of w/s where it abuts a wall
REPW | Reporting Workstation | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
REPW | Reporting Workstation | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
REPW | Reporting Workstation | FA | CLCN-009 | CORNICE: wall trim fixing | 1
REPW | Reporting Workstation | FFE | FQBS-018 | CHAIR: office, ergonomic | 2 | optional, 1 per w/s with a 2nd per w/s
REPW | Reporting Workstation | FFE | FQCW-016 | BIN: waste, general, 20L | 1
REPW | Reporting Workstation | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 | optional, for ceiling mounted display screen
REPW | Reporting Workstation | FFE | ITNE-063 | DISPLAY SCREEN: for computer | 2 | RIS/PMS monitor per w/s
REPW | Reporting Workstation | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
REPW | Reporting Workstation | FFE | FIJO-099 | CAC: cable access cap | 1
REPW | Reporting Workstation | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
REPW | Reporting Workstation | FFE | FIHR-070 | BRACKET: for display screen, dual, desk mounted | 2
REPW | Reporting Workstation | FFE | FQDW-043 | PARTITION: workstation system, acoustic | 2
REPW | Reporting Workstation | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 1
REPW | Reporting Workstation | FFE | FQDW-044 | WORKSTATION: straight, adj height, 1800W x 800D x 750H nom. | 1 | adjustable sit to standing height workstation optional
REPW | Reporting Workstation | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
REPW | Reporting Workstation | FFE | ITNE-069 | DISPLAY SCREEN: PACS, portrait | 2
REPW | Reporting Workstation | FFE | ITNE-070 | DISPLAY SCREEN: PACS | 1 | optional, ceiling mounted, for viewing by teams
REPW | Reporting Workstation | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | for deskbox soft wired deskbox connection
REPW | Reporting Workstation | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | optional, for use with optional large format ceiling mounted display screen, 1 per w/s
REPW | Reporting Workstation | SE | LIFX-011 | LIGHT: reading light | 1
REPW | Reporting Workstation | SE | ELGP-109 | GPO: single, wall mounted | 1 | for deskbox soft wired deskbox connection
REPW | Reporting Workstation | SE | ELBO-012 | SWITCH: light, dimmer | 1
REPW | Reporting Workstation | SE | ITIN-061 | OUTLET: HDMI, ceiling mounted | 1 | optional, for use with optional large format ceiling mounted display screen, 1 per w/s
REPW | Reporting Workstation | SE | ITIN-066 | OUTLET: HDMI, wall mounted | 1 | optional, for deskbox soft wired deskbox connection
REPW | Reporting Workstation | SE | ITIN-029 | OUTLET: data, double RJ45, desk box | 2
REPW | Reporting Workstation | SE | ITIN-067 | OUTLET: HDMI, desk box | 1 | optional
REPW | Reporting Workstation | SE | ELGP-212 | GPO: double, desk box | 4
REPW | Reporting Workstation | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 1
SECL | Seclusion Room | FA | FLVY-002 | FLOOR FINISH: vinyl, seamless, coved, cushioned | 1 | Secure fixings with acoustic underlay.
SECL | Seclusion Room | FA | WLWA-005 | WALL FINISH: paint, scrub resistant | 1 | Walls to be robust and not able to be penetrated.
SECL | Seclusion Room | FA | CLFS-005 | CEILING: plasterboard, flush set, suspended, paint, scrub resistant | 1 | Min. 3000mm height, impact resistant & sealed, robust and not able to be penetrated, consider plywood or equivalent backing to ceiling finish for high dependency and intensive care areas.
SECL | Seclusion Room | FA | DWWH-005 | WINDOW | 1 | External windows double glazed Grade A safety glass with integral venetians.
SECL | Seclusion Room | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1 | Grade A safety glass, controls outside room.
SECL | Seclusion Room | FA | DWGL-075 | DOOR: 1270mm c/o, single leaf, observation panel, solid core/safety glass, paint | 1 | 50mm solid core door; outward opening, 180 deg swing. Anti ligature hardware; locks to be provided at top bottom and centre of door; key cylinder to centre lock to both sides of door and flush to inside face of door; snibs to top and bottom locks to outside face of door only. Speech to be audible through door, alternatively intercom to be provided. Security-grade noggings will be required to support weight of door and resist attempts to force the door.
SECL | Seclusion Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
SECL | Seclusion Room | FA | FLSK-011 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished, anti ligature | 1 | Seamless painted bullnose timber capping to match wall function, to terminate/ secure coved vinyl skirting at approx. 40mm off the finished floor level for cleaning purposes, fully glued and screw fixed at 100mm intervals.
SECL | Seclusion Room | FFE | DWWD-007 | BLIND: venetian, integral | 3 | To window, observation panel, controls outside room.
SECL | Seclusion Room | FFE | FIBM-004 | MIRROR: fixed, convex, tamper proof, anti ligature | 1 | Securely fixed within a frame and infilled.
SECL | Seclusion Room | FFE | FQBS-047 | MATTRESS: foam | 1 | On floor.
SECL | Seclusion Room | SE | DWWD-010 | CONTROL: venetian blind, remote | 2 | Outside room, for remote control of blinds to external windows.
SECL | Seclusion Room | SE | FSDE-004 | DETECTOR: smoke | 1
SECL | Seclusion Room | SE | ELBO-015 | SWITCH: light, single | 2 | Outside room, lighting to have controlled switching to create low stimulus environment.
SECL | Seclusion Room | SE | ELGP-208 | GPO: double, wall mounted | 1 | Outside room, close to entrance door for mechanical emergency equipment. RCD protected as part of patient areas.
SECL | Seclusion Room | SE | ITSE-006 | BUTTON: duress, fixed | 1 | Optional; outside room. Mobile duress preferred.
SECL | Seclusion Room | SE | LIFX-034 | LIGHT: reading light, tamper proof, anti ligature, ceiling recessed | 1
SECR | Security Observation Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
SECR | Security Observation Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
SECR | Security Observation Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
SECR | Security Observation Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
SECR | Security Observation Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
SECR | Security Observation Room | FA | DWWH-005 | WINDOW | 1 | optional, provide as required for surveillance of external areas
SECR | Security Observation Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable, with secure staff-only access
SECR | Security Observation Room | FA | DWOB-016 | OBSERVATION: internal window, alum/safety glass, one way, powdercoat | 1
SECR | Security Observation Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
SECR | Security Observation Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
SECR | Security Observation Room | FFE | DWWD-004 | BLIND: roller | 1 | optional, to external window if provided
SECR | Security Observation Room | FFE | FQSN-061 | SAFE: medium | 1 | for securing lost items of value as required
SECR | Security Observation Room | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 1
SECR | Security Observation Room | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 3
SECR | Security Observation Room | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
SECR | Security Observation Room | FFE | FQSN-060 | SAFE: guns | 1 | optional, for securing contraband and weapons, provision in alignment with operational policies and jurisdictional requirements; may be floor mounted.
SECR | Security Observation Room | FFE | DWWH-002 | HATCH: pass-through | 1 | sliding window for reception
SECR | Security Observation Room | FFE | ITSE-019 | CAMERA: identification photo | 1 | optional, for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | FFE | FQGE-003 | CHARGER: battery | 1 | for radios, cameras and other devices as required
SECR | Security Observation Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2
SECR | Security Observation Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | optional, for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | FFE | ITSE-048 | DISPLAY SCREEN: CCTV system | 1 | type and quantity to meet security requirements for CCTV camera feed observation
SECR | Security Observation Room | FFE | ITNE-023 | PRINTER: networked | 1
SECR | Security Observation Room | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 2 | 1 to each computer workstation
SECR | Security Observation Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
SECR | Security Observation Room | FFE | ITSE-010 | CABINET: key management, electronic | 1 | optional
SECR | Security Observation Room | FFE | ITNE-022 | PRINTER: identification / access control card | 1 | optional, for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 1
SECR | Security Observation Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead is also acceptable
SECR | Security Observation Room | FFE | FIHR-080 | BRACKET: for bench, 750D, wall mounted | 2
SECR | Security Observation Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional, to PC for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 to each workstation, 1 to bench with printers
SECR | Security Observation Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to CCTV display screen; quantity to meet security requirements
SECR | Security Observation Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 6 | 2 to each workstation, 2 to bench with printers
SECR | Security Observation Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | optional, to PC for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | to CCTV display screen; quantity to meet security requirements
SECR | Security Observation Room | SE | ITSE-006 | BUTTON: duress, fixed | 1 | mounted under bench; may be wall mounted
SECR | Security Observation Room | SE | ITSE-038 | READER: access control, general | 1
SECR | Security Observation Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
SHAC | Shower - Accessible | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
SHAC | Shower - Accessible | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
SHAC | Shower - Accessible | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
SHAC | Shower - Accessible | FA | WLWA-019 | WALL FINISH: vinyl, full height | 6 | tiles are also acceptable
SHAC | Shower - Accessible | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | water resistant ceiling tiles are also acceptable
SHAC | Shower - Accessible | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | with privacy latch and emergency release
SHAC | Shower - Accessible | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
SHAC | Shower - Accessible | FFE | MMGE-024 | CHAIR: shower | 1
SHAC | Shower - Accessible | FFE | FIHR-026 | HOOK: coat | 2
SHAC | Shower - Accessible | FFE | FIRT-033 | TRACK: curtain, shower | 1 | optional, refer to local infection control policy
SHAC | Shower - Accessible | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, refer to local infection control policy
SHAC | Shower - Accessible | FFE | FIJO-194 | SHELF: laminate | 1
SHAC | Shower - Accessible | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 | or soap dispenser
SHAC | Shower - Accessible | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
SHAC | Shower - Accessible | FFE | HYTP-045 | SHOWER: hand-held, accessible | 1
SHAC | Shower - Accessible | FFE | FIRT-045 | GRAB RAIL: shower, horizontal and vertical | 1
SHAC | Shower - Accessible | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | optional, IPX4 rating required
SHAC | Shower - Accessible | SE | HYDR-004 | DRAIN: floor waste | 1
SHAC | Shower - Accessible | SE | ELBO-015 | SWITCH: light, single | 1
SHAC | Shower - Accessible | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | optional, IPX4 rating required
SHAC | Shower - Accessible | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | optional, IPX4 rating required
SHPT | Shower - Patient | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
SHPT | Shower - Patient | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
SHPT | Shower - Patient | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
SHPT | Shower - Patient | FA | WLWA-019 | WALL FINISH: vinyl, full height | 6 | tiles are also acceptable
SHPT | Shower - Patient | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | water resistant ceiling tiles are also acceptable
SHPT | Shower - Patient | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | with privacy latch and emergency release
SHPT | Shower - Patient | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
SHPT | Shower - Patient | FFE | MMGE-024 | CHAIR: shower | 1 | or commode chair, optional
SHPT | Shower - Patient | FFE | FIHR-026 | HOOK: coat | 2
SHPT | Shower - Patient | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | optional, refer to local infection control policy
SHPT | Shower - Patient | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, refer to local infection control policy
SHPT | Shower - Patient | FFE | FQCW-016 | BIN: waste, general, 20L | 1
SHPT | Shower - Patient | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
SHPT | Shower - Patient | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
SHPT | Shower - Patient | FFE | FIBM-006 | MIRROR: fixed, glass | 1
SHPT | Shower - Patient | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 | or soap dispenser
SHPT | Shower - Patient | FFE | FIRT-016 | RAIL: towel | 1 | with grab rail strength/fixings
SHPT | Shower - Patient | FFE | HYBA-011 | BASIN: handwash, Type C | 1
SHPT | Shower - Patient | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
SHPT | Shower - Patient | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
SHPT | Shower - Patient | FFE | HYTP-020 | SHOWER: hand-held | 1
SHPT | Shower - Patient | FFE | FIRT-045 | GRAB RAIL: shower, horizontal and vertical | 1
SHPT | Shower - Patient | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | IPX4 rating required
SHPT | Shower - Patient | SE | HYDR-004 | DRAIN: floor waste | 1
SHPT | Shower - Patient | SE | ELBO-015 | SWITCH: light, single | 1 | IPX4 rating required
SHPT | Shower - Patient | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | IPX4 rating required
SHPT | Shower - Patient | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | IPX4 rating required
SHPT | Shower - Patient | SE | ELGP-208 | GPO: double, wall mounted | 1 | optional, to be classified as a shaver outlet or installed within a cupboard if provided
SHST | Shower - Staff | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
SHST | Shower - Staff | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
SHST | Shower - Staff | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
SHST | Shower - Staff | FA | WLWA-019 | WALL FINISH: vinyl, full height | 6 | tiles are also acceptable
SHST | Shower - Staff | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | water resistant ceiling tiles are also acceptable
SHST | Shower - Staff | FA | DWSC-001 | DOOR: 850mm c/o, single leaf, solid core, paint | 1 | with privacy latch
SHST | Shower - Staff | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
SHST | Shower - Staff | FFE | FIGE-003 | BENCH SEAT: fixed, indoor | 1 | material to be suitable for wet areas
SHST | Shower - Staff | FFE | FIHR-026 | HOOK: coat | 1
SHST | Shower - Staff | FFE | FIRT-033 | TRACK: curtain, shower | 1 | optional, refer to local infection control policy
SHST | Shower - Staff | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, refer to local infection control policy
SHST | Shower - Staff | FFE | FIDI-030 | DISPENSER: soap | 1
SHST | Shower - Staff | FFE | FIBM-006 | MIRROR: fixed, glass | 1
SHST | Shower - Staff | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 | optional
SHST | Shower - Staff | FFE | FIRT-016 | RAIL: towel | 1
SHST | Shower - Staff | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1
SHST | Shower - Staff | FFE | HYTP-018 | SHOWER: fixed rose | 1
SHST | Shower - Staff | SE | HYDR-004 | DRAIN: floor waste | 1
SHST | Shower - Staff | SE | ELBO-015 | SWITCH: light, single | 1
SHST | Shower - Staff | SE | ITSE-038 | READER: access control, general | 1 | optional
SPECT-CT | SPECT-CT Imaging Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
SPECT-CT | SPECT-CT Imaging Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 11
SPECT-CT | SPECT-CT Imaging Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
SPECT-CT | SPECT-CT Imaging Room | FA | WLWA-007 | WALL FINISH: splashback | 2
SPECT-CT | SPECT-CT Imaging Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
SPECT-CT | SPECT-CT Imaging Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 7
SPECT-CT | SPECT-CT Imaging Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
SPECT-CT | SPECT-CT Imaging Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | optional, patient observation by camera may be considered, glazing to be AS1428 compliant safety glass
SPECT-CT | SPECT-CT Imaging Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
SPECT-CT | SPECT-CT Imaging Room | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
SPECT-CT | SPECT-CT Imaging Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MGFP-002 | FLOWMETER: medical air | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | FIHR-019 | BRACKET: for suction bottle | 2
SPECT-CT | SPECT-CT Imaging Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 2
SPECT-CT | SPECT-CT Imaging Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
SPECT-CT | SPECT-CT Imaging Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | near door
SPECT-CT | SPECT-CT Imaging Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
SPECT-CT | SPECT-CT Imaging Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
SPECT-CT | SPECT-CT Imaging Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
SPECT-CT | SPECT-CT Imaging Room | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMGE-045 | IV STAND: mobile | 1 | optional
SPECT-CT | SPECT-CT Imaging Room | FFE | MGFP-004 | FLOWMETER: oxygen | 2
SPECT-CT | SPECT-CT Imaging Room | FFE | MMBE-042 | SLIDE: patient | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMGE-139 | TROLLEY: procedure | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMGE-002 | ADAPTER: suction | 2
SPECT-CT | SPECT-CT Imaging Room | FFE | MMGE-100 | SUCTION BOTTLE | 2
SPECT-CT | SPECT-CT Imaging Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-262 | DEVICE: nuclear medicine, SPECT/CT | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | ITCL-012 | CAMERA: observation | 2
SPECT-CT | SPECT-CT Imaging Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-264 | CART: collimator, SPECT/CT | 4 | required quantity dependent on patient mix
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-265 | BOARD: distribution, mains, SPECT/CT | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-263 | BOX: line connection, SPECT/CT | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-100 | INJECTOR: contrast, CT | 1 | optional, floor or ceiling mounted to be confirmed
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-272 | BOARD: disconnect, mains, SPECT/CT | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-273 | PHANTOM: SPECT/CT | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | MMMI-377 | WARMER: contrast | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | FIHR-078 | BRACKET: for observation camera, wall mounted | 2
SPECT-CT | SPECT-CT Imaging Room | FFE | MMGE-179 | MACHINE: electrocardiography (ECG), c/w trolley and printer shelf | 1 | procured with SPECT/CT system vendor
SPECT-CT | SPECT-CT Imaging Room | FFE | MMHA-032 | MONITOR: patient, cardiac, SPECT/CT | 1
SPECT-CT | SPECT-CT Imaging Room | FFE | FQCW-066 | BIN: waste, sharps, on benchtop, shielded | 1
SPECT-CT | SPECT-CT Imaging Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
SPECT-CT | SPECT-CT Imaging Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | on wall near SPECT/CT unit
SPECT-CT | SPECT-CT Imaging Room | SE | ELPR-006 | RCD: residual current device | 1 | on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | auto on when modality is in use
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light
SPECT-CT | SPECT-CT Imaging Room | SE | ELGP-109 | GPO: single, wall mounted | 2 | clock
SPECT-CT | SPECT-CT Imaging Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 5 | to walls
SPECT-CT | SPECT-CT Imaging Room | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 2
SPECT-CT | SPECT-CT Imaging Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
SPECT-CT | SPECT-CT Imaging Room | SE | ELGT-007 | UPS: uninterruptable power supply unit | 1 | optional, dependent on vendor requirements
SPECT-CT | SPECT-CT Imaging Room | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
SPECT-CT | SPECT-CT Imaging Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | patient services
SPECT-CT | SPECT-CT Imaging Room | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors extent as specified by radiation consultant
SPECT-CT | SPECT-CT Imaging Room | SE | ELBO-012 | SWITCH: light, dimmer | 1 | number determined by number of doors
SPECT-CT | SPECT-CT Imaging Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
SPECT-CT | SPECT-CT Imaging Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
SPECT-CT | SPECT-CT Imaging Room | SE | ELPR-007 | UPS: status indicator | 1
SPECT-CT | SPECT-CT Imaging Room | SE | LIFX-038 | LIGHT: backlit feature panels | 2
SPECT-CTCR | SPECT-CT Control Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
SPECT-CTCR | SPECT-CT Control Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
SPECT-CTCR | SPECT-CT Control Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
SPECT-CTCR | SPECT-CT Control Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
SPECT-CTCR | SPECT-CT Control Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
SPECT-CTCR | SPECT-CT Control Room | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | safety glass
SPECT-CTCR | SPECT-CT Control Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
SPECT-CTCR | SPECT-CT Control Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
SPECT-CTCR | SPECT-CT Control Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
SPECT-CTCR | SPECT-CT Control Room | FFE | DWWD-004 | BLIND: roller | 1 | to observation window for patient privacy
SPECT-CTCR | SPECT-CT Control Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-044 | RACK: lead apron | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1 | optional
SPECT-CTCR | SPECT-CT Control Room | FFE | FQGE-056 | PRINTER: desktop, labels | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITAV-057 | SPEAKER: ceiling recessed | 1 | communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1 | communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 2
SPECT-CTCR | SPECT-CT Control Room | FFE | MMMI-269 | COMPUTER: tower, acquisition, SPECT/CT | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | MMMI-274 | CONSOLE: control, SPECT/CT | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | MMMI-369 | DISPLAY SCREEN: contrast injector | 1 | optional
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-070 | BRACKET: for display screen, dual, desk mounted | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 2
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | ITNE-070 | DISPLAY SCREEN: PACS | 2
SPECT-CTCR | SPECT-CT Control Room | FFE | FQDW-054 | WORKSTATION: straight, adj height, 1600W x 750D x 750H nom. | 1
SPECT-CTCR | SPECT-CT Control Room | FFE | FQGE-094 | SCANNER: desktop, document, upright | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 outlet for display screen, patient monitor slave; one outlet for telephone
SPECT-CTCR | SPECT-CT Control Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4
SPECT-CTCR | SPECT-CT Control Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ELBO-001 | BUTTON: emergency stop | 1 | mains power, consult manufacturer for safety and compatibility with equipment.
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-135 | GPO: UPS, single, wall mounted | 5
SPECT-CTCR | SPECT-CT Control Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | auto on when modality is in use
SPECT-CTCR | SPECT-CT Control Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-208 | GPO: double, wall mounted | 1 | one for printer
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 4
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
SPECT-CTCR | SPECT-CT Control Room | SE | ELBO-012 | SWITCH: light, dimmer | 2
SRM-15 | Staff Room, 15m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent around sink
SRM-15 | Staff Room, 15m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9
SRM-15 | Staff Room, 15m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
SRM-15 | Staff Room, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
SRM-15 | Staff Room, 15m2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2
SRM-15 | Staff Room, 15m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
SRM-15 | Staff Room, 15m2 | FA | DWWH-005 | WINDOW | 1 | desirable
SRM-15 | Staff Room, 15m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
SRM-15 | Staff Room, 15m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
SRM-15 | Staff Room, 15m2 | FFE | FSPV-004 | FIRE EXTINGUISHER | 1
SRM-15 | Staff Room, 15m2 | FFE | FQBS-015 | CHAIR: dining | 4
SRM-15 | Staff Room, 15m2 | FFE | FQBS-039 | LOUNGE: 1 seat | 2
SRM-15 | Staff Room, 15m2 | FFE | DWWD-004 | BLIND: roller | 1
SRM-15 | Staff Room, 15m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
SRM-15 | Staff Room, 15m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
SRM-15 | Staff Room, 15m2 | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 1
SRM-15 | Staff Room, 15m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to sink
SRM-15 | Staff Room, 15m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to sink
SRM-15 | Staff Room, 15m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
SRM-15 | Staff Room, 15m2 | FFE | FSPV-005 | FIRE EXTINGUISHER: blanket | 1
SRM-15 | Staff Room, 15m2 | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1
SRM-15 | Staff Room, 15m2 | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | quantity and type of bins to be based on local waste management policies
SRM-15 | Staff Room, 15m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
SRM-15 | Staff Room, 15m2 | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 1
SRM-15 | Staff Room, 15m2 | FFE | HYGE-003 | BOILING/CHILLED WATER UNIT: Combination | 1 | provide grille in joinery for ventilation
SRM-15 | Staff Room, 15m2 | FFE | HYTP-029 | TAPWARE: boiling/chilled water unit (comb) | 1
SRM-15 | Staff Room, 15m2 | FFE | FQCA-067 | OVEN: microwave, domestic | 1
SRM-15 | Staff Room, 15m2 | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
SRM-15 | Staff Room, 15m2 | FFE | FQCA-032 | FRIDGE: domestic, 300L | 1
SRM-15 | Staff Room, 15m2 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
SRM-15 | Staff Room, 15m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
SRM-15 | Staff Room, 15m2 | FFE | FQTA-055 | TABLE: round, 900 diam, dining height | 1
SRM-15 | Staff Room, 15m2 | FFE | FQTA-075 | TABLE: square, 600W, low height | 1
SRM-15 | Staff Room, 15m2 | FFE | FQBS-042 | LOUNGE: 2 seat, 1200 wide | 1
SRM-15 | Staff Room, 15m2 | FFE | FIJO-163 | CUPBOARD: tall, single microwave | 1
SRM-15 | Staff Room, 15m2 | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead is also acceptable
SRM-15 | Staff Room, 15m2 | FFE | HYBA-080 | SINK: single, with drainer, accessible | 1
SRM-15 | Staff Room, 15m2 | FFE | FIJO-226 | CUPBOARD: drawer unit, bin enclosure | 1 | inclusion will depend on waste management and infection control policies
SRM-15 | Staff Room, 15m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 x to television, 1 x to telephone
SRM-15 | Staff Room, 15m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
SRM-15 | Staff Room, 15m2 | SE | ITIN-070 | OUTLET: MATV | 1 | to television, may be replaced with data outlet in accordance with ICT policy
SRM-15 | Staff Room, 15m2 | SE | ELBO-015 | SWITCH: light, single | 1
SRM-15 | Staff Room, 15m2 | SE | ITCL-001 | ANNUNCIATOR: nurse call | 1 | optional, as required in patient care areas, audible
SRM-15 | Staff Room, 15m2 | SE | ELGP-109 | GPO: single, wall mounted | 4
SRM-15 | Staff Room, 15m2 | SE | ELGP-208 | GPO: double, wall mounted | 4
SRM-15 | Staff Room, 15m2 | SE | ITSE-038 | READER: access control, general | 1 | optional
SRM-35 | Staff Room, 35m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent around sink
SRM-35 | Staff Room, 35m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 13
SRM-35 | Staff Room, 35m2 | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
SRM-35 | Staff Room, 35m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
SRM-35 | Staff Room, 35m2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 3
SRM-35 | Staff Room, 35m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
SRM-35 | Staff Room, 35m2 | FA | DWWH-005 | WINDOW | 1 | desirable
SRM-35 | Staff Room, 35m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
SRM-35 | Staff Room, 35m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
SRM-35 | Staff Room, 35m2 | FFE | FSPV-004 | FIRE EXTINGUISHER | 1
SRM-35 | Staff Room, 35m2 | FFE | FQBS-015 | CHAIR: dining | 16
SRM-35 | Staff Room, 35m2 | FFE | FQBS-039 | LOUNGE: 1 seat | 4
SRM-35 | Staff Room, 35m2 | FFE | DWWD-004 | BLIND: roller | 1
SRM-35 | Staff Room, 35m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
SRM-35 | Staff Room, 35m2 | FFE | FIJO-116 | CUPBOARD: tall, double door, adj shelves | 1
SRM-35 | Staff Room, 35m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
SRM-35 | Staff Room, 35m2 | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 2
SRM-35 | Staff Room, 35m2 | FFE | FIJO-156 | CUPBOARD: wall mount, single door, adj shelves | 1
SRM-35 | Staff Room, 35m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to sink
SRM-35 | Staff Room, 35m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to sink
SRM-35 | Staff Room, 35m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
SRM-35 | Staff Room, 35m2 | FFE | FSPV-005 | FIRE EXTINGUISHER: blanket | 1
SRM-35 | Staff Room, 35m2 | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1
SRM-35 | Staff Room, 35m2 | FFE | FQCW-019 | BIN: waste, general, 50L | 1 | quantity and type of bins to be based on local waste management policies
SRM-35 | Staff Room, 35m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
SRM-35 | Staff Room, 35m2 | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 1
SRM-35 | Staff Room, 35m2 | FFE | HYGE-003 | BOILING/CHILLED WATER UNIT: Combination | 1 | provide grille in joinery for ventilation
SRM-35 | Staff Room, 35m2 | FFE | HYTP-029 | TAPWARE: boiling/chilled water unit (comb) | 1
SRM-35 | Staff Room, 35m2 | FFE | FQCA-067 | OVEN: microwave, domestic | 2
SRM-35 | Staff Room, 35m2 | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
SRM-35 | Staff Room, 35m2 | FFE | FQCA-032 | FRIDGE: domestic, 300L | 1
SRM-35 | Staff Room, 35m2 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
SRM-35 | Staff Room, 35m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
SRM-35 | Staff Room, 35m2 | FFE | FQTA-055 | TABLE: round, 900 diam, dining height | 4
SRM-35 | Staff Room, 35m2 | FFE | FQTA-075 | TABLE: square, 600W, low height | 3
SRM-35 | Staff Room, 35m2 | FFE | FQBS-042 | LOUNGE: 2 seat, 1200 wide | 2
SRM-35 | Staff Room, 35m2 | FFE | FIJO-164 | CUPBOARD: tall, double microwave | 1
SRM-35 | Staff Room, 35m2 | FFE | FIJO-212 | BULKHEAD: joinery | 3 | plasterboard bulkhead is also acceptable
SRM-35 | Staff Room, 35m2 | FFE | FQCW-062 | BIN: waste, recycling, comingled, 50L | 1 | quantity and type of bins to be based on local waste management policies
SRM-35 | Staff Room, 35m2 | FFE | FIJO-228 | JOINERY UNIT: sink shroud, accessible | 1
SRM-35 | Staff Room, 35m2 | FFE | HYBA-080 | SINK: single, with drainer, accessible | 1
SRM-35 | Staff Room, 35m2 | FFE | FIJO-226 | CUPBOARD: drawer unit, bin enclosure | 2 | inclusion will depend on waste management and infection control policies
SRM-35 | Staff Room, 35m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 x to television, 1 x to telephone
SRM-35 | Staff Room, 35m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
SRM-35 | Staff Room, 35m2 | SE | ITIN-070 | OUTLET: MATV | 1 | to television, may be replaced with data outlet in accordance with ICT policy
SRM-35 | Staff Room, 35m2 | SE | ELBO-015 | SWITCH: light, single | 1
SRM-35 | Staff Room, 35m2 | SE | ITCL-001 | ANNUNCIATOR: nurse call | 1 | optional, as required in patient care areas, audible
SRM-35 | Staff Room, 35m2 | SE | ELGP-109 | GPO: single, wall mounted | 5
SRM-35 | Staff Room, 35m2 | SE | ELGP-208 | GPO: double, wall mounted | 6
SRM-35 | Staff Room, 35m2 | SE | ITSE-038 | READER: access control, general | 1 | optional
SSTN-10 | Staff Station, 10m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
SSTN-10 | Staff Station, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
SSTN-10 | Staff Station, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
SSTN-10 | Staff Station, 10m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | acoustic ceiling treatments are also acceptable, including bulkheads
SSTN-10 | Staff Station, 10m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
SSTN-10 | Staff Station, 10m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
SSTN-10 | Staff Station, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
SSTN-10 | Staff Station, 10m2 | FFE | FIJO-178 | JOINERY UNIT: staff station | 1 | depth of bench and counter top to be confirmed based on service requirements and must consider ergonomics, staff safety and security, WHS requirements and Australian Standards
SSTN-10 | Staff Station, 10m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1
SSTN-10 | Staff Station, 10m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | under counter top
SSTN-10 | Staff Station, 10m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2
SSTN-10 | Staff Station, 10m2 | FFE | ITNE-023 | PRINTER: networked | 1
SSTN-10 | Staff Station, 10m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2
SSTN-10 | Staff Station, 10m2 | FFE | FIJO-099 | CAC: cable access cap | 2
SSTN-10 | Staff Station, 10m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
SSTN-10 | Staff Station, 10m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | SE | ELBO-003 | CONTROL PANEL: lighting | 1 | optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | SE | LIFX-008 | LIGHT: task light, built in | 2 | under counter top
SSTN-10 | Staff Station, 10m2 | SE | ELBO-015 | SWITCH: light, single | 2 | to task lighting
SSTN-10 | Staff Station, 10m2 | SE | MGFP-001 | ALARM PANEL: medical gases | 1 | optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 3 | 2 x for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | under bench
SSTN-10 | Staff Station, 10m2 | SE | ELGP-130 | GPO: UPS, single | 1 | to printer; UPS to be provided if downtime computer required
SSTN-10 | Staff Station, 10m2 | SE | ELGP-235 | GPO: UPS, double, wall mounted | 1 | UPS to be provided if downtime computer required, location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | SE | ELPR-007 | UPS: status indicator | 1 | optional
SSTN-14 | Staff Station, 14m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
SSTN-14 | Staff Station, 14m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
SSTN-14 | Staff Station, 14m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
SSTN-14 | Staff Station, 14m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | acoustic ceiling treatments are also acceptable, including bulkheads
SSTN-14 | Staff Station, 14m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
SSTN-14 | Staff Station, 14m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 3
SSTN-14 | Staff Station, 14m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
SSTN-14 | Staff Station, 14m2 | FFE | FIJO-178 | JOINERY UNIT: staff station | 1 | depth of bench and counter top to be confirmed based on service requirements and must consider ergonomics, staff safety and security, WHS requirements and Australian Standards
SSTN-14 | Staff Station, 14m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 2
SSTN-14 | Staff Station, 14m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | under counter top
SSTN-14 | Staff Station, 14m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 3
SSTN-14 | Staff Station, 14m2 | FFE | ITNE-023 | PRINTER: networked | 1
SSTN-14 | Staff Station, 14m2 | FFE | FQGE-056 | PRINTER: desktop, labels | 1 | optional, dependent on service requirements
SSTN-14 | Staff Station, 14m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 3
SSTN-14 | Staff Station, 14m2 | FFE | FIJO-099 | CAC: cable access cap | 3
SSTN-14 | Staff Station, 14m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 x optional, to labels printer if provided
SSTN-14 | Staff Station, 14m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 3 | location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | SE | ELBO-003 | CONTROL PANEL: lighting | 1 | optional, location dependent on project requirements
SSTN-14 | Staff Station, 14m2 | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | optional, location dependent on project requirements
SSTN-14 | Staff Station, 14m2 | SE | LIFX-008 | LIGHT: task light, built in | 3 | under counter top
SSTN-14 | Staff Station, 14m2 | SE | ELBO-015 | SWITCH: light, single | 2 | to task lighting
SSTN-14 | Staff Station, 14m2 | SE | MGFP-001 | ALARM PANEL: medical gases | 1 | optional, location dependent on project requirements
SSTN-14 | Staff Station, 14m2 | SE | ELGP-208 | GPO: double, wall mounted | 6 | 3 x for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3 | location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | under bench
SSTN-14 | Staff Station, 14m2 | SE | ELGP-130 | GPO: UPS, single | 1 | to printer, UPS to be provided if downtime computer required
SSTN-14 | Staff Station, 14m2 | SE | ELGP-235 | GPO: UPS, double, wall mounted | 1 | UPS to be provided if downtime computer required, location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | SE | ELPR-007 | UPS: status indicator | 1 | optional
SSTN-20 | Staff Station, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
SSTN-20 | Staff Station, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 18
SSTN-20 | Staff Station, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
SSTN-20 | Staff Station, 20m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | acoustic ceiling treatments are also acceptable, including bulkheads
SSTN-20 | Staff Station, 20m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
SSTN-20 | Staff Station, 20m2 | FFE | FQBS-018 | CHAIR: office, ergonomic | 4
SSTN-20 | Staff Station, 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
SSTN-20 | Staff Station, 20m2 | FFE | FIJO-178 | JOINERY UNIT: staff station | 1 | depth of bench and counter top to be confirmed based on service requirements and must consider ergonomics, staff safety and security, WHS requirements and Australian Standards
SSTN-20 | Staff Station, 20m2 | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 2
SSTN-20 | Staff Station, 20m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 6 | under counter top
SSTN-20 | Staff Station, 20m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 4
SSTN-20 | Staff Station, 20m2 | FFE | ITNE-023 | PRINTER: networked | 1
SSTN-20 | Staff Station, 20m2 | FFE | FQGE-056 | PRINTER: desktop, labels | 1 | optional, dependent on service requirements
SSTN-20 | Staff Station, 20m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 4
SSTN-20 | Staff Station, 20m2 | FFE | FIJO-099 | CAC: cable access cap | 5 | 1 x optional, to central monitor if provided
SSTN-20 | Staff Station, 20m2 | FFE | MMGE-187 | MONITOR: patient, central monitoring | 1 | optional, dependent on service requirements
SSTN-20 | Staff Station, 20m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 2 x optional, to central monitor and labels printer if provided
SSTN-20 | Staff Station, 20m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | location of outlets to meet local operational/WHS requirements
SSTN-20 | Staff Station, 20m2 | SE | ELBO-003 | CONTROL PANEL: lighting | 1 | optional, location dependent on project requirements
SSTN-20 | Staff Station, 20m2 | SE | MEGE-007 | CONTROL PANEL: temperature | 1 | optional, location dependent on project requirements
SSTN-20 | Staff Station, 20m2 | SE | LIFX-008 | LIGHT: task light, built in | 4 | under counter top
SSTN-20 | Staff Station, 20m2 | SE | ELBO-015 | SWITCH: light, single | 4 | to task lighting
SSTN-20 | Staff Station, 20m2 | SE | MGFP-001 | ALARM PANEL: medical gases | 1 | optional, location dependent on project requirements
SSTN-20 | Staff Station, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 8 | 4 x for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
SSTN-20 | Staff Station, 20m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 5 | 1 x optional, to central monitor if provided
SSTN-20 | Staff Station, 20m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | under bench
SSTN-20 | Staff Station, 20m2 | SE | ELGP-130 | GPO: UPS, single | 1 | to printer, UPS to be provided if downtime computer required
SSTN-20 | Staff Station, 20m2 | SE | ELGP-235 | GPO: UPS, double, wall mounted | 1 | UPS to be provided if downtime computer required, location of outlets to meet local operational/WHS requirements
SSTN-20 | Staff Station, 20m2 | SE | ELPR-007 | UPS: status indicator | 1 | optional
STAD | Store - Accountable Drugs | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STAD | Store - Accountable Drugs | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
STAD | Store - Accountable Drugs | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
STAD | Store - Accountable Drugs | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
STAD | Store - Accountable Drugs | FA | DWGE-003 | DOOR: 910mm c/o, steel, strongroom, security door, paint | 1 | outer door; access and door release controls to be determined based on security strategy
STAD | Store - Accountable Drugs | FA | DWGE-002 | DOOR: 910mm c/o, steel, strongroom, grille gate door, paint | 1 | inner door; access and door release controls to be determined based on security strategy
STAD | Store - Accountable Drugs | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
STAD | Store - Accountable Drugs | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1 | extent dependent on type and height storage solution
STAD | Store - Accountable Drugs | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
STAD | Store - Accountable Drugs | FFE | FIHR-002 | BRACKET: for CCTV camera, ceiling mounted | 1
STAD | Store - Accountable Drugs | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1
STAD | Store - Accountable Drugs | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
STAD | Store - Accountable Drugs | FFE | ITSE-012 | CAMERA: CCTV | 1
STAD | Store - Accountable Drugs | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | may be on wall or desk mounted bracket, an additional screen may be provided depending on project ICT requirements
STAD | Store - Accountable Drugs | FFE | MMGE-034 | FRIDGE: drugs, large | 1 | optional
STAD | Store - Accountable Drugs | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
STAD | Store - Accountable Drugs | FFE | ITNE-003 | BAR CODING: reader | 1
STAD | Store - Accountable Drugs | FFE | FIJO-212 | BULKHEAD: joinery | 1
STAD | Store - Accountable Drugs | FFE | FQSM-048 | SHELVING: storage solution, shelving, 600W x 400D x 2100H nom., wire, mobile | 3 | type and quantity of storage options to be determined based on service requirements
STAD | Store - Accountable Drugs | FFE | FQGE-093 | PRINTER: desktop, labels, pharmacy | 1
STAD | Store - Accountable Drugs | FFE | FQDW-051 | DESK: adj height, 1500W x 600D x 900H nom. | 1
STAD | Store - Accountable Drugs | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, temperature monitoring, for refrigerator if provided
STAD | Store - Accountable Drugs | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
STAD | Store - Accountable Drugs | SE | MEGE-015 | VENTILATION PORT | 2
STAD | Store - Accountable Drugs | SE | LIFX-008 | LIGHT: task light, built in | 1 | under wall mounted joinery
STAD | Store - Accountable Drugs | SE | ELBO-015 | SWITCH: light, single | 2 | 1 x general room lighting, 1 x task light
STAD | Store - Accountable Drugs | SE | ELGP-208 | GPO: double, wall mounted | 3 | extent of emergency power to be determined based on service requirements
STAD | Store - Accountable Drugs | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | optional, for refrigerator if provided
STAD | Store - Accountable Drugs | SE | ITSE-038 | READER: access control, general | 1
STAD | Store - Accountable Drugs | SE | ITSE-003 | ALARM: intruder detection | 1 | to entry lock mechanism
STBK | Store - Bulk | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STBK | Store - Bulk | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
STBK | Store - Bulk | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
STBK | Store - Bulk | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
STBK | Store - Bulk | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 | height dependent on movement of trolleys and pallets, crash rails are also acceptable
STBK | Store - Bulk | FA | DWGL-062 | DOOR: 1800mm c/o, double leaf, observation panel, solid core/glass, paint | 1 | lockable or secure staff access, hold open hardware may be required
STBK | Store - Bulk | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STBK | Store - Bulk | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STBK | Store - Bulk | FFE | FQSN-086 | SHELVING: floor standing, 900W x 400D x 2100H nom., metal | 2 | type and extent of storage solutions will be dependent on service requirements
STBK | Store - Bulk | FFE | FQSM-032 | TROLLEY: receiving | 3
STBK | Store - Bulk | FFE | FQCA-026 | FRIDGE: commercial, floor standing, double door | 1 | optional
STBK | Store - Bulk | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | optional, to refrigerator if provided and temperature monitoring is required
STBK | Store - Bulk | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
STBK | Store - Bulk | SE | ELGP-208 | GPO: double, wall mounted | 1
STBK | Store - Bulk | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | optional, to refrigerator if provided
STBK | Store - Bulk | SE | ITSE-038 | READER: access control, general | 1
STCL | Store - Cleaner | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STCL | Store - Cleaner | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
STCL | Store - Cleaner | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
STCL | Store - Cleaner | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
STCL | Store - Cleaner | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 | height dependent on movement of trolleys and pallets, crash rails are also acceptable
STCL | Store - Cleaner | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STCL | Store - Cleaner | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1 | lockable or secure staff access, hold open hardware may be required, vision panel may be provided
STCL | Store - Cleaner | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STCL | Store - Cleaner | FFE | FQSN-012 | CABINET: cleaning equipment | 1 | lockable
STCL | Store - Cleaner | FFE | FIHR-029 | HOOK: equipment | 2 | type and extent of storage solutions will be dependent on service requirements
STCL | Store - Cleaner | FFE | FQSN-086 | SHELVING: floor standing, 900W x 400D x 2100H nom., metal | 3 | type and extent of storage solutions will be dependent on service requirements
STCL | Store - Cleaner | SE | ELBO-015 | SWITCH: light, single | 1
STCL | Store - Cleaner | SE | ELGP-208 | GPO: double, wall mounted | 2
STCL | Store - Cleaner | SE | ITSE-038 | READER: access control, general | 1
STEQ-14 | Store - Equipment, 14m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STEQ-14 | Store - Equipment, 14m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
STEQ-14 | Store - Equipment, 14m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
STEQ-14 | Store - Equipment, 14m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
STEQ-14 | Store - Equipment, 14m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 5 | height dependent on type and height of mobile equipment, crash rails are also acceptable
STEQ-14 | Store - Equipment, 14m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STEQ-14 | Store - Equipment, 14m2 | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
STEQ-14 | Store - Equipment, 14m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STEQ-14 | Store - Equipment, 14m2 | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 4 | optional, provision dependent on service requirements, to be rated for minimum 10kg per hook if provided
STEQ-14 | Store - Equipment, 14m2 | FFE | FIRT-012 | RAIL: equipment | 2 | optional, provision dependent on service requirements
STEQ-14 | Store - Equipment, 14m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
STEQ-14 | Store - Equipment, 14m2 | FFE | FQSN-082 | SHELVING: floor standing, 900W x 450D x 2100H nom., wire | 3 | adjustable shelving; type and quantity of storage options to be determined based on service requirements
STEQ-14 | Store - Equipment, 14m2 | SE | ELBO-015 | SWITCH: light, single | 1
STEQ-14 | Store - Equipment, 14m2 | SE | ELGP-208 | GPO: double, wall mounted | 13 | type, quantity and configuration of outlets dependent on operational and equipment requirements
STEQ-20 | Store - Equipment, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STEQ-20 | Store - Equipment, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
STEQ-20 | Store - Equipment, 20m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
STEQ-20 | Store - Equipment, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
STEQ-20 | Store - Equipment, 20m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 5 | height dependent on type and height of mobile equipment, crash rails are also acceptable
STEQ-20 | Store - Equipment, 20m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STEQ-20 | Store - Equipment, 20m2 | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
STEQ-20 | Store - Equipment, 20m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STEQ-20 | Store - Equipment, 20m2 | FFE | FIHR-030 | HOOK: equipment, on mounting plate | 4 | optional, provision dependent on service requirements, to be rated for minimum 10kg per hook if provided
STEQ-20 | Store - Equipment, 20m2 | FFE | FIRT-012 | RAIL: equipment | 3 | optional, provision dependent on service requirements
STEQ-20 | Store - Equipment, 20m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
STEQ-20 | Store - Equipment, 20m2 | FFE | FQSN-082 | SHELVING: floor standing, 900W x 450D x 2100H nom., wire | 3 | adjustable shelving; type and quantity of storage options to be determined based on service requirements
STEQ-20 | Store - Equipment, 20m2 | SE | ELBO-015 | SWITCH: light, single | 1
STEQ-20 | Store - Equipment, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 16 | type, quantity and configuration of outlets dependent on operational and equipment requirements
STFS-10 | Store - Files, 10m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STFS-10 | Store - Files, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
STFS-10 | Store - Files, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
STFS-10 | Store - Files, 10m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STFS-10 | Store - Files, 10m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
STFS-10 | Store - Files, 10m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | Lockable
STFS-10 | Store - Files, 10m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STFS-10 | Store - Files, 10m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional.
STFS-10 | Store - Files, 10m2 | FFE | FQSN-085 | SHELVING: floor standing, 900W x 400D x 2100H nom., wire | 9
STFS-10 | Store - Files, 10m2 | FFE | FQGE-095 | STEP: safety | 1
STFS-10 | Store - Files, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1
STFS-10 | Store - Files, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
STFS-10 | Store - Files, 10m2 | SE | ITSE-038 | READER: access control, general | 1
STFS-20 | Store - Files, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STFS-20 | Store - Files, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
STFS-20 | Store - Files, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
STFS-20 | Store - Files, 20m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STFS-20 | Store - Files, 20m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
STFS-20 | Store - Files, 20m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1
STFS-20 | Store - Files, 20m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STFS-20 | Store - Files, 20m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
STFS-20 | Store - Files, 20m2 | FFE | FQSN-063 | SHELVING: compactus | 2 | static shelving is also acceptable
STFS-20 | Store - Files, 20m2 | FFE | FQGE-095 | STEP: safety | 1
STFS-20 | Store - Files, 20m2 | SE | ELBO-015 | SWITCH: light, single | 1
STFS-20 | Store - Files, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
STFS-20 | Store - Files, 20m2 | SE | ITSE-038 | READER: access control, general | 1
STGN | Store - General | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STGN | Store - General | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
STGN | Store - General | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
STGN | Store - General | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
STGN | Store - General | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STGN | Store - General | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1
STGN | Store - General | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STGN | Store - General | FFE | FQSN-007 | BIN: storage bins, wire mesh, stainless steel | 15 | optional
STGN | Store - General | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 3 | optional
STGN | Store - General | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
STGN | Store - General | FFE | FQSN-082 | SHELVING: floor standing, 900W x 450D x 2100H nom., wire | 6 | adjustable shelving; type and quantity of storage options to be determined based on service requirements
STGN | Store - General | SE | ELBO-015 | SWITCH: light, single | 1
STGN | Store - General | SE | ELGP-208 | GPO: double, wall mounted | 1
STPP | Store - Patient Property | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
STPP | Store - Patient Property | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
STPP | Store - Patient Property | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Optional. To be decided at project level.
STPP | Store - Patient Property | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
STPP | Store - Patient Property | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
STPP | Store - Patient Property | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | External face only.
STPP | Store - Patient Property | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | Lock set
STPP | Store - Patient Property | FA | CLCN-009 | CORNICE: wall trim fixing | 1
STPP | Store - Patient Property | FFE | FQSN-050 | LOCKER: 4 tier (quarter size) | 4 | 16 compartments, lockable
STPP | Store - Patient Property | FFE | FQSN-086 | SHELVING: floor standing, 900W x 400D x 2100H nom., metal | 5
STPP | Store - Patient Property | SE | ELBO-015 | SWITCH: light, single | 1
STPP | Store - Patient Property | SE | ELGP-208 | GPO: double, wall mounted | 1
STRT | Stress Testing | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
STRT | Stress Testing | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
STRT | Stress Testing | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
STRT | Stress Testing | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
STRT | Stress Testing | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
STRT | Stress Testing | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
STRT | Stress Testing | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1
STRT | Stress Testing | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
STRT | Stress Testing | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
STRT | Stress Testing | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 5
STRT | Stress Testing | FFE | MGFP-002 | FLOWMETER: medical air | 1 | optional
STRT | Stress Testing | FFE | FIHR-019 | BRACKET: for suction bottle | 2
STRT | Stress Testing | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
STRT | Stress Testing | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
STRT | Stress Testing | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
STRT | Stress Testing | FFE | FIHR-026 | HOOK: coat | 2 | optional
STRT | Stress Testing | FFE | FIJO-131 | CUPBOARD: tall, single door, adj shelves, lockable | 1
STRT | Stress Testing | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
STRT | Stress Testing | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to entry door
STRT | Stress Testing | FFE | FQCW-016 | BIN: waste, general, 20L | 1
STRT | Stress Testing | FFE | FIDI-019 | DISPENSER: gown/apron | 1
STRT | Stress Testing | FFE | FIDI-014 | DISPENSER: disposable glove | 1
STRT | Stress Testing | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
STRT | Stress Testing | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
STRT | Stress Testing | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
STRT | Stress Testing | FFE | FIDI-021 | DISPENSER: mask | 1
STRT | Stress Testing | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
STRT | Stress Testing | FFE | MGFP-004 | FLOWMETER: oxygen | 2
STRT | Stress Testing | FFE | MMHA-027 | TROLLEY: resuscitation, adult | 1
STRT | Stress Testing | FFE | MMGE-088 | SAFE: dangerous drugs, small | 1 | optional, for pharmacological stress testing
STRT | Stress Testing | FFE | FQBS-052 | STOOL: mobile, high, adj height | 2
STRT | Stress Testing | FFE | MMGE-002 | ADAPTER: suction | 2
STRT | Stress Testing | FFE | MMGE-100 | SUCTION BOTTLE | 2
STRT | Stress Testing | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
STRT | Stress Testing | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
STRT | Stress Testing | FFE | FQSM-003 | PEDESTAL: mobile, wire basket unit, 840H | 2
STRT | Stress Testing | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar)
STRT | Stress Testing | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
STRT | Stress Testing | FFE | ITCL-014 | CLOCK: analogue, electric | 1
STRT | Stress Testing | FFE | MMHA-002 | DEFIBRILLATOR | 1
STRT | Stress Testing | FFE | MMMI-325 | DEVICE: imaging, echocardiography machine | 1
STRT | Stress Testing | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
STRT | Stress Testing | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
STRT | Stress Testing | FFE | MMAH-027 | TREADMILL: automatic | 1
STRT | Stress Testing | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
STRT | Stress Testing | FFE | FIJO-212 | BULKHEAD: joinery | 1
STRT | Stress Testing | FFE | MMGE-179 | MACHINE: electrocardiography (ECG), c/w trolley and printer shelf | 1
STRT | Stress Testing | FFE | MMBE-069 | TROLLEY: patient, echocardiography | 1
STRT | Stress Testing | FFE | ITNE-071 | COMPUTER: desktop, with dual display screens | 1
STRT | Stress Testing | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 5 | 1 outlet for telephone
STRT | Stress Testing | SE | ELPR-006 | RCD: residual current device | 2
STRT | Stress Testing | SE | ELGP-101 | GPO: single, ceiling mounted | 1
STRT | Stress Testing | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
STRT | Stress Testing | SE | ELBO-015 | SWITCH: light, single | 2 | optional, to optional change room
STRT | Stress Testing | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
STRT | Stress Testing | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel, optional
STRT | Stress Testing | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
STRT | Stress Testing | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
STRT | Stress Testing | SE | ELGP-109 | GPO: single, wall mounted | 1
STRT | Stress Testing | SE | ELGP-208 | GPO: double, wall mounted | 6
STRT | Stress Testing | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3
STRT | Stress Testing | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
STRT | Stress Testing | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
STRT | Stress Testing | SE | ELBO-012 | SWITCH: light, dimmer | 1
STRT | Stress Testing | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 3
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 2
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | MGFP-002 | FLOWMETER: medical air | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIDI-003 | DISPENSER: bedroll | 1 | or provided as an attachment to exam couch
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 | consider weight capacity of chair
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIHR-026 | HOOK: coat | 2 | optional
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1 | to patient access door
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIRT-031 | TRACK: curtain, privacy | 2 | to staff access doorway and internal window as required
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQGE-010 | CURTAIN: privacy screen | 3 | to internal window as required
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | 1 to basin, 1 to desk
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIHR-011 | BRACKET: for monitor, wall mounted | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | MMBE-044 | TROLLEY: patient, transport | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | wall mounted
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FIJO-194 | SHELF: laminate | 1 | to observation window
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | MMGE-002 | ADAPTER: suction | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | MMGE-100 | SUCTION BOTTLE | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQSM-016 | TROLLEY | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | LIFX-026 | LIGHT: examination, wall mounted | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | FFE | WLPT-012 | SCREEN: security, safety glass, with communication slot | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 outlet for telephone
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ELPR-006 | RCD: residual current device | 1 | to services panel
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ELBO-015 | SWITCH: light, single | 2
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | in discreet location easily accessible by staff
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITSE-038 | READER: access control, general | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ELGP-130 | GPO: UPS, single | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional, to reception door
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 3
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWOB-007 | OBSERVATION: internal window, alum/safety glass, powdercoat/paint | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional, to reception
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-003 | DISPENSER: bedroll | 1 | or provided as an attachment to exam couch
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 | consider weight capacity of chair
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-026 | HOOK: coat | 2 | optional
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIRT-031 | TRACK: curtain, privacy | 2 | to internal window as required
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQGE-010 | CURTAIN: privacy screen | 3 | to internal window as required
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | 1 to basin, 1 to desk
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-011 | BRACKET: for monitor, wall mounted | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMBE-044 | TROLLEY: patient, transport | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | wall mounted
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQSM-016 | TROLLEY | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | LIFX-026 | LIGHT: examination, wall mounted | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELPR-006 | RCD: residual current device | 1 | to services panel
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELBO-015 | SWITCH: light, single | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | to WOW
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | in discreet location easily accessible by staff
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITSE-038 | READER: access control, general | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-130 | GPO: UPS, single | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
TRMT | Treatment Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
TRMT | Treatment Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 7
TRMT | Treatment Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
TRMT | Treatment Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
TRMT | Treatment Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | to basin
TRMT | Treatment Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
TRMT | Treatment Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 5
TRMT | Treatment Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
TRMT | Treatment Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
TRMT | Treatment Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
TRMT | Treatment Room | FFE | MGFP-002 | FLOWMETER: medical air | 1
TRMT | Treatment Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
TRMT | Treatment Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
TRMT | Treatment Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
TRMT | Treatment Room | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
TRMT | Treatment Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
TRMT | Treatment Room | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
TRMT | Treatment Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
TRMT | Treatment Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1
TRMT | Treatment Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
TRMT | Treatment Room | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
TRMT | Treatment Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
TRMT | Treatment Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
TRMT | Treatment Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
TRMT | Treatment Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
TRMT | Treatment Room | FFE | MMGE-119 | TROLLEY: equipment | 1
TRMT | Treatment Room | FFE | MMBE-043 | TROLLEY: patient, examination | 1
TRMT | Treatment Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
TRMT | Treatment Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
TRMT | Treatment Room | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1
TRMT | Treatment Room | FFE | MMGE-002 | ADAPTER: suction | 1
TRMT | Treatment Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
TRMT | Treatment Room | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
TRMT | Treatment Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
TRMT | Treatment Room | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
TRMT | Treatment Room | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 | optional, may be portable/mobile on stand
TRMT | Treatment Room | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
TRMT | Treatment Room | FFE | ITNE-023 | PRINTER: networked | 1 | optional
TRMT | Treatment Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
TRMT | Treatment Room | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
TRMT | Treatment Room | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1 | optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT | Treatment Room | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
TRMT | Treatment Room | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
TRMT | Treatment Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to telephone
TRMT | Treatment Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2
TRMT | Treatment Room | SE | ELPR-006 | RCD: residual current device | 4
TRMT | Treatment Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to exam light
TRMT | Treatment Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
TRMT | Treatment Room | SE | LIFX-008 | LIGHT: task light, built in | 1 | under wall mounted joinery
TRMT | Treatment Room | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 1 x task light, 1 x examination light
TRMT | Treatment Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRMT | Treatment Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
TRMT | Treatment Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRMT | Treatment Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light
TRMT | Treatment Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset
TRMT | Treatment Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
TRMT | Treatment Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level, for patient trolley
TRMT | Treatment Room | SE | ELGP-208 | GPO: double, wall mounted | 2
TRMT | Treatment Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
TRMT | Treatment Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
TRMT | Treatment Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
TRMT | Treatment Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
TRMT | Treatment Room | SE | ELGP-105 | GPO: single, on services panel | 3
TRMT | Treatment Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent to extend under basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 8
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | WLWA-007 | WALL FINISH: splashback | 2 | to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to bench
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | optional, second door for egress
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FA | CLCN-009 | CORNICE: wall trim fixing | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FQBS-030 | CHAIR: visitor, patient | 6
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIJO-116 | CUPBOARD: tall, double door, adj shelves | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIJO-140 | CUPBOARD: underbench, single door, adj shelves | 2
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FQGE-010 | CURTAIN: privacy screen | 3
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIJO-104 | CUPBOARD: drawer unit, 3 equal | 1 | for thermaplastic storage, width to be confirmed to suit size of material
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 4
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | HYBA-010 | BASIN: handwash, Type B | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | HYBA-069 | SINK: single, with drainer, 930mmL | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | MMAH-012 | DEVICE: continuous passive motion (CPM), hand and fingers | 1 | optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | MMAH-021 | PAN: splint, molding | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | LIFX-026 | LIGHT: examination, wall mounted | 2 | to therapy tables, ceiling mounted is also acceptable
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | HYDR-008 | TRAP: plaster | 1 | optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FQGE-043 | MACHINE: sewing | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | MMLA-014 | DEVICE: wax bath | 1 | optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | MMGE-150 | VIEWER: X-ray, 1 screen | 1 | optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 3
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FQCW-010 | BIN: waste, clinical, 80L | 1 | type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead also acceptable
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 2 | to therapy tables, dependent on ICT strategy
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 2 | to therapy tables, dependent on ICT strategy
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FQTA-084 | TABLE: adjustable height, hand therapy | 2
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FQDW-049 | DESK: adj height, 1200W x 600D x 750H nom. | 2
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIDI-053 | DISPENSER: velcro | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | FFE | FIRT-047 | TRACK: curtain, privacy, U shaped | 2
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to telephone
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ELPR-006 | RCD: residual current device | 2
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 2 x examination lights
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ELGP-109 | GPO: single, wall mounted | 3 | 1 x optional to x-ray viewing box
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ELGP-208 | GPO: double, wall mounted | 9 | extent of emergency power to be determined based on service requirements
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | SE | ITSE-006 | BUTTON: duress, fixed | 2
TRMT-POD | Treatment Room - Podiatry | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent to extend under basin
TRMT-POD | Treatment Room - Podiatry | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 9
TRMT-POD | Treatment Room - Podiatry | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
TRMT-POD | Treatment Room - Podiatry | FA | WLWA-007 | WALL FINISH: splashback | 2
TRMT-POD | Treatment Room - Podiatry | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 5
TRMT-POD | Treatment Room - Podiatry | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 4
TRMT-POD | Treatment Room - Podiatry | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
TRMT-POD | Treatment Room - Podiatry | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1
TRMT-POD | Treatment Room - Podiatry | FA | CLCN-009 | CORNICE: wall trim fixing | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FIHR-019 | BRACKET: for suction bottle | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FIHR-016 | BRACKET: for sharps bin | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 2
TRMT-POD | Treatment Room - Podiatry | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FQGE-010 | CURTAIN: privacy screen | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
TRMT-POD | Treatment Room - Podiatry | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
TRMT-POD | Treatment Room - Podiatry | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
TRMT-POD | Treatment Room - Podiatry | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
TRMT-POD | Treatment Room - Podiatry | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
TRMT-POD | Treatment Room - Podiatry | FFE | MGFP-004 | FLOWMETER: oxygen | 1
TRMT-POD | Treatment Room - Podiatry | FFE | MMGE-139 | TROLLEY: procedure | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FQBS-051 | STOOL: mobile, adj height | 1
TRMT-POD | Treatment Room - Podiatry | FFE | MMGE-002 | ADAPTER: suction | 1
TRMT-POD | Treatment Room - Podiatry | FFE | MMGE-100 | SUCTION BOTTLE | 1
TRMT-POD | Treatment Room - Podiatry | FFE | HYBA-010 | BASIN: handwash, Type B | 1
TRMT-POD | Treatment Room - Podiatry | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
TRMT-POD | Treatment Room - Podiatry | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | computer may alternatively be on benchtop or wall mounted
TRMT-POD | Treatment Room - Podiatry | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
TRMT-POD | Treatment Room - Podiatry | FFE | MMAH-010 | CHAIR: podiatry, electric | 1
TRMT-POD | Treatment Room - Podiatry | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1 | optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT-POD | Treatment Room - Podiatry | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | computer may alternatively be on benchtop or wall mounted
TRMT-POD | Treatment Room - Podiatry | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead also acceptable
TRMT-POD | Treatment Room - Podiatry | FFE | FIDI-054 | DISPENSER: ppe combination | 1
TRMT-POD | Treatment Room - Podiatry | FFE | FIRT-047 | TRACK: curtain, privacy, U shaped | 1
TRMT-POD | Treatment Room - Podiatry | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to telephone
TRMT-POD | Treatment Room - Podiatry | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1
TRMT-POD | Treatment Room - Podiatry | SE | ELPR-006 | RCD: residual current device | 3
TRMT-POD | Treatment Room - Podiatry | SE | ELGP-101 | GPO: single, ceiling mounted | 1
TRMT-POD | Treatment Room - Podiatry | SE | LIFX-008 | LIGHT: task light, built in | 1
TRMT-POD | Treatment Room - Podiatry | SE | ELBO-015 | SWITCH: light, single | 3 | 1 x general room lighting, 1 x task light, 1 x examination light
TRMT-POD | Treatment Room - Podiatry | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRMT-POD | Treatment Room - Podiatry | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRMT-POD | Treatment Room - Podiatry | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1
TRMT-POD | Treatment Room - Podiatry | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
TRMT-POD | Treatment Room - Podiatry | SE | ELGP-208 | GPO: double, wall mounted | 3 | extent of emergency power to be determined based on service requirements
TRMT-POD | Treatment Room - Podiatry | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
TRMT-POD | Treatment Room - Podiatry | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
TRMT-POD | Treatment Room - Podiatry | SE | ITSE-006 | BUTTON: duress, fixed | 1
TRMT-POD | Treatment Room - Podiatry | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
TRMT-POD | Treatment Room - Podiatry | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
TRMT-POD | Treatment Room - Podiatry | SE | ELGP-205 | GPO: double, on services panel | 2 | extent of emergency power to be determined based on service requirements
ULTR | Ultrasound Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
ULTR | Ultrasound Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
ULTR | Ultrasound Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
ULTR | Ultrasound Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
ULTR | Ultrasound Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
ULTR | Ultrasound Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin; selection of material to comply with AHFG Part D Infection Control
ULTR | Ultrasound Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiled ceiling also acceptable
ULTR | Ultrasound Room | FA | DWSC-012 | DOOR: 1200mm c/o, 1 1/2 leaf, solid core, paint | 1
ULTR | Ultrasound Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ULTR | Ultrasound Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 6
ULTR | Ultrasound Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
ULTR | Ultrasound Room | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 | optional
ULTR | Ultrasound Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
ULTR | Ultrasound Room | FFE | FIHR-026 | HOOK: coat | 2 | optional
ULTR | Ultrasound Room | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
ULTR | Ultrasound Room | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1 | over mobile storage unit
ULTR | Ultrasound Room | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
ULTR | Ultrasound Room | FFE | FIRT-031 | TRACK: curtain, privacy | 1 | optional, external to entry doors
ULTR | Ultrasound Room | FFE | FQGE-010 | CURTAIN: privacy screen | 2 | 1-internal to entry door, 1-external to entry door optional
ULTR | Ultrasound Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ULTR | Ultrasound Room | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
ULTR | Ultrasound Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ULTR | Ultrasound Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ULTR | Ultrasound Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ULTR | Ultrasound Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
ULTR | Ultrasound Room | FFE | MMBE-043 | TROLLEY: patient, examination | 1
ULTR | Ultrasound Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
ULTR | Ultrasound Room | FFE | FIHR-055 | RACK: scanhead | 1
ULTR | Ultrasound Room | FFE | FQBS-051 | STOOL: mobile, adj height | 1
ULTR | Ultrasound Room | FFE | FQSM-016 | TROLLEY | 1 | for gel warmer
ULTR | Ultrasound Room | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
ULTR | Ultrasound Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
ULTR | Ultrasound Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
ULTR | Ultrasound Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
ULTR | Ultrasound Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
ULTR | Ultrasound Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
ULTR | Ultrasound Room | FFE | MMMI-340 | DISPLAY SCREEN: slave, for ultrasound | 1
ULTR | Ultrasound Room | FFE | MMMI-329 | DEVICE: imaging, ultrasound scanning unit | 1
ULTR | Ultrasound Room | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 1
ULTR | Ultrasound Room | FFE | FIJO-212 | BULKHEAD: joinery | 1
ULTR | Ultrasound Room | FFE | MMGE-169 | SLING: arm, dynamic, ceiling mounted | 1
ULTR | Ultrasound Room | FFE | MMMI-376 | WARMER: gel | 1 | on trolley
ULTR | Ultrasound Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 2-scanning station; 1-desk
ULTR | Ultrasound Room | SE | ELPR-006 | RCD: residual current device | 2
ULTR | Ultrasound Room | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for slave display screen
ULTR | Ultrasound Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
ULTR | Ultrasound Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
ULTR | Ultrasound Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
ULTR | Ultrasound Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ULTR | Ultrasound Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | to patient bed
ULTR | Ultrasound Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | clock
ULTR | Ultrasound Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | desk
ULTR | Ultrasound Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | scanning station
ULTR | Ultrasound Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | as required
ULTR | Ultrasound Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
ULTR | Ultrasound Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
ULTR | Ultrasound Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
ULTR | Ultrasound Room | SE | ITIN-061 | OUTLET: HDMI, ceiling mounted | 1
ULTR | Ultrasound Room | SE | ITIN-066 | OUTLET: HDMI, wall mounted | 1
ULTR | Ultrasound Room | SE | ELGP-105 | GPO: single, on services panel | 2
ULTR | Ultrasound Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2 | patient services panel
ULTR-PR | Ultrasound Room - Procedures | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
ULTR-PR | Ultrasound Room - Procedures | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
ULTR-PR | Ultrasound Room - Procedures | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
ULTR-PR | Ultrasound Room - Procedures | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
ULTR-PR | Ultrasound Room - Procedures | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin; selection of material to comply with AHFG Part D Infection Control
ULTR-PR | Ultrasound Room - Procedures | FA | WLWA-019 | WALL FINISH: vinyl, full height | 7
ULTR-PR | Ultrasound Room - Procedures | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
ULTR-PR | Ultrasound Room - Procedures | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
ULTR-PR | Ultrasound Room - Procedures | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIHR-019 | BRACKET: for suction bottle | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FQBS-018 | CHAIR: office, ergonomic | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 | optional
ULTR-PR | Ultrasound Room - Procedures | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIHR-026 | HOOK: coat | 2 | optional
ULTR-PR | Ultrasound Room - Procedures | FFE | FQSN-031 | CABINET: short, single door, tambour, adj shelves, lockable | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to entry door
ULTR-PR | Ultrasound Room - Procedures | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ULTR-PR | Ultrasound Room - Procedures | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIDI-014 | DISPENSER: disposable glove | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
ULTR-PR | Ultrasound Room - Procedures | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
ULTR-PR | Ultrasound Room - Procedures | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
ULTR-PR | Ultrasound Room - Procedures | FFE | MMBE-043 | TROLLEY: patient, examination | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MGFP-004 | FLOWMETER: oxygen | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMGE-138 | TROLLEY: preparation | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIHR-055 | RACK: scanhead | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FQBS-051 | STOOL: mobile, adj height | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMGE-002 | ADAPTER: suction | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMGE-100 | SUCTION BOTTLE | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | ITCL-014 | CLOCK: analogue, electric | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMMI-340 | DISPLAY SCREEN: slave, for ultrasound | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMMI-329 | DEVICE: imaging, ultrasound scanning unit | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIJO-212 | BULKHEAD: joinery | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | FIRT-041 | TRACK: curtain, privacy, U shaped, angled | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMGE-169 | SLING: arm, dynamic, ceiling mounted | 1
ULTR-PR | Ultrasound Room - Procedures | FFE | MMMI-376 | WARMER: gel | 1
ULTR-PR | Ultrasound Room - Procedures | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 2-scanning station; 1-desk
ULTR-PR | Ultrasound Room - Procedures | SE | ELPR-006 | RCD: residual current device | 2
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for slave display screen
ULTR-PR | Ultrasound Room - Procedures | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, if N2O is required
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, for invasive procedures
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-062 | OUTLET: suction, on services panel | 1
ULTR-PR | Ultrasound Room - Procedures | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
ULTR-PR | Ultrasound Room - Procedures | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
ULTR-PR | Ultrasound Room - Procedures | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-109 | GPO: single, wall mounted | 1 | to patient bed
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-109 | GPO: single, wall mounted | 1 | clock
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-208 | GPO: double, wall mounted | 2
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | 2 - scanning station, 2 - desk
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | ultrasound machine
ULTR-PR | Ultrasound Room - Procedures | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
ULTR-PR | Ultrasound Room - Procedures | SE | ELBO-012 | SWITCH: light, dimmer | 1
ULTR-PR | Ultrasound Room - Procedures | SE | ITIN-061 | OUTLET: HDMI, ceiling mounted | 1
ULTR-PR | Ultrasound Room - Procedures | SE | ITIN-066 | OUTLET: HDMI, wall mounted | 1
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-105 | GPO: single, on services panel | 2
ULTR-PR | Ultrasound Room - Procedures | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2
UTRM | Uptake Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
UTRM | Uptake Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
UTRM | Uptake Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 5
UTRM | Uptake Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
UTRM | Uptake Room | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1
UTRM | Uptake Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1 | automated, hold open
UTRM | Uptake Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
UTRM | Uptake Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
UTRM | Uptake Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1
UTRM | Uptake Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
UTRM | Uptake Room | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
UTRM | Uptake Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
UTRM | Uptake Room | FFE | FIHR-029 | HOOK: equipment | 2
UTRM | Uptake Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
UTRM | Uptake Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
UTRM | Uptake Room | FFE | MMGE-002 | ADAPTER: suction | 1
UTRM | Uptake Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
UTRM | Uptake Room | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
UTRM | Uptake Room | FFE | ITCL-012 | CAMERA: observation | 1
UTRM | Uptake Room | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | optional
UTRM | Uptake Room | FFE | MMMI-219 | PASS THROUGH: injection port | 1 | optional
UTRM | Uptake Room | FFE | FIHR-077 | BRACKET: for observation camera, ceiling mounted | 1
UTRM | Uptake Room | FFE | MMBE-091 | CHAIR: recliner, clinical, electric | 1 | consider bariatric capacity as required
UTRM | Uptake Room | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1
UTRM | Uptake Room | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | handsfree to control room
UTRM | Uptake Room | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
UTRM | Uptake Room | SE | ELGP-101 | GPO: single, ceiling mounted | 3
UTRM | Uptake Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1
UTRM | Uptake Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
UTRM | Uptake Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
UTRM | Uptake Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1
UTRM | Uptake Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
UTRM | Uptake Room | SE | ELGP-109 | GPO: single, wall mounted | 1
UTRM | Uptake Room | SE | ELGP-208 | GPO: double, wall mounted | 1
UTRM | Uptake Room | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
UTRM | Uptake Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
UTRM | Uptake Room | SE | ELBO-012 | SWITCH: light, dimmer | 2 | inside and outside room, to be reviewed to suit operational requirements
UTRM | Uptake Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2
WAIT-10 | Waiting, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
WAIT-10 | Waiting, 10m2 | FA | WLPR-006 | WALL PROTECTION: corner guards | 1 | coordinated with adjacent wall protection
WAIT-10 | Waiting, 10m2 | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | carpet tiles are also acceptable
WAIT-10 | Waiting, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
WAIT-10 | Waiting, 10m2 | FA | WLWA-022 | WALL FINISH: vinyl, to 900 AFFL | 3 | as required to suit loose furniture layout; crash rails are also acceptable
WAIT-10 | Waiting, 10m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
WAIT-10 | Waiting, 10m2 | FA | DWWH-005 | WINDOW | 1 | desirable
WAIT-10 | Waiting, 10m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WAIT-10 | Waiting, 10m2 | FFE | FQGE-002 | ARTWORK | 1 | optional
WAIT-10 | Waiting, 10m2 | FFE | FQBS-032 | CHAIR: waiting | 6
WAIT-10 | Waiting, 10m2 | FFE | DWWD-004 | BLIND: roller | 1 | desirable, associated with window
WAIT-10 | Waiting, 10m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | to suit local infection control policies
WAIT-10 | Waiting, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WAIT-10 | Waiting, 10m2 | FFE | FQBS-027 | CHAIR: visitor, bariatric | 1 | quantity dependent on service requirements
WAIT-10 | Waiting, 10m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
WAIT-10 | Waiting, 10m2 | FFE | FIHR-045 | RACK: magazine/pamphlet | 1 | optional
WAIT-10 | Waiting, 10m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
WAIT-10 | Waiting, 10m2 | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 1
WAIT-10 | Waiting, 10m2 | FFE | FQTA-071 | TABLE: square, 500W, low height | 1
WAIT-10 | Waiting, 10m2 | SE | ITIN-070 | OUTLET: MATV | 1 | may be replaced with data outlet in accordance with ICT policy
WAIT-10 | Waiting, 10m2 | SE | ELGP-109 | GPO: single, wall mounted | 1 | to television
WAIT-10 | Waiting, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
WAIT-20 | Waiting, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
WAIT-20 | Waiting, 20m2 | FA | WLPR-006 | WALL PROTECTION: corner guards | 1 | coordinated with adjacent wall protection
WAIT-20 | Waiting, 20m2 | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | carpet tiles are also acceptable
WAIT-20 | Waiting, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
WAIT-20 | Waiting, 20m2 | FA | WLWA-022 | WALL FINISH: vinyl, to 900 AFFL | 3 | as required to suit loose furniture layout; crash rails are also acceptable
WAIT-20 | Waiting, 20m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
WAIT-20 | Waiting, 20m2 | FA | DWWH-005 | WINDOW | 1 | desirable
WAIT-20 | Waiting, 20m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WAIT-20 | Waiting, 20m2 | FFE | FQGE-002 | ARTWORK | 1 | optional
WAIT-20 | Waiting, 20m2 | FFE | FQBS-032 | CHAIR: waiting | 14
WAIT-20 | Waiting, 20m2 | FFE | DWWD-004 | BLIND: roller | 1 | desirable, associated with window
WAIT-20 | Waiting, 20m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | to suit local infection control policies
WAIT-20 | Waiting, 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WAIT-20 | Waiting, 20m2 | FFE | FQBS-027 | CHAIR: visitor, bariatric | 2 | quantity dependent on service requirements
WAIT-20 | Waiting, 20m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1
WAIT-20 | Waiting, 20m2 | FFE | FIHR-045 | RACK: magazine/pamphlet | 1 | optional
WAIT-20 | Waiting, 20m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
WAIT-20 | Waiting, 20m2 | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 1
WAIT-20 | Waiting, 20m2 | FFE | FQTA-071 | TABLE: square, 500W, low height | 2
WAIT-20 | Waiting, 20m2 | SE | ITIN-070 | OUTLET: MATV | 1 | may be replaced with data outlet in accordance with ICT policy
WAIT-20 | Waiting, 20m2 | SE | ELGP-109 | GPO: single, wall mounted | 1 | to television
WAIT-20 | Waiting, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
WAIT-30 | Waiting, 30m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
WAIT-30 | Waiting, 30m2 | FA | WLPR-006 | WALL PROTECTION: corner guards | 2 | coordinated with adjacent wall protection
WAIT-30 | Waiting, 30m2 | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 | carpet tiles are also acceptable
WAIT-30 | Waiting, 30m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
WAIT-30 | Waiting, 30m2 | FA | WLWA-022 | WALL FINISH: vinyl, to 900 AFFL | 3 | as required to suit loose furniture layout; crash rails are also acceptable
WAIT-30 | Waiting, 30m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
WAIT-30 | Waiting, 30m2 | FA | DWWH-005 | WINDOW | 1 | desirable
WAIT-30 | Waiting, 30m2 | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WAIT-30 | Waiting, 30m2 | FFE | FQGE-002 | ARTWORK | 2 | optional
WAIT-30 | Waiting, 30m2 | FFE | FQBS-032 | CHAIR: waiting | 21
WAIT-30 | Waiting, 30m2 | FFE | DWWD-004 | BLIND: roller | 1 | desirable, associated with window
WAIT-30 | Waiting, 30m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2 | to suit local infection control policies
WAIT-30 | Waiting, 30m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WAIT-30 | Waiting, 30m2 | FFE | FQBS-027 | CHAIR: visitor, bariatric | 2 | quantity dependent on service requirements
WAIT-30 | Waiting, 30m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 2
WAIT-30 | Waiting, 30m2 | FFE | FIHR-045 | RACK: magazine/pamphlet | 1 | optional
WAIT-30 | Waiting, 30m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional
WAIT-30 | Waiting, 30m2 | FFE | ITBU-011 | DISPLAY SCREEN: MATV | 2
WAIT-30 | Waiting, 30m2 | FFE | FQTA-071 | TABLE: square, 500W, low height | 3
WAIT-30 | Waiting, 30m2 | SE | ITIN-070 | OUTLET: MATV | 2 | Optional. May be replaced with data outlet, in accordance with ICT policy if required.
WAIT-30 | Waiting, 30m2 | SE | ELGP-109 | GPO: single, wall mounted | 2
WAIT-30 | Waiting, 30m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
WAIT-S | Waiting, Sub | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | coordinated with adjacent area, carpet tiles are also acceptable
WAIT-S | Waiting, Sub | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
WAIT-S | Waiting, Sub | FA | WLPR-006 | WALL PROTECTION: corner guards | 1 | coordinated with adjacent wall protection
WAIT-S | Waiting, Sub | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
WAIT-S | Waiting, Sub | FA | WLWA-022 | WALL FINISH: vinyl, to 900 AFFL | 3 | as required to suit loose furniture layout; crash rails are also acceptable
WAIT-S | Waiting, Sub | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | coordinated with adjacent area
WAIT-S | Waiting, Sub | FA | CLCN-009 | CORNICE: wall trim fixing | 1 | coordinated with adjacent area
WAIT-S | Waiting, Sub | FFE | FQBS-032 | CHAIR: waiting | 2
WAIT-S | Waiting, Sub | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | to suit local infection control policies
WAIT-S | Waiting, Sub | FFE | FQBS-027 | CHAIR: visitor, bariatric | 1 | quantity dependent on service requirements
WAIT-S | Waiting, Sub | FFE | FQTA-071 | TABLE: square, 500W, low height | 1
WAIT-S | Waiting, Sub | FFE | FIDI-056 | HOLDER: document, A4 | 1
WAIT-S | Waiting, Sub | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | optional
WAIT-S | Waiting, Sub | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | optional
WAIT-S | Waiting, Sub | SE | ELGP-208 | GPO: double, wall mounted | 1
WAIT-SEC | Waiting - Secure, 6m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1 | Default = carpet; vinyl also acceptable
WAIT-SEC | Waiting - Secure, 6m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 1 | Default = Feather edged: or floor vinyl coved skirting
WAIT-SEC | Waiting - Secure, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
WAIT-SEC | Waiting - Secure, 6m2 | FA | DWGL-032 | DOOR: 1400mm c/o, 1 1/2 leaf, half glazed, solid core/safety glass, paint | 1 | lockable
WAIT-SEC | Waiting - Secure, 6m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
WAIT-SEC | Waiting - Secure, 6m2 | FA | DWPR-003 | DOOR PROTECTION: kickplate, to 300 AFFL, vinyl, prefinished | 1
WAIT-SEC | Waiting - Secure, 6m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
WAIT-SEC | Waiting - Secure, 6m2 | FFE | FQBS-032 | CHAIR: waiting | 3 | some with arms, space for wheelchair/ pram
WAIT-SEC | Waiting - Secure, 6m2 | FFE | FIHR-045 | RACK: magazine/pamphlet | 1 | securely fixed
WAIT-SEC | Waiting - Secure, 6m2 | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 1 | or artwork, optional, secure fixings
WAIT-SEC | Waiting - Secure, 6m2 | FFE | FQGE-080 | STAND: public telephone | 1 | optional; securely fixed
WAIT-SEC | Waiting - Secure, 6m2 | FFE | ITNE-057 | TELEPHONE: public | 1 | with stand, securely fixed; optional
WAIT-SEC | Waiting - Secure, 6m2 | FFE | FQTA-075 | TABLE: square, 600W, low height | 1
WAIT-SEC | Waiting - Secure, 6m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
WAIT-SEC | Waiting - Secure, 6m2 | SE | ITSE-023 | DOOR RELEASE: access control, buzzer | 1
WAIT-SEC | Waiting - Secure, 6m2 | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | to Reception/ Staff Station
WAIT-SEC | Waiting - Secure, 6m2 | SE | ELGP-208 | GPO: double, wall mounted | 1
WCAC | Toilet - Accessible | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
WCAC | Toilet - Accessible | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles are also acceptable
WCAC | Toilet - Accessible | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
WCAC | Toilet - Accessible | FA | WLWA-007 | WALL FINISH: splashback | 1
WCAC | Toilet - Accessible | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
WCAC | Toilet - Accessible | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
WCAC | Toilet - Accessible | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | with privacy latch, emergency release required if inward opening door
WCAC | Toilet - Accessible | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WCAC | Toilet - Accessible | FFE | FQBS-035 | CHANGE TABLE: baby | 1 | optional
WCAC | Toilet - Accessible | FFE | FIHR-026 | HOOK: coat | 2
WCAC | Toilet - Accessible | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WCAC | Toilet - Accessible | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
WCAC | Toilet - Accessible | FFE | FIDI-030 | DISPENSER: soap | 1
WCAC | Toilet - Accessible | FFE | FIDI-036 | DISPENSER: toilet paper | 1
WCAC | Toilet - Accessible | FFE | FIRT-007 | GRAB RAIL: WC, accessible use | 1
WCAC | Toilet - Accessible | FFE | FIRT-006 | GRAB RAIL: WC | 1
WCAC | Toilet - Accessible | FFE | FIBM-006 | MIRROR: fixed, glass | 1
WCAC | Toilet - Accessible | FFE | FQCW-037 | BIN: waste, sanitary | 1
WCAC | Toilet - Accessible | FFE | HYBA-005 | BASIN: handwash, accessible | 1
WCAC | Toilet - Accessible | FFE | HYWC-001 | TOILET SUITE: accessible | 1 | Large format flush buttons to cistern
WCAC | Toilet - Accessible | FFE | HYTP-035 | TAPWARE: mixer, basin, accessible | 1
WCAC | Toilet - Accessible | FFE | FIGE-011 | BACKREST: accessible toilet | 1
WCAC | Toilet - Accessible | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | optional
WCAC | Toilet - Accessible | SE | HYDR-004 | DRAIN: floor waste | 1
WCAC | Toilet - Accessible | SE | ELBO-015 | SWITCH: light, single | 1
WCAC | Toilet - Accessible | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1
WCAC | Toilet - Accessible | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | optional
WCPT | Toilet - Patient | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
WCPT | Toilet - Patient | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles are also acceptable
WCPT | Toilet - Patient | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
WCPT | Toilet - Patient | FA | WLWA-007 | WALL FINISH: splashback | 1
WCPT | Toilet - Patient | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
WCPT | Toilet - Patient | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
WCPT | Toilet - Patient | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | with privacy latch, emergency release required if inward opening door
WCPT | Toilet - Patient | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WCPT | Toilet - Patient | FFE | FIHR-026 | HOOK: coat | 2
WCPT | Toilet - Patient | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WCPT | Toilet - Patient | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
WCPT | Toilet - Patient | FFE | FIDI-030 | DISPENSER: soap | 1
WCPT | Toilet - Patient | FFE | FIDI-036 | DISPENSER: toilet paper | 1
WCPT | Toilet - Patient | FFE | FIRT-006 | GRAB RAIL: WC | 1
WCPT | Toilet - Patient | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | optional
WCPT | Toilet - Patient | FFE | FIBM-006 | MIRROR: fixed, glass | 1
WCPT | Toilet - Patient | FFE | FQCW-037 | BIN: waste, sanitary | 1
WCPT | Toilet - Patient | FFE | HYBA-011 | BASIN: handwash, Type C | 1
WCPT | Toilet - Patient | FFE | HYWC-006 | TOILET SUITE: patient | 1
WCPT | Toilet - Patient | FFE | HYTP-035 | TAPWARE: mixer, basin, accessible | 1
WCPT | Toilet - Patient | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
WCPT | Toilet - Patient | SE | HYDR-004 | DRAIN: floor waste | 1
WCPT | Toilet - Patient | SE | ELBO-015 | SWITCH: light, single | 1
WCPT | Toilet - Patient | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light
WCPT | Toilet - Patient | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
WCPU | Toilet - Public | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
WCPU | Toilet - Public | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles are also acceptable
WCPU | Toilet - Public | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
WCPU | Toilet - Public | FA | WLWA-007 | WALL FINISH: splashback | 1
WCPU | Toilet - Public | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
WCPU | Toilet - Public | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
WCPU | Toilet - Public | FA | DWSC-001 | DOOR: 850mm c/o, single leaf, solid core, paint | 1 | with privacy latch, emergency release required if inward opening door
WCPU | Toilet - Public | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WCPU | Toilet - Public | FFE | FIHR-026 | HOOK: coat | 1
WCPU | Toilet - Public | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WCPU | Toilet - Public | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
WCPU | Toilet - Public | FFE | FIDI-030 | DISPENSER: soap | 1
WCPU | Toilet - Public | FFE | FIDI-036 | DISPENSER: toilet paper | 1
WCPU | Toilet - Public | FFE | FIBM-006 | MIRROR: fixed, glass | 1
WCPU | Toilet - Public | FFE | FQCW-037 | BIN: waste, sanitary | 1
WCPU | Toilet - Public | FFE | HYBA-011 | BASIN: handwash, Type C | 1
WCPU | Toilet - Public | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
WCPU | Toilet - Public | FFE | HYWC-008 | TOILET SUITE: standard | 1
WCPU | Toilet - Public | SE | HYDR-004 | DRAIN: floor waste | 1
WCPU | Toilet - Public | SE | ELBO-015 | SWITCH: light, single | 1
WCST | Toilet - Staff | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | to be tiles if tiled floor
WCST | Toilet - Staff | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles are also acceptable
WCST | Toilet - Staff | FA | DWPR-001 | DOOR PROTECTION: kickplate, to 300 AFFL | 1
WCST | Toilet - Staff | FA | WLWA-007 | WALL FINISH: splashback | 1
WCST | Toilet - Staff | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
WCST | Toilet - Staff | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1
WCST | Toilet - Staff | FA | DWSC-001 | DOOR: 850mm c/o, single leaf, solid core, paint | 1 | with privacy latch, emergency release required if inward opening door
WCST | Toilet - Staff | FA | CLCN-009 | CORNICE: wall trim fixing | 1
WCST | Toilet - Staff | FFE | FIHR-026 | HOOK: coat | 1
WCST | Toilet - Staff | FFE | FQCW-016 | BIN: waste, general, 20L | 1
WCST | Toilet - Staff | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
WCST | Toilet - Staff | FFE | FIDI-030 | DISPENSER: soap | 1
WCST | Toilet - Staff | FFE | FIDI-036 | DISPENSER: toilet paper | 1
WCST | Toilet - Staff | FFE | FIBM-006 | MIRROR: fixed, glass | 1
WCST | Toilet - Staff | FFE | FQCW-037 | BIN: waste, sanitary | 1
WCST | Toilet - Staff | FFE | HYBA-011 | BASIN: handwash, Type C | 1
WCST | Toilet - Staff | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
WCST | Toilet - Staff | FFE | HYWC-008 | TOILET SUITE: standard | 1
WCST | Toilet - Staff | SE | HYDR-004 | DRAIN: floor waste | 1
WCST | Toilet - Staff | SE | ELBO-015 | SWITCH: light, single | 1
WCST | Toilet - Staff | SE | ITSE-038 | READER: access control, general | 1 | optional, may be provided if room located in a public area