## Room Template Data
Standard Components - Room Templates Properties and Room Template Data
2025-11-12 12:16
No. of Standard Components = 45
Code | Template Name | Standard Component Set | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | 16 | 2700 |  | 8 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1-2 staff | The Consult Room ENT/ Ophthalmology provides the space and facilities for consultation, assessment, examination and minor treatment and observation of patients for acute ENT and Ophthalmology related injury and illness with specialised equipment. | ~ This Standard Component is intended to support minor treatments. Where patients require sedation (including with nitrous oxide) access to a larger procedure room is required. ~ Where this room may also be used for general consultation, specialised equipment for ENT and Ophthalmology should be able to be stored within a lockable cupboard. ~ Eye testing with a visual acuity chart and mirror requires a 6m distance from the chart to the patient when chart is reflected. ~ Observation window within the door(s) to have a cover to support blackout of room for eye testing as determined by clinical services requirements. ~ A eye wash station has been indicated within the room. Disposable eye wash bottles may be considered in conjunction with or instead of a fixed eye wash station depending clinical services requirements and local IPC policies ~ Acoustic treatment to be determined suit clinical services requirements for ENT testing. ~ A second door may be required for staff safety and security; provision will be dependent on local Work Health and Safety (WHS) policies. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ Consideration for the weight capacity of chair, capability to transfer patient from chair to trolley and ability to use with current lifting equipment within the unit to be confirmed at project level to suit local jurisdictional policies and operational service requirements. ~ Ready access to medications, including refrigerated medications, is required. A small medication fridge with temperature monitoring, connected to building management system (BMS), may be provided within the room depending on local operational models for medication management. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical service requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | 12 | 2700 | PBTR-A | 7 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Acute Treatment provides the space and facilities for assessment, treatment and observation of patients with acute conditions and injuries within the Emergency Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station is required for patient observation. The patient bay may be configured with side walls. Inclusion, height and extent of side walls is to be determined at project level to suit the overall department layout and requirements for patient observation. For the requirements of an enclosed bay refer to PTB-E-ACU-E Patient Bay – Emergency, Acute Treatment, Enclosed. ~ A handwash basin is to be provided for every four to six patient bays subject to the overall department layout and ease of access from each patient bay. Close access to a PPE bay shared between patient bays is required. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Electronic medical record (EMR) input may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays and rationalised across the unit, with quantity to suit clinical service requirements and staffing models. Ensure circulation space is sufficient for bedside and bed-end data entry. Parking areas for WOWs and facilities for battery/equipment charging are required to support this model of care. Alternative configurations, such as wall mounted computers (to individual bays or shared between bays) may be provided depending on clinical service requirements, operational models for medical records and local ICT policies. ~ The location of the patient monitor is to be determined to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the monitor bracket. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The clear area required for patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist/complete the patient transfer, is to be considered for transfers to and from beds. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, etc.) should be considered for patient and visitor comfort and convenience. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple patient bays. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable, and patient privacy must be considered when determining window placement. Where high-level windows are provided to the bedhead wall of enclosed patient bays consideration must be given to the location of wall mounted items such as patient monitors. Window coverings must meet IPC requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | 15 | 2700 | PRTR-AS | 2 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Acute Treatment, Enclosed provides an enclosed space and the facilities for assessment, treatment and observation of patients with acute conditions and injuries within the Emergency Unit. | ~ This Standard Component shows the requirements for a general enclosed patient bay for acute emergency treatment. Where it is intended for use as a standard isolation room, an ensuite that is not shared with other patients will be required. Where it is intended for use as a negative pressure isolation room, an ensuite that is not shared and an anteroom will be required. A negative pressure room will also have specific air handling and grille location requirements, and these are to be confirmed at project level to suit local engineering services guidance. For the requirements of an open patient bay refer to PTB-E-ACU-E Patient Bay – Emergency, Acute Treatment ~ The extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation. Provision of integral blinds or extension of the privacy curtain track over the internal window is to be determined to suit requirements for observation and patient privacy. ~ Close access to PPE is required between rooms. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Electronic medical record (EMR) input may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays and rationalised across the unit, with quantity to suit clinical service requirements and staffing models. Ensure circulation space is sufficient for bedside and bed-end data entry. Parking areas for WOWs and facilities for battery/equipment charging are required to support this model of care. Alternative configurations, such as wall mounted computers (to individual bays or shared between bays) may be provided depending on clinical service requirements, operational models for medical records and local ICT policies. ~ The location of the patient monitor is to be determined to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the monitor bracket. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The clear area required for patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist/complete the patient transfer, is to be considered for transfers to and from beds. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, etc.) should be considered for patient and visitor comfort and convenience. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Patient entertainment systems may be considered depending on anticipated length of stay within the patient bay and patient cohort requirements (e.g. paediatrics). Solutions may include individual systems provided to each enclosed patient bay (with integration to patient handset for speaker, and audio/content controls) or portable solutions, such as tablets, brought to patients as needed. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable, and patient privacy must be considered when determining window placement. Where high-level windows are provided to the bedhead wall of enclosed patient bays consideration must be given to the location of wall mounted items such as patient monitors. Window coverings must meet IPC requirements. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | 6.5 | 2700 | PBAT | 2 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay- Emergency, Ambulance Triage provides the space and facilities for initial assessment and physical examination of patients arriving to the Emergency Department via ambulance. | ~ Clear line of sight to the patient in the patient bay from the ambulance write-up is required for patient observation. Direct access from ambulance write-up, triage and the reception/administration area of the Emergency Department is required. ~ A handwash basin is to be provided for every four to six patient bays subject to the overall department layout and ease of access from each patient bay. Close access to a PPE bay shared between patient bays is required. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The clear area required for patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist/complete the patient transfer, is to be considered for transfers to and from beds/ambulance trolleys. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple patient bays. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable, and patient privacy must be considered when determining window placement. Where high-level windows are provided to the bedhead wall of enclosed patient bays consideration must be given to the location of wall mounted. Window coverings must meet IPC requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | 6.5 | 2700 | PBTR-FT | 2 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay- Emergency, Ambulatory Treatment (also known as Fast Track) provides the space and facilities for assessment, treatment and observation of ambulant patients with non-complex (e.g. single system) acute conditions and injuries requiring a short episode of care within the Emergency Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station is required for patient observation. ~ A handwash basin is to be provided for every four to six patient bays subject to the overall department layout and ease of access from each patient bay. Close access to a PPE bay shared between patient bays is required. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The clear area required for patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist/complete the patient transfer, is to be considered for transfers to and from recliners. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ The weight capacity of recliners selected must be considered to suit a wide range of patient requirements. Recliner must have the ability to lay flat. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple patient bays. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable, and patient privacy must be considered when determining window placement. Where high-level windows are provided to the bedhead wall of enclosed patient bays consideration must be given to the location of wall mounted items. Window coverings must meet IPC requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | 10 | 2700 | PBTR-NA | 6 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Non Acute Treatment provides the space and facilities for assessment, treatment and observation of patients with non acute conditions and injuries requiring a short episode of care (less than 24 hours) within the Emergency Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station is required for patient observation. The patient bay may be configured with side walls. Inclusion, height and extent of side walls is to be determined at project level to suit the overall department layout and requirements for patient observation. ~ A handwash basin is to be provided for every four to six patient bays subject to the overall department layout and ease of access from each patient bay. Close access to a PPE bay shared between patient bays is required. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Inclusion of a patient monitor is optional, and provision is dependent on clinical services requirements. If provided, the location of the patient monitor is to be determined to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the monitor bracket. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The clear area required for patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist/complete the patient transfer, is to be considered for transfers to and from beds. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, etc.) should be considered for patient and visitor comfort and convenience. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple patient bays. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable, and patient privacy must be considered when determining window placement. Where high-level windows are provided to the bedhead wall of enclosed patient bays consideration must be given to the location of wall mounted. Window coverings must meet IPC requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | 25 | 3000 | PBTR-R | 7 | 18.08.2025 | 24 hours | 1 patient; 5-8 staff | The Patient Bay - Emergency, Resuscitation provides the space and facilities for assessment, resuscitation, treatment and observation of patients with critical conditions and injuries within the Emergency Unit. | ~ The requirement for body protection or cardiac protection within the Patient Bay - Emergency, Resuscitation, in accordance with AS/NZS 3003, is to be confirmed at project level based on the medical procedures to be undertaken in the space and the level of protection against electric shock afforded in the medical electrical equipment available for these procedures. ~ Clear area is required to both sides of the patient bed to accommodate an ambulance trolley and the staff required to assist/complete patient transfers. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used should be confirmed at project level. Ceiling mounted patient lifting tracks may be considered based on local WHS policies. ~ Use of mobile imaging equipment within the resuscitation bay is to be confirmed at project level. Radiation shielding and signage requirements will need to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ Clinical requirements and models of care for paediatric and neonatal patients are to be confirmed at project level. One resuscitation bay may be assigned for use with paediatric and neonatal patients and hold the required equipment (e.g. resuscitation trolleys and warming equipment) and consumables. Alternatively, equipment and consumables for paediatric and neonatal patients may be stored in a central shared zone to be brought to resuscitation bays as required. ~ Clinical requirements and models of care for trauma services, and their resulting spatial requirements are to be confirmed at project level. ~ The content and configuration of the medical services pendant, including medical gases, power and data, will be dependent on clinical service requirements and medical equipment selection and is to be confirmed at project level. A medical services panel may be provided in lieu of a medical services pendant, depending on models of care and subject to consultation and confirmation with Emergency Department clinicians. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Enclosing the Patient Bay - Emergency, Resuscitation may be considered at project level. Where a bay is enclosed, sliding glazed doors that support observation are advised. ~ Where a resuscitation bay is enclosed for use as a negative pressure isolation room, an anteroom and an ensuite will be required. A negative pressure room will also have specific air handling and grille location requirements, and these are to be confirmed at project level to suit local engineering services guidance. Provision of negative pressure isolation rooms will be dependent on jurisdictional requirements, service level and patient profile and must be confirmed at project level. ~ Direct access from ambulance arrivals or a diagnostic imaging room to a Patient Bay - Emergency, Resuscitation may be provided depending on clinical services requirements and operational models. Provision of an additional point of entry to the resuscitation bay will require coordination with ceiling and wall mounted equipment. ~ Personal protective equipment (PPE) is to be in readily accessible locations between resuscitation bays. Refer to Part D: Infection Prevention and Control for more information. ~ Patient monitoring and display screen requirements (e.g. for patient information, review of medical imaging, emergency decision support tool, etc.) are to be confirmed at project level to suit clinical service requirements and local ICT policies. ~ Provision of cameras for education and/or to enable remote assistance in small services is dependent on clinical services requirements and local ICT policies. ~ Close access is required to linen bays and blanket warming cabinets. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ The type, extent and configuration of storage within the room for stationery and consumables will be dependent on service requirements and operational models. This includes considering the facility’s use of electronic medical records (EMR) as well as remaining paper forms. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
RECP-E | Reception - Emergency | Emergency | 20 | 2700 | REC-E | 7 | 18.08.2025 | 24 hours | 4 staff, with 1-2 additional staff intermittently | The Reception - Emergency provides the space and facilities for receiving patients and visitors and directing them to their destination or to the waiting area of the Emergency Department. The Reception - Emergency also acts as an administrative base for the unit. | ~ Triage - Emergency, Assessment Counters or Triage - Emergency, Assessment Rooms are to be in close proximity to this space. Alternatively, a number of Triage - Emergency, Assessment Counters may be combined with the Reception - Emergency. When Standard Components are combined, the final overall room configuration should include an egress that takes staff behind the secure line of the Emergency Department. ~ Provision of a window for visual access to a Triage - Emergency, Assessment Room (if collocated) may be considered to ensure staff are not isolated in the front of house area. This window may be fixed or an operable sliding type (e.g. to allow passing of items / documents). ~ Provision of a window for visual access to the ambulance entry area (if collocated) may be considered to support efficient registration of patients arriving by ambulance. ~ Clear line of sight to the waiting room is recommended for observation. ~ While oversight of the patient/visitor entry, ambulance entry and waiting room is desirable, it is not always possible and security cameras and feeds are typically required. Display screens for CCTV feeds should be located so they are not viewable by the public. Size and quantity of screens is to be determined to suit security requirements. ~ An intercom and door release buttons linked to the main emergency entry point(s) may be required for access control depending on service requirements. Lockdown alarms and buttons will also be required to suit operational models. ~ This Standard Component shows 2 x counters where patients / visitors are standing and 1 x wheelchair accessible counter. Counters may be provided as standing height or seated height, or a mix of both – with at least one counter to provide wheelchair access. Where only one counter is provided, the configuration must meet requirements for wheelchair access (AS1428.1 or NZS 4121). ~ Security glazing configuration (size of communication slot, size of pass-through aperture for paperwork, support for use of small diagnostic equipment, etc.) is to be determined at project level to suit operational models. ~ Provision of a Hearing Loop and associated items (microphones, signage, etc.) to be determined to suit the configuration of the counter and security glazing. ~ The final location of doors is to be determined to suit overall department layout and minimise risk of staff entrapment. At least one door must provide an egress that takes staff behind the secure line of the Emergency Department. The other door may provide direct access to the waiting room. Provision of access control devices (e.g. proximity card readers) is to be finalised to suit security requirements. ~ Acoustic treatment to be determined suit patient privacy requirements and potential noise transfer from the adjacent waiting area (e.g. use of absorptive finishes to reduce reverberance). ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ The type, extent and configuration of storage within the room for stationery and consumables will be dependent on service requirements and operational models. This includes considering the facility’s use of electronic medical records (EMR) as well as remaining paper forms. ~ Size, type and quantity of waste bins will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | 14 | 2700 |  | 1 | 18.08.2025 | 24 hours | 3 staff, with 1-2 additional staff intermittently | The Staff Station - Emergency, Control Hub provides the space and facilities for a central operational and administrative base of an Emergency Department. It supports the coordination of patient care, patient flow, and ambulance arrivals as well as overseeing central monitoring, security feeds and ambulance phone. These functions may be distributed across the unit depending on operational models, staffing profile, size and complexity of service, etc. | ~ This Standard Component indicates 3 x workstations (providing a base for 1 x doctor-in-charge, 1 x nurse-in-charge and 1 x clerk), with an additional area for central monitoring. The number of workstations required will vary depending on operational models, staffing models and size and complexity of service. ~ One computer workstation has been shown as a downtime workstation with provision of UPS power. Requirements for and location of downtime facilities will need to be confirmed to meet clinical service requirements, operational models for downtime, and local ICT policies. Provision of downtime computers will need to be rationalised across the unit to avoid unnecessary duplication. ~ The Staff Station - Emergency, Control Hub may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security. Requirements are to be determined at project level based on a risk assessment. If provided, security glazing configuration (size of communication slot, size of pass-through aperture for samples/paperwork, etc.) is to be determined at project level to suit clinical service requirements and operational models. Provision of a Hearing Loop and associated items (microphones, signage, etc.) may also be required to suit the configuration of the counter and security glazing. ~ The quantity and type of display screens required to oversee and control the flow of patients throughout the Emergency Department (including ambulance arrivals, emergency patient flow and security feeds) are to be confirmed at project level to suit clinical service requirements and operational models. ~ If overall department planning results in rooms being accessed from behind the Staff Station, additional area for appropriate door circulation clearances will be required. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and work health and safety (WHS) policies and operational service requirements. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Acoustic treatments may be considered to assist with noise transfer from adjacent spaces. All materials must meet local infection prevention and control (IPC) policies. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Placement and visibility of nurse annunciators in adjacent corridors must be considered and coordinated with other ceiling elements such as bulkheads. ~ The type, extent and configuration of storage within the room for stationery and consumables will be dependent on service requirements and operational models. This includes considering the facility’s use of electronic medical records (EMR) as well as remaining paper forms. ~ Size, type and quantity of waste bins will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or in an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | 6.5 | 2700 | TRIAGE-1 | 2 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1 staff | The Triage Assessment Counter - Emergency provides the space and facilities for initial assessment of patients presenting to the Emergency Department. | ~ Multiple Triage Assessment Counters may be arranged together and may be connected to or in close proximity to the Reception - Emergency. When Standard Components are combined, the final overall room configuration should include an egress that takes staff behind the secure line of the Emergency Department. ~ Clear line of sight to the waiting room is recommended for observation when the triage nurse is not seeing a patient. ~ Provision of a window for visual access from Reception - Emergency (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. ~ Direct access is required to a handwash basin. This basin is to be shared between multiple Triage Assessment Counters. Refer to Part D: Infection Prevention and Control for more information. ~ This Standard Component shows a counter where patients would be assessed while standing. Counters may be provided as standing height or seated height, or a mix of both – with at least one counter to provide wheelchair access. Where only one triage counter is provided, the configuration must meet requirements for wheelchair access (AS1428.1 or NZS 4121). ~ Security glazing configuration (size of communication slot, size of pass-through aperture for samples/paperwork, support for use of small diagnostic equipment, etc.) is to be determined at project level to suit clinical service requirements and operational models. ~ Provision of a Hearing Loop and associated items (microphones, signage, etc.) to be determined to suit the configuration of the counter and security glazing. ~ Acoustic treatment to be determined suit patient privacy requirements and potential noise transfer from the adjacent waiting area. Finishes must meet IPC requirements. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Triage journey board/bed flow board should be located nearby to Triage Assessment Counters. ~ Ready access to weighing facilities, including baby weighing, is recommended. ~ Ready access to medications, including refrigerated medications, is required. Depending on model of care, access to a separate refrigerator for icepacks, oral rehydration solutions, etc. may also be required to support waiting room medicine. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical service requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple triage counters. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | 13 | 2700 | TRIAGE-2 | 2 | 18.08.2025 | 24 hours | 1 patient; 1 visitor; 1-2 staff | The Triage Assessment Room - Emergency provides the space and facilities for initial assessment, physical examination and commencement of first aid for patients presenting to the Emergency Department. This room will be located adjacent or in close proximity to the Reception - Emergency. | ~ Clear line of sight to the waiting room is recommended for observation when the triage nurse is not seeing a patient. The extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation. Provision of integral blinds or extension of the privacy curtain track over the internal window is to be determined to suit requirements for observation and patient privacy. ~ Triage - Emergency, Assessment Rooms should be located in close proximity to the Reception - Emergency. ~ Provision of a window for visual access from Reception - Emergency (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. ~ A handwash basin is shown within this Standard Component but may instead be provided nearby and shared between multiple Triage Assessment Rooms. Removal of the handwash basin is subject to consultation with Emergency Department and Infection Prevention and Control (IPC) staff. Refer to Part D: Infection Prevention and Control for more information. ~ Triage journey board/bed flow board should be located nearby to Triage Assessment Rooms. ~ Ready access to weighing facilities, including baby weighing, is recommended. ~ Ready access to medications, including refrigerated medications, is required. Depending on model of care, access to a separate refrigerator for icepacks, oral rehydration solutions, etc. may also be required to support waiting room medicine. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Electronic medical record (EMR) input may be performed on a wall mounted computer workstation, a desk/bench with computer, or a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT policies. ~ The location of the patient monitor is to be determined to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the monitor bracket. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The weight capacity of recliners selected must be considered to suit a wide range of patient requirements. Recliner must have the ability to lay flat. ~ The clear area required for a patient trolley and patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist/complete the patient transfer, is to be considered. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical service requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple triage rooms. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | 25 | 3000 | 1BR-IC | 2 | 12.11.2025 | 24 hours | 1 patient; 1-2 visitors; 1-2 staff (with 4-6 additional staff as required) | The 1 Bed Room - Intensive Care provides an acuity adaptable, enclosed room for a patient requiring intensive medical treatment, nursing care and monitoring for potentially life threatening conditions. | ~ Visual access to the room from a Staff Station is required. ~ In planning of the overall department, room layouts should not be mirrored. Layout are to be "handed", with any specific items being "mirrored" to be confirmed at project level to suit clinical service requirements. ~ The dialysis machine, RO water machine, and the dialysis wall box and its associated large cooling water trap with sealed lid are optional. These items may not be provided in all services or to all bedrooms/bays within a service. Provision is dependent on the clinical service requirements in relation to the delivery of dialysis. The various dialysis therapies will have specific implications for plumbing and pipework in relation to flushing, maintenance and wastewater/effluent handling. See HPU 360 Intensive Care for more information. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door is to be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) isolation rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms refer to ‘AusHFG Part D: Infection Prevention and Control’ and ‘AusHFG Isolation Room- Engineering and Design Requirements’. ~ Overall content and configuration of the medical services pendants is to be confirmed at project level, including type and quantity of medical gases, power and data. The final arrangement will be dependent on clinical service requirements and will vary depending on clinical needs and the selection of mobile vs pendant mounted equipment. Pendants may be provided as one pendant with two arms on a single mounting point, or as single arms on multiple mounting points to increase the reach around the bed space (e.g. when the bed is located as shown or rotated 90 degrees) to support clinical care. Tertiary facilities that act as ECMO retrieval centres or otherwise perform a significant number of ECMO procedures may consider including a pendant located at the foot of the bed to enhance delivery of this treatment by supporting femoral access and connection to the required medical equipment. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from the patient bed. Clear access for bed movement must also be considered when positioning the basin; Refer to Part D Section 4.1.2-5 for more information. ~ Access to natural light and outlook is essential (with non-reflected light and views preferred). To balance this requirement with clinical requirements, the room should provide the ability to provide care with the bed in various orientations. This Standard Component shows the bed oriented vertically on the page with the head of the bed toward the window, supporting quick access by staff to either side from the entry to the room. The bed may be re-oriented to provide views to the window as a patient’s clinical state improves. The reach of the arms of the pendant should support provision of clinical care when the bed is turned 90 degrees. ~ Design to suit local cultural requirements to be considered at project level and supported by community consultation. For more information refer to ‘AusHFG Culturally Sensitive Planning and Design’ and local policies and guidance on culturally responsive design. ~ Requirements for staff notetaking/write-up within the room, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. Configurations such as a ceiling mounted arm at the foot of the bed with a computer and keyboard mounting bracket, or provision of a computer based on a fixed bench as an alternative to a workstation on wheels (WoW), may be considered and assessed at project level. Provision may be dependent on alignment with local ICT strategies, policies and workflows as well as cost impact. ~ A write-up workstation with observation windows is currently indicated directly outside the bed room (area not included calculation for the area of this Standard Component). Provision of this write up area is dependent on models of care for observation/write-up and is to be confirmed at project level. ~ Connection of the patient monitor to a central monitoring system is required. ~ Additional ICT requirements, particularly in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. ~ The configuration of the patient lifter track (i.e. linear track, H-track, pendant mounted, etc.), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) are to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Coordination of the lifter track with room lighting, pendants, examination light, patient entertainment system and any ceiling mounted services is to be carefully considered. ~ Patient entertainment systems may be mounted on the wall or ceiling. Configuration of the patient entertainment (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall or ceiling is required for mounting the patient entertainment system. ~ The ability for slave monitoring (i.e. mirror content from the pendant mounted patient monitor) to be provided through the screen for the patient entertainment system for added visibility of information in emergency situations is to be considered to suit project requirements. Where slave monitoring is not possible through patient entertainment system display screen, and is required to suit models of care, an additional slave display screen and associated services may be required. ~ A wall clock should be visible in all patient rooms. Clocks can support orientation of patients to the time of day, helping to reduce confusion and delirium. However, it has been noted they may also cause distress (e.g. from a sense of time passing too slowly or losing chunks of time). Clock products with the ability to turn off/dim the display may be considered to flexibly respond to patient preferences/needs. The placement of the clock within the room and type of clock provided, including connections to a master clock system, is to be confirmed at a project level. ~ Automation of entry doors is not recommended. As automatic doors are only able to be fully open or closed and are not designed to be kept open. This results in staff feeling isolated from support. ~ A privacy curtain is provided to the glazed door and fixed glazed panel. The use of integral blinds or switchable glass in this area may be considered at project level. In particular, the consideration of provision of switchable glass in lieu of integral blinds throughout the room would be based on an assessment of maintenance, product lifecycle and downtime requirements. For longevity of the product, switchable glass must be turned off (i.e. be opaque) for a period of time each day; this must be considered in relation to where this product is intended to be used to ensure the downtime requirement does not compromise patient observation. ~ Operational models, work health and safety requirements and IPC policies regarding the changing/laundering of privacy curtains is to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient spaces is to suit local security and WHS policies and operational service requirements. ~ Furniture to accommodate a carer within the room is to be confirmed at project level, including consideration of anticipated length of stay, operational models for provision of linen, provision of carer property storage, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use. Fixed joinery items may be considered to provide this function; however, freestanding furniture is recommended where flexibility is required. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ Lighting is to be designed support clinical observation of patients (e.g. accurate colour rendering, appropriate colour temperature, etc.) as per AS/NZS 1680. Consideration of lighting systems that are automated to support circadian rhythms (e.g. through intensity tuning, color tuning, etc.) may be considered at project level. ~ Positioning of light fixtures is to be coordinated with ceiling mounted equipment (e.g. pendant, examination light, patient lifter track, display screen, etc.) to ensure appropriate, uniform illumination of the patient for observation when needed. It is recommended to avoid direct of light fittings over the patient’s head (noting that the bed is movable and may be arranged in different configurations to meet clinical needs and equipment set-up). ~ A dedicated power outlet, clearly separate from outlets for clinical use, is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | 24.5 | 3000 | PBIC | 2 | 12.11.2025 | 24 hours | 1 patient; 1-2 visitors; 1-2 staff (with 4-6 additional staff as required) | The Patient Bay - Intensive Care provides an acuity adaptable, curtained bay for a patient requiring intensive medical treatment, nursing care and monitoring for potentially life threatening conditions. | ~ Visual access to the room from a Staff Station is required. ~ In planning of the overall department, room layouts should not be mirrored. Layout are to be "handed", with any specific items being "mirrored" to be confirmed at project level to suit clinical service requirements. ~ The dialysis machine, RO water machine, and the dialysis wall box and its associated large cooling water trap with sealed lid are optional. These items may not be provided in all services or to all bedrooms/bays within a service. Provision is dependent on the clinical service requirements in relation to the delivery of dialysis. The various dialysis therapies will have specific implications for plumbing and pipework in relation to flushing, maintenance and wastewater/effluent handling. See HPU 360 Intensive Care for more information. ~ Overall content and configuration of the medical services pendants is to be confirmed at project level, including type and quantity of medical gases, power and data. The final arrangement will be dependent on clinical service requirements and will vary depending on clinical needs and the selection of mobile vs pendant mounted equipment. Pendants may be provided as one pendant with two arms on a single mounting point, or as single arms on multiple mounting points to increase the reach around the bed space (e.g. when the bed is located as shown or rotated 90 degrees) to support clinical care. Tertiary facilities that act as ECMO retrieval centres or otherwise perform a significant number of ECMO procedures may consider including a pendant located at the foot of the bed to enhance delivery of this treatment by supporting femoral access and connection to the required medical equipment. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ Access to natural light and outlook is essential (with non-reflected light and views preferred). To balance this requirement with clinical requirements, the room should provide the ability to provide care with the bed in various orientations. This Standard Component shows the bed oriented vertically on the page with the head of the bed toward the window, supporting quick access by staff to either side from the entry to the room. The bed may be re-oriented to provide views to the window as a patient’s clinical state improves. The reach of the arms of the pendant should support provision of clinical care when the bed is turned 90 degrees. ~ Design to suit local cultural requirements to be considered at project level and supported by community consultation. For more information refer to ‘AusHFG Culturally Sensitive Planning and Design’ and local policies and guidance on culturally responsive design. ~ Requirements for staff notetaking/write-up within the room, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. Configurations such as a ceiling mounted arm at the foot of the bed with a computer and keyboard mounting bracket, or provision of a computer based on a fixed bench as an alternative to a workstation on wheels (WoW), may be considered and assessed at project level. Provision may be dependent on alignment with local ICT strategies, policies and workflows as well as cost impact. ~ Connection of the patient monitor to a central monitoring system is required. ~ Additional ICT requirements, particularly in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. ~ The configuration of the patient lifter track (i.e. linear track, H-track, pendant mounted, etc.), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) are to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Coordination of the lifter track with room lighting, pendants, examination light, patient entertainment system and any ceiling mounted services is to be carefully considered. ~ Patient entertainment systems may be mounted on the wall or ceiling. Configuration of the patient entertainment (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall or ceiling is required for mounting the patient entertainment system. ~ The ability for slave monitoring (i.e. mirror content from the pendant mounted patient monitor) to be provided through the screen for the patient entertainment system for added visibility of information in emergency situations is to be considered to suit project requirements. Where slave monitoring is not possible through patient entertainment system display screen, and is required to suit models of care, an additional slave display screen and associated services may be required. ~ A wall clock should be visible in all patient bays. Clocks can support orientation of patients to the time of day, helping to reduce confusion and delirium. However, it has been noted they may also cause distress (e.g. from a sense of time passing too slowly or losing chunks of time). Clock products with the ability to turn off/dim the display may be considered to flexibly respond to patient preferences/needs. The placement of the clock within the room and type of clock provided, including connections to a master clock system, is to be confirmed at a project level. ~ The use of switchable glass in lieu of integral blinds to observation windows may be considered at project level and inclusion would be based on an assessment of maintenance, product lifecycle and downtime requirements. For longevity of the product, switchable glass must be turned off (i.e. be opaque) for a period of time each day; this must be considered in relation to where this product is intended to be used to ensure the downtime requirement does not compromise patient observation. ~ Operational models, work health and safety requirements and IPC policies regarding the changing/laundering of privacy curtains is to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient spaces is to suit local security and WHS policies and operational service requirements. ~ Furniture to accommodate a carer within the room is to be confirmed at project level, including consideration of anticipated length of stay, operational models for provision of linen, provision of carer property storage, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use. Fixed joinery items may be considered to provide this function; however, freestanding furniture is recommended where flexibility is required. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ Lighting is to be designed support clinical observation of patients (e.g. accurate colour rendering, appropriate colour temperature, etc.) as per AS/NZS 1680. Consideration of lighting systems that are automated to support circadian rhythms (e.g. through intensity tuning, color tuning, etc.) may be considered at project level. ~ Positioning of light fixtures is to be coordinated with ceiling mounted equipment (e.g. pendant, examination light, patient lifter track, display screen, etc.) to ensure appropriate, uniform illumination of the patient for observation when needed. It is recommended to avoid direct of light fittings over the patient’s head (noting that the bed is movable and may be arranged in different configurations to meet clinical needs and equipment set-up). ~ A dedicated power outlet, clearly separate from outlets for clinical use, is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
CTIR | CT Imaging Room | Medical Imaging | 45 | 2700 |  | 2 | 15.05.2025 | Up to 24 hours | 1 patient; 2-4 staff | The CT Imaging Room is designed for undertaking Computed Tomography (CT) scanning with direct overview and access from the adjoining CT Control Room. The CT Imaging Room may have a CT Equipment Room immediately adjacent for accommodating supporting power and control equipment. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between imaging unit, the equipment room (if provided) and the control room will be required and must be coordinated with the MME vendor. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room will require sufficient clearance to allow access for a patient on a bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Physiological monitoring on a display screen in the CT Control Room may be provided and would need to be supported with a connection provided within the CT Imaging Room. Provision will depend on service requirements and ICT policies. ~ Acoustic treatment to be considered to manage noise from the imaging device and the adjacent equipment room. All finishes must be meet infection prevention and control requirements. ~ Dimmable light may be considered to support patient comfort. Similarly, feature artwork or back lit panels on the ceiling may be considered above the CT table. ~ Depending on service requirements, general anaesthesia may be administered in this room. This must be confirmed by project teams to ensure appropriate workflows are provided to support this model of care, to confirm the correct building services are provided to ensure patient safety, and to determine medical gas system requirements. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Time tracking requirements (i.e. provision of electric or synchronised clock) is to be confirmed to suit service requirements. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and imaging equipment selection. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | 16 | 2700 | CTCR | 5 | 15.05.2025 | Up to 24 hours | up to 4 staff | The CT Control Room provides the space and equipment for remote control of CT imaging equipment, and amenities for review of images and reporting. Direct visibility of the patient through an observation window and direct access to the imaging room is required. | ~ Cable ducts for services between the imaging unit, the equipment room (if provided) and the control room will be required and must be coordinated with the MME vendor. Additional building services connections and outlets are to be coordinated to suit equipment requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The size, quantity and configuration of computer display screens is to be finalised based on the specific image display and processing task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. Providing flexibility of monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Depending on service requirements and staffing profile, workflow control and advanced processing workstations may be combined into the CT control room to support staffing and efficient patient flow. ~ Additional RIS/PACs/EMR workstations may be required in larger services depending on service requirements and staffing models. ~ Physiological monitoring on a display screen in the CT Control Room may be provided and would need to be supported with a connection provided within the CT Imaging Room. Provision will depend on service requirements and ICT policies. ~ Acoustic treatment to be considered to manage noise from the CT machine and the adjacent equipment room. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
FLUO | Fluoroscopy Room | Medical Imaging | 40 | 2700 |  | 2 | 15.05.2025 | Up to 24 hours | 1 patient; 1-2 staff | The Fluoroscopy Room provides the space and equipment for radiographic imaging and minor interventional procedures involving contrast media. Direct access from an adjacent Fluoroscopy Control Room is required. | ~ Optional general x-ray equipment has been indicated in this Standard Component; this equipment may be provided in this room in addition to fluoroscopy equipment to optimise utilisation of this room in small services and/or provide for redundancy when another machine requires maintenance. Unistrut type ceiling may be required, depending on the equipment to be installed. ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between imaging unit, the equipment room (if provided) and the control room will be required and must be coordinated with the MME vendor. ~ A separate Fluoroscopy Equipment Room for power supply and control elements for the imaging device may be required depending on equipment selected. Where equipment generates a significant amount of heat and noise, separation from the patient area is to be considered. If provided the equipment room should be accessible directly from the imaging room or control room. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ Depending on service requirements, general anaesthesia may be administered in this room. This must be confirmed by project teams to ensure appropriate workflows are provided to support this model of care, to confirm the correct building services are provided to ensure patient safety, and to determine medical gas system requirements. ~ Where the Fluoroscopy service is to include interventional procedures an increase in area is required to accommodate additional staff, trolleys, an anaesthetic machine and other equipment. For interventional procedures, general anaesthesia may be given in this room and the appropriate services and support areas for recovery of patients will be required. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ The room will require sufficient clearance to allow access for a patient on a bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Patient transfer aids such as patient slides and hover mats are to be considered for assisted patient transfers to and from the fluoroscopy table. Final selection of transfer aids will be dependent on service requirements, the needs of the anticipated patient cohort (e.g. for ambulatory services, acute services, etc.), as well as WHS risk assessments/policies. ~ Close access to a patient toilet/shower/change room is required, with direct access from the room preferred to support patients that have changed into gowns. ~ An appropriate patient chair for barium swallows is to be stored outside of room and brought in as required. ~ Acoustic treatment to be considered to manage noise from the imaging device and the adjacent equipment room. All finishes must be meet infection prevention and control requirements. ~ Dimmable light may be considered to support patient comfort. ~ Time tracking requirements (i.e. provision of electric or synchronised clock) is to be confirmed to suit service requirements. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and imaging equipment selection. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | 13 | 2700 | FLUOC | 2 | 15.05.2025 | Up to 24 hours | up to 2 staff | The Fluoroscopy Control Room provides the space and equipment for remote control of fluoroscopy equipment and amenities for the review of images and reporting. Direct visibility of the patient through an observation window and direct access to the imaging room is required. | ~ Cable ducts for services between the imaging device and the control area will be required and must be coordinated with the MME vendor. Additional building services connections and outlets are to be coordinated to suit equipment requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The size, quantity and configuration of computer display screens is to be finalised based on the specific image display and processing task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. Providing flexibility of monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
MAMMO | Mammography Room | Medical Imaging | 18 | 2700 |  | 5 | 15.05.2025 | Up to 24 hours | 1 patient; 1-2 staff | The Mammography Room provides the space and equipment for undertaking diagnostic and screening mammography, as well as performing minor procedures such as biopsies. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between the imaging device and the control area will be required and must be coordinated with the MME vendor. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room will require sufficient clearance to allow access for a patient on a bed. ~ Close access to a patient toilet and change room is required, with direct access from the room being preferred to support patients that have changed into gowns. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
MRI | MRI Room | Medical Imaging | 46 | 2700 | MRIR | 2 | 15.05.2025 | Up to 24 hours | 1 patient; Up to 3 staff | The MRI Imaging Room is designed for undertaking Magnetic Resonance Imaging (MRI) scanning with direct overview from the adjoining MRI Control Room. The MRI Imaging Room must have the MRI Equipment Room immediately adjacent for accommodating supporting power and control equipment. | ~ The MRI Imaging Room is located within Zone IV as set out in the RANZCR MRI Safety Guidelines. ~ Magnetic and Radiofrequency shielding is to be as advised by specialist consultant. ~ The entrance of the MRI Imaging Room must be visible from the MRI Control Room. ~ Appropriate warning signs are required indicating the presence and permanency of a strong magnetic field and identifying items for which entry is prohibited. ~ There shall be a designated site outside the MRI Imaging Room, outside the 0.5m T line and away from the room entry door, for patients to be brought to if requiring emergency treatment. ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between imaging unit, the equipment room and the control room will be required and must be coordinated with the MME vendor. ~ Structural assessment is required to ensure the floor of the MRI Imaging Room and the access route for installation/replacement of equipment will accommodate the weight of the MRI unit. ~ A removable panel to the wall of the MRI Imaging Room is required to allow MRI Unit replacement. ~ Depending on service requirements, general anaesthesia may be administered in this room. This must be confirmed by project teams to ensure appropriate workflows are provided to support this model of care, to confirm the correct building services are provided to ensure patient safety, and to determine medical gas system requirements. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Waveguide ports, also known as penetration panels, are specialised openings in the walls designed to allow the passage of various items like tubing and cables without compromising the magnetic and radiofrequency shielding. Waveguide ports are required from the MRI Control Room to the MRI Imaging Room. Where a service includes administration of anaesthetic, waveguide ports are required from the Anaesthetic Preparation Area to the MRI Imaging Room, along with an observation window with clear view of the patient. ~ All equipment and fittings in the room to be MRI compatible and constructed of non-ferrous material ~ Consideration for the use of multi-parameter MRI compatible monitors and infusion pumps to be confirmed at project level to suit local jurisdictional policies and operational service requirements. Where not provided, a cable port may need to be installed to run clinical leads from outside the imaging room to the patient for continuous monitoring and provision of care. ~ Florescent light fixtures are not permitted in the MRI Imaging Room ~ Temperature and humidity control are required. ~ In planning, room location to be considered in relation to location and movement of metal object outside the MRI Room, such as beds, trolleys, lifts, motor vehicles, trains, trams, AGV’s, transformers and AC cables. Room location must also take into consideration static elements such as steel beams and reinforcement, especially beneath the MRI Unit. ~ Room location to consider building vibration limits that can impact image quality. This may include new building works and potential refurbishments nearby. ~ Smoke detection within the MRI room shall be multi-aspirated detection with the sampling unit located outside of the risk area. Fire sprinklers and pipework shall be of non-ferrous material and suitable for an MRI room. A performance solution shall be completed to address the minimum fire protection requirements of the MRI room. ~ The room will require sufficient clearance to allow access for a patient on an MRI compatible trolley. Trolley movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Patient transfer aids such as patient slides and hover mats are to be considered for assisted patient transfers to and from the MRI table. Final selection of transfer aids will be dependent on service requirements, the needs of the anticipated patient cohort (e.g. for ambulatory services, acute services, etc.), as well as WHS risk assessments/policies. All equipment to be used within the room must be non-ferrous/MRI compatible. ~ Acoustic treatment to be considered to manage noise from the imaging device and the adjacent equipment room. All finishes must be meet infection prevention and control requirements. ~ Dimmable light may be considered to support patient comfort. Similarly, feature artwork on the ceiling may be considered above the MRI table. ~ Time tracking requirements (i.e. provision of electric or synchronised clock) is to be confirmed to suit service requirements. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE
MRI-CTRL | MRI Control Room | Medical Imaging | 14 | 2700 | MRICR | 2 | 15.05.2025 | Up to 24 hours | up to 3 staff | The MRI Control Room provides the space and equipment for remote control of MRI equipment, and the amenities for review of images and reporting. Direct visibility of the patient through an observation window and direct access to the imaging room is required. | ~ The MRI Control Room is located within Zone III (the outer controlled area) as set out in the RANZCR MRI Safety Guidelines. ~ The entrance of the MRI Imaging Room must be visible from the MRI Control Room. ~ Magnetic and Radiofrequency shielding is to be as advised by specialist consultant. ~ Cable ducts for services between the imaging unit, the equipment room and the control room will be required and must be coordinated with the MME vendor. Additional building services connections and outlets are to be coordinated to suit equipment requirements. ~ Waveguide ports, also known as penetration panels, are specialised openings in the walls designed to allow the passage of various items like tubing and cables without compromising the magnetic and radiofrequency shielding. Waveguide ports are required from the MRI Control Room to the MRI Imaging Room. ~ The size, quantity and configuration of computer display screens is to be finalised based on the specific image display and processing task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. Providing flexibility of monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
OPG | OPG Room | Medical Imaging | 19 | 2700 |  | 2 | 15.05.2025 | Up to 24 hours | 1 patient; 1 staff | The OPG Room provides the space and equipment for diagnostic orthopantomogram x-ray imaging which produces panoramic x-rays of the jaw. This Standard Component may be located within a Dental/Oral Health Unit or Medical Imaging Unit. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between the imaging device and the control area will be required and must be coordinated with the MME vendor. ~ The OPG Room is designed to accommodate OPG, Lateral Cephalogram and Cone Beam CT imaging devices with minor adjustments to suit equipment and meet shielding requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
REPR | Reporting Room | Medical Imaging | 12 | 2700 |  | 2 | 15.05.2025 | Up to 24 hours (dependent on unit opening hours) | up to 4 staff | The Reporting Room provides two workspaces with high-performance computers for reviewing of and reporting on patient images from various medical imaging modalities. | ~ The size, quantity and configuration of computer display screens is to be finalised based on reviewing and reporting task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. ~ Display screens shown on desk mounted brackets may be wall mounted. Ensure appropriate in-wall support is provided where display screens are to be wall mounted. Where monitors are wall mounted, interaction with height adjustable desks and distances to services connections must be considered. Flexible monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Emerging technology, and its implications for the space, are to be considered. This may include investigating potential hardware, software and process changes that may, for example, result in the inclusion of additional display screens or CPUs, and the ergonomic, services and construction requirements for accommodating these changes in the future (e.g. supports in the wall for mounting, provision for installing additional services, etc.). ~ A large PACS display screen may be provided to be shared between the two workstations for collaborative image reviewing by teams. Screen sharing capabilities from each workstation would be required to support this. Where this is provided, the room occupancy could be up to 8 staff for limited periods. ~ Type and number of data connections for display screens to be confirmed to suit service and equipment requirements (cat-6 data, HDMI, etc.). ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ It is recommended by RANZCR that the light level of the room is able to be lowered to 20-40 lux. The combination of dimmable general room lighting, dimmable indirect lighting (wall and/or ceiling fixtures), and the use of FF&E items such as back lit monitors and keyboards, as well as any light from external sources (e.g. from corridor through glazing), is to be assessed to ensure the overall quality of light in the room is appropriate. Removal of any potential sources of glare on the computer screens is required to ensure it meets requirements for the performance of reviewing and reporting tasks. Each workstation is to have, to the extent possible, independent control for lighting effecting that workstation. ~ Acoustic wall panels and screens shown are indicative and the acoustic treatment of the room is to be designed to mitigate noise transfer between workstations and from adjacent areas. ~ The heat generated by computer equipment is to be considered when determining the air-conditioning requirements for this room. ~ Depending on the location of the Reporting Room, access control (e.g. via proximity card reader) may be provided to ensure staff only access and inclusion of a fixed duress button that is accessible from both workstations may be required to support staff safety. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for shielding to this room will be determined by the arrangement of the overall department floor plan and proximity of the Reporting Room to any imaging modalities. Radiation shielding requirements are to be assessed and advised by a qualified Radiation Consultant. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
REPW | Reporting Workstation | Medical Imaging | 6 | 2700 |  | 2 | 15.05.2025 | Available 24 hours | 1-2 staff | The Reporting Workstation is a single workspace with a high-performance computer for reviewing of and reporting on patient images from various medical imaging modalities. | ~ This Standard Component is provided as a module that would be multiplied in an open plan arrangement. The number of workstations will be determined at a project level to suit service requirements and staffing profile. Shared elements that are not provided at each workstation, e.g. fixed duress in central location, nurse call annunciators, storage, etc. must be considered when modules are combined. ~ Depending on the overall layout when workstation modules are combined, services may be wall mounted for each individual workstation or soft-wired cable trays may be provided and connected to a central point where power and data are wall mounted or delivered via an umbilical/pole from the ceiling or floor. ~ The size, quantity and configuration of computer display screens is to be finalised based on reviewing and reporting task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. ~ Display screens shown on desk mounted brackets may be wall mounted. Ensure appropriate in-wall support is provided where display screens are to be wall mounted. Where monitors are wall mounted, interaction with height adjustable desks and distances to services connections must be considered. Flexible monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Emerging technology, and its implications for the space, are to be considered. This may include investigating potential hardware, software and process changes that may, for example, result in the inclusion of additional display screens or CPUs, and the ergonomic, services and construction requirements for accommodating these changes in the future (e.g. supports in the wall for mounting, provision for installing additional services, etc.). ~ A large PACS display screen may be provided to be shared between multiple workstations for collaborative image reviewing by teams. Screen sharing capabilities from each workstation would be required to support this. ~ Type and number of data connections for display screens to be confirmed to suit service and equipment requirements (cat-6 data, HDMI, etc.). ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ A modesty panel or an extended acoustic panel to the back of the workstation may be required depending on the layout developed for multiple workstations. ~ It is recommended by RANZCR that the light level of the room is able to be lowered to 20-40 lux. The combination of dimmable general room lighting, dimmable indirect lighting (wall and/or ceiling fixtures), and the use of FF&E items such as back lit monitors and keyboards, as well as any light from external sources (e.g. from corridor through glazing), is to be assessed to ensure the overall quality of light in the room is appropriate. Removal of any potential sources of glare on the computer screens is required to ensure it meets requirements for the performance of reviewing and reporting tasks. Each workstation is to have, to the extent possible, independent control for lighting effecting that workstation. ~ Acoustic wall panels and screens shown are indicative and acoustic treatment of the overall room with multiple workstations is to be considered as a whole when designing to mitigate noise transfer between workstations and from adjacent areas. ~ The heat generated by computer equipment is to be considered when determining the air-conditioning requirements for this room. ~ Storage spaces for staff property and stationery may be allocated separately to be shared between multiple workstations. ~ An annunciator for nurse calls may be located to be shared between multiple workstations depending on overall service requirements. ~ Depending on the location of the room containing Reporting Workstations, access control (e.g. via proximity card reader) may be provided to ensure staff only access and the inclusion of a fixed duress button that is accessible in a central location to all workstations may be required to support staff safety. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for shielding to this room will be determined by the arrangement of the overall department floor plan and proximity of the Reporting Room to imaging modalities. Radiation shielding requirements are to be assessed and advised by a qualified Radiation Consultant. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
ULTR | Ultrasound Room | Medical Imaging | 16 | 2700 |  | 6 | 15.05.2025 | Up to 24 hours | 1 patient; 1 visitor/carer; 1-2 staff | The Ultrasound Room provides the space and amenities for sonographers to perform diagnostic ultrasound imaging on patients. | ~ The room will require sufficient clearance for the ultrasound machine and sonographer to be positioned to either side of the examination trolley and may need to occasionally accommodate a patient on a bed to either be transferred to the examination trolley or have the ultrasound performed while they are in the bed. ~ Close access to a patient toilet and change room is required, with direct access from the room being preferred to support patients that have changed into gowns and require ultrasounds to be performed with a full bladder and then with an empty bladder. ~ A combination of dimmable general room lighting and dimmable indirect lighting (wall and/ or ceiling fixtures) is preferred to obtain appropriate lighting levels and avoid glare on the screen of the ultrasound machine. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | 20 | 2700 |  | 2 | 15.05.2025 | Up to 24 hours | 1 patient; 1 visitor/carer; 1-2 staff | The Ultrasound Room - Procedures provides the space and amenities for sonographers to perform ultrasound imaging in support of clinicians carrying out biopsies and interventional procedures. General anaesthesia will not be administered in this room. | ~ The room will require sufficient clearance for the ultrasound machine and sonographer to be positioned to either side of the examination trolley and may need to occasionally accommodate a patient on a bed to either be transferred to the examination trolley or have the ultrasound/procedure performed while they are in the bed. ~ The ceiling height has been nominally shown at 2700mm, however 3000mm is also acceptable and the height is to be determined based on ceiling mounted equipment and service requirements. ~ Patient transfer aids such as mobile hoists, patient slides and hover mats are to be considered for assisted patient transfers to and from the examination couch where a procedure cannot alternatively be performed on a patient bed. A ceiling mounted hoist may be considered for patient transfers. Final selection of transfer aids will be dependent on service requirements, the needs of the anticipated patient cohort (e.g. for ambulatory services, acute services, etc.), as well as WHS risk assessments/policies. Appropriate ceiling support is required for the provision of a ceiling mounted hoist. ~ A combination of dimmable general room lighting and dimmable indirect lighting (wall and/ or ceiling fixtures) is preferred to obtain appropriate lighting levels and avoid glare on the screen of the ultrasound machine. Additional directional lighting for procedures may be required and is best provided with mobile procedure lights to allow sufficient adjustability to perform tasks while ensuring the ultrasound screen can still be visualised. ~ Sufficient space for pathology staff to bring in a trolley and plug in equipment (e.g. microscopes) is required. ~ Close access to a patient toilet and change room is required, with direct access from the room being preferred to support patients that have changed into gowns and require ultrasounds to be performed with a full bladder and then with an empty bladder. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
XRAY | General X-Ray Room | Medical Imaging | 38 | 3000 | GNXR | 5 | 15.05.2025 | Up to 24 hours | 1 patient; 1-2 staff | The General X-ray Room provides the space and equipment for undertaking general radiographic imaging. This Standard Component may be located within a Medical Imaging Unit or Emergency Unit. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between the patient table, vertical bucky, imaging device and the control area will be required and must be coordinated with the MME vendor. ~ A unistrut type ceiling may be required depending on equipment to be installed. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room may need to accommodate a patient on a bed to either be transferred to the x-ray table or have the x-ray performed while they are on the bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and equipment selection. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | 45 | 3000 |  | 1 | 15.05.2025 | Up to 24 hours | 1 patient; 1-2 staff | The combined General X-ray and OPG Room provides the space and equipment for undertaking general radiographic imaging and orthopantomogram (OPG) imaging. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for x-ray equipment services between the patient table, vertical bucky, imaging device and the control area, and for OPG equipment services between the imaging device and control area will be required and must be coordinated with the MME vendor. ~ A unistrut type ceiling may be required depending on equipment to be installed. ~ The OPG area is designed to accommodate OPG, Lateral Cephalogram and Cone Beam CT imaging devices with minor adjustments to suit equipment and meet shielding requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room may need to accommodate a patient on a bed to either be transferred to the x-ray table or have the x-ray performed while they are on the bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and equipment selection. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | 15 | 2700 | 1BR-MH-A | 6 | 20.08.2025 | 24 hours | 1 patient; 1-2 staff intermittently | The 1 Bed Room - Mental Health, Inboard Ensuite provides a single occupancy bedroom for mental health inpatients. The inboard ensuite layout is used in conjunction with the Ensuite - Mental Health, Inboard (ENS-MH-IN). Alternatively, a nested ensuite layout may be provided (see 1BR-MH-NE). | ~ All fittings and fixtures used in bedrooms must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible bedroom is required to be provided, anti-ligature fittings may require a performance solution to be provided in order for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Window size and minimum sill height are to be confirmed at project level to ensure access to natural daylight and external views from the bed and seating areas within the room. Type of blinds (e.g. integral venetians, integral blackout, etc.) to be confirmed at project level. ~ Doors should support consumer safety, dignity and wellbeing, and be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Project should consider the use of prototypes to confirm solution to address all requirements. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be considered and assessed at project level to suit service requirements. ~ Vision panel is provided for observation checks by staff in consultation with the consumer. Inclusion and size of vision panel to be confirmed to suit service requirements. Controls for integral blind to be provided to both bedroom and corridor sides of the vision panel. Switchable glass may be provided in lieu of integral blind. Placement of vision panel to be confirmed to support requirements for observation. ~ Rooms are to be lockable from the bedroom side, with staff override/master key access from the outside. ~ The ergonomic operation of the door hardware/handles is to be considered as some products are difficult to grip for those with limited hand function. ~ Access control devices, such as card/wristband readers, are optional and provision is dependent on service requirements and operational models. Support for programming and provision of devices is required for implementation. ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Bed may alternatively be provided as a fixed plinth type instead of adjustable height electric bed, depending on service requirements. Clearances around bed to be maintained. ~ Configuration and size of wardrobe is to be confirmed at project level to suit consumer property storage requirements. ~ Provision of safe within the wardrobe joinery is optional and provision is dependent on operational models for property storage. Where provided, shelves will need to be reinforced. ~ Lighting configuration and types (general room, reading, task, night lights, sensory, etc.) to be confirmed at project level. Access and type of switch controls to be determined to suit requirements. ~ Staff assist and emergency call buttons have not been indicated in this Standard Component on the assumption that a portable call and duress devices are provided to staff, and projects must confirm requirements based on operational models. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ The provision of USB outlets is to be determined at project level to suit local jurisdictional requirements. ~ Provision of wall mounted television/patient entertainment systems are to be considered and confirmed at project level to suit local jurisdictional and operational service requirements. If provided, ensure that the screen is recessed or within an enclosure with tamper proof fittings and sufficient ventilation. ~ Provision of radar assist sensors to detect falls and monitor high risk behaviour patterns may be considered at project level to suit local jurisdictional and operational service requirements. ~ Co-ordination of the ceiling services on the ceiling is required. It is ideal to reduce visual 'clutter' over the bed and place services out of reach from raised fixed surfaces (e.g. bench). Removal of emergency warning equipment such as speakers/strobes may be considered via a performance solution to patient rooms to reduce the number of services provided on the ceiling within the room. All fixtures provided (lights, air conditioning grilles, detectors, wireless access points) are to be recessed with tamper proof fittings. ~ Anti-pick caulking is recommended for finishing between surfaces. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | 15 | 2700 | 1BR-MH-C | 6 | 20.08.2025 | 24 hours | 1 patient; 1-2 staff; 1-2 visitors | The 1 Bed Room - Mental Health, Nested Ensuite provides a single occupancy bedroom for mental health inpatients. The nested ensuite layout is used in conjunction with the Ensuite - Mental Health, Nested (ENS-MH-NE). Alternatively, an inboard ensuite layout may be provided (see 1BR-MH-IN). | ~ All fittings and fixtures used in bedrooms must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible bedroom is required to be provided, anti-ligature fittings may require a performance solution to be provided in order for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Window size and minimum sill height are to be confirmed at project level to ensure access to natural daylight and external views from the bed and seating areas within the room. Type of blinds (e.g. integral venetians, integral blackout, etc.) to be confirmed at project level. ~ Doors should support consumer safety, dignity and wellbeing, and be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Project should consider the use of prototypes to confirm solution to address all requirements. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be considered and assessed at project level to suit service requirements. ~ Vision panel is provided for observation checks by staff in consultation with the consumer. Inclusion and size of vision panel to be confirmed to suit service requirements. Controls for integral blind to be provided to both bedroom and corridor sides of the vision panel. Switchable glass may be provided in lieu of integral blind. Placement of vision panel to be confirmed to support requirements for observation. ~ Rooms are to be lockable from the bedroom side, with staff override/master key access from the outside. ~ The ergonomic operation of the door hardware/handles is to be considered as some products are difficult to grip for those with limited hand function. ~ Access control devices, such as card/wristband readers, are optional and provision is dependent on service requirements and operational models. Support for programming and provision of devices is required for implementation. ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Bed may alternatively be provided as a fixed plinth type instead of adjustable height electric bed, depending on service requirements. Clearances around bed to be maintained. ~ Configuration and size of wardrobe is to be confirmed at project level to suit consumer property storage requirements. ~ Provision of safe within the wardrobe joinery is optional and provision is dependent on operational models for property storage. Where provided, shelves will need to be reinforced. ~ Lighting configuration and types (general room, reading, task, night lights, sensory, etc.) to be confirmed at project level. Access and type of switch controls to be determined to suit requirements. ~ Staff assist and emergency call buttons have not been indicated in this Standard Component on the assumption that a portable call and duress devices are provided to staff, and projects must confirm requirements based on operational models. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ The provision of USB outlets is to be determined at project level to suit local jurisdictional requirements. ~ Provision of wall mounted television/patient entertainment systems are to be considered and confirmed at project level to suit local jurisdictional and operational service requirements. If provided, ensure that the screen is recessed or within an enclosure with tamper proof fittings and sufficient ventilation. ~ Provision of radar assist sensors to detect falls and monitor high risk behaviour patterns may be considered at project level to suit local jurisdictional and operational service requirements. ~ Co-ordination of the ceiling services on the ceiling is required. It is ideal to reduce visual 'clutter' over the bed and place services out of reach from raised fixed surfaces (e.g. bench). Removal of emergency warning equipment such as speakers/strobes may be considered via a performance solution to patient rooms to reduce the number of services provided on the ceiling within the room. All fixtures provided (lights, air conditioning grilles, detectors, wireless access points) are to be recessed with tamper proof fittings. ~ Anti-pick caulking is recommended for finishing between surfaces. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | 4 | 2700 |  | 1 | 20.08.2025 | Up to 24 hours | 1-2 intermittently | The Bay - Beverage, Mental Health is provided to allow consumers and support persons access to self-serve facilities for cold drinks and snacks (as determined by operational models for food service), including 24-hour consumer access to chilled water. | ~ The Beverage Bay - Mental Health is typically collocated with consumer dining and lounge areas. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ The temperature of hot water, if made available, should be suitable to prepare tea and coffee, with staff only access to controls. ~ A side approach to the sink for wheelchair access has been shown; front access may be required and is to be determined at project level. ~ It is recommended that joinery is designed will finger pull edges for opening in lieu of fixed handles. Requirements for locks to cupboards and drawers is to be considered to suit service requirements. ~ Locking/restricting access to beverage bays should be avoided where possible, but may be required depending on service requirements. If access to the space is to be restricted, provision of an appropriate locking solution (such as roller shutter) is to be considered. Where roller shutters are provided, robustness must be considered, and design is to meet local work health and safety (WHS) requirements for manual handling of the door curtain. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. ~ Fridge dimensions will vary depending on service requirements and item selection. Adequate clear area must be provided for the fridge to allow for ventilation and full opening of door. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | 5 | 2700 | ENS-MH-A | 5 | 20.08.2025 | 24 hours | 1 patient; 1 staff assisting as required | The Ensuite - Mental Health, Inboard provides a shower, toilet and basin for use by consumers in a mental health inpatient unit. The inboard ensuite layout is used in conjunction with the 1 Bed Room - Mental Health, Inboard Ensuite (1BR-MH-IN). | ~ All fittings and fixtures used in ensuites must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible ensuite is required to be provided, anti-ligature fittings may require a performance solution to be provided in order for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~If provided, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific the mental health environment (i.e. non-acute, acute, intensive care). ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ The ensuite door configuration is to be confirmed at project level to suit service requirements and jurisdictional policies (options include solid door, anti-ligature sliding door, lightweight saloon doors, without door, provision of undercut/overcut). The door in this Standard Component is shown with an angled cut down at top and optional cut at bottom. Alternatively magnetic load release leaf/saloon style doors may be provided. Anti-ligature sliding doors may also be considered based on risk assessment. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof and anti-ligature requirements when used together. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be assessed at project level to suit service requirements. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Coat hooks are shown as optional. Some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered ~ Anti-pick caulking is recommended for finishing between surfaces. ~ Provision of motion sensor lighting or switched lighting to be considered at project level. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | 5 | 2700 | ENS-MH-B | 4 | 20.08.2025 | 24 hours | 1 patient; 1 staff assisting as required | The Ensuite - Mental Health, Nested provides a shower, toilet and basin for use by consumers in a mental health inpatient unit. The nested ensuite layout is used in conjunction with the 1 Bed Room - Mental Health, Nested Ensuite (1BR-MH-NE). | ~ All fittings and fixtures used in ensuites must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible ensuite is required to be provided, anti-ligature fittings may require a performance solution to be provided in order for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~ This Standard Component may be configured to be accessed from a corridor instead of directly from a bedroom. Additional requirements to suit this scenario (e.g. access control, occupancy indicators, etc.) are to be confirmed based on local jurisdictional policies. ~If provided, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific the mental health environment (i.e. non-acute, acute, intensive care). ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ The ensuite door configuration is to be confirmed at project level to suit service requirements and jurisdictional policies (options include solid door, anti-ligature sliding door, lightweight saloon doors, without door, provision of undercut/overcut). The door in this Standard Component is shown with an angled cut down at top and optional cut at bottom. Alternatively magnetic load release leaf/saloon style doors may be provided. Anti-ligature sliding doors may also be considered based on risk assessment. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof and anti-ligature requirements when used together. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be assessed at project level to suit service requirements. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Coat hooks are shown as optional. Some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered ~ Anti-pick caulking is recommended for finishing between surfaces. ~ Provision of motion sensor lighting or switched lighting to be considered at project level. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
INTV-MH | Interview Room - Mental Health | Mental Health | 14 | 2700 | INTF-MH | 2 | 20.08.2025 | Up to 24 hours | up to 6 persons | The Interview Room - Mental Health (may be referred to on projects as a Dialogue Room) provides the space and amenities for interviews, counselling, collaborative care planning and small support network discussions. | ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Inclusion and size of a vision panel to be confirmed to suit service requirements. Privacy film may be applied to the vision panel as required. ~ A second door is required for safety and security. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ Provision of a workstation is dependent on service requirements (e.g. for computer based assessments to be undertaken). Impact on furniture arrangement when workstation is included must be considered to support a positive dynamic between staff and consumers, and encourage participation of consumers as equal partners in care. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Nearby access to a beverage bay or water fountain is recommended. ~ Natural light and external outlook is desirable. Consider placement of windows and room orientation to suit privacy requirements. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
LAUN-MH | Laundry - Mental Health | Mental Health | 6 | 2700 |  | 5 | 20.08.2025 | 8am to 6pm, daily (may vary depending on operational models) | 1 patient; 1 staff | The Laundry - Mental Health provides the space and facilities for consumers to wash and dry clothing while staying in the Mental Health unit. Consumer access to this room and level of staff supervision is to be confirmed at project level to suit service requirements. | ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~All glazing is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ A second door may be required for safety and security; provision will be dependent on service requirements and local Work Health and Safety (WHS) policies. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ This Standard Component shows a bench, laundry sink, and a domestic washing machine and dryer. Ironing facilities are not included, and provision will be based on operational models. The use and storage of clothes airers/drying racks may be considered, and inclusion would be based on a risk assessment and operational models. ~ The selection of finishes in rooms for mental health units is to support provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate and institutional feel. ~ The number of washing machines and dryers required will vary depending on the size of the unit and the operational models for handling patient laundry. Additional space will be required to accommodate any increase in the number of machines. ~ While domestic washing machines and dryers are typically selected, the increased frequency of use compared to residential applications must be considered to ensure robustness and longevity of the selected items. ~ Air conditioning and exhaust requirements are to be confirmed to suit the number of machines and anticipated frequency of use. ~ A residual current device (RCD) has been shown within this room. Requirement for restricted access to RCDs as per AS/NZS 3003 is to be confirmed at project level. Where access needs to be restricted, RCDs may be consolidated in a staff area (e.g. at the staff station). ~ Anti-pick caulking is recommended for finishing between surfaces. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
SECL | Seclusion Room | Mental Health | 14 | 3300 |  | 6 | 20.08.2025 | 24 hours | 1 patient; 1-2 staff intermittently | A Seclusion Room provides for the sole confinement of a distressed or agitated person requiring separation for short periods at any hour of the day or night on an involuntary basis. | ~ The design of the Seclusion room should take into account future flexibility for conversion to another function (e.g. de-escalation room, sensory room, etc.) when services are able to phase out the practice of seclusion through changes in models of care. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as tamper proof and anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, any engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). Jurisdictional requirements may require an increase in the thickness of the glass for a Seclusion Room. ~ Provision of a clear zone outside the seclusion room is required for safe access to the seclusion room for the patient and staff, staff observation, and to support consumer privacy and dignity. An observation window is required with height to suit observation from a seated position. Placement and size to be confirmed to maximise visibility to all areas of the room. A secondary observation window on an adjacent wall may be provided for improved visibility, dependent on layout. ~ Door is to be provided as an outward opening, single leaf (min 1200mm clear opening). Door and door frame to be designed with no sharp edges, and no element of the door hinges to protrude into the seclusion room. Doors must be fitted with robust door hinges, door support structure and electric strike security. Lock requirements to be confirmed at project level to suit local jurisdictional policies and operational service requirements. The door is to be robust and is to be designed so the consumer cannot open it or use any element of it for self-harm. ~ No sharp edges to any doors, door frames, window frames (external and internal) and corners are permitted within this room. All fittings should be flush. Floor, wall and ceiling construction must meet all relevant standards. ~ It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. ~ Direct/close access to a toilet/ensuite may be required to suit jurisdictional policies. Design of door (e.g. hinged, sliding, etc.), access control and observation requirements are to be confirmed to inform inclusion of ensuite. Where direct access to a toilet/ensuite is provided from within the seclusion room, observation windows and an additional door for staff access may be required from the corridor. ~ Direct/close access to an external space may be considered to support future flexibility for use of this space as a de-escalation space. ~ An external outlook is desirable. Access to natural light is required. Controls for integral blinds to external windows to be located in the staff observation area. ~ Provision of a static camera within the seclusion room to connect to staff member in the observation area outside of the room may be considered subject to jurisdictional policies. ~ Robustness of finishes to be suitable for high impact. All finishes to be flush and not provide ligature points or sharp edges. ~ A clock must be located within the area outside the seclusion room and be visible from within the seclusion room (i.e. through the observation window or door vision panel). ~ Acoustic separation and treatment to be considered carefully to minimise disruption to other consumers, along with physical separation from communal (lounge and dining) and sleeping areas. ~ Room lighting must be dimmable and/or have controlled switching to allow for the provision of a low stimulus environment. Provision of lighting to provide sensory input as per therapeutic care plans may be considered based on service requirements and operational models. ~ Ceiling recessed speakers have been shown as optional depending on service requirements. Speaker connection requirements are to be confirmed if included. Music input is to be controlled from device in the staff observation area. Options for controls within the seclusion room to support self-regulation by consumers is subject to jurisdictional policies. ~ The ability for a patient and staff to communicate is required. Where this is not possible through the door, a two-way intercom within the seclusion room may be considered subject to jurisdictional policies. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Air-conditioning vents/grilles are to be flush, and of the type manufactured and marketed as tamper proof and anti-ligature. Local temperature control to the staff observation area may to be considered. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE
STPP | Store - Patient Property | Mental Health | 8 | 2700 |  | 6 | 20.08.2025 | Available 24 hours | 1-2 staff intermittently | The Store - Patient Property provides a secure room for the storage of patient property, including luggage. | ~ The type, extent and configuration of storage solutions within the room, including provision of lockers, will be dependent on service requirements and operational policies for the method of property separation and volume of property to be stored per patient. ~ Maximum and minimum shelf heights are to be confirmed at project level to meet local work health and safety (WHS) policies. Requirements for the storage and restraint of items over certain heights and weights must also be confirmed to ensure safety conditions are able to be met (including for seismic considerations as applicable). ~ This room may be provided in Mental Health Units. Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE
TRBNL | Tribunal Hearing Room | Mental Health | 30 | 2700 |  | 1 | 20.08.2025 | Available 24 hours |  | The Tribunal Hearing Room provides the space and amenities to support the functions of the Mental Health Tribunal, including hearings, confidential discussions and/or counselling between the Tribunal members, the treating team, consumer, and their support person(s) and representative(s). Hearings may be conducted in person or by video conference. The room may also be used for Staff handovers, clinical reviews, education, large family meetings and other activities during times when not in use as a Tribunal Hearing Room. | ~ Requirements for Tribunal Hearing Rooms, including audio visual/teleconferencing requirements, may vary across jurisdictions. Refer to local policies for guidance. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Requirement for the provision of an adjacent observation area is to be confirmed based on service requirements and jurisdictional policies. Where provided, an observation window with integral venetians is to be provided. ~ It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Inclusion and size of a vision panel to be confirmed to suit service requirements. Privacy film may be applied to the vision panel as required. ~ The Tribunal Hearing Room will require safe and effective access and egress. A second door is required. The location and swing of the secondary egress door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ Mobile duress alarms are assumed to be provided. Fixed duress buttons may also be included as appropriate locations throughout the room (e.g. nearby to secondary egress door or mounted to the underside of a table). Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Provision of hearing augmentation may be required depending on audio visual/teleconferencing capabilities and features. Requirements to be confirmed at project level. ~ Furniture selected for the room, such as tables and chairs, should be appropriate for the various activities anticipated to be undertaken in the room as per service requirements. Storage for furniture may be required to support flexible use of room. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Nearby access to a beverage bay and toilet facilities is recommended. ~ Provision of a room booking system (control panel, service requirements) may be considered at project level to suit service requirements and operational models. ~ A high level of acoustic privacy is required for confidentiality. Acoustic treatments and installation to be considered to meet requirements of the mental health environment, including for robustness. ~ Natural light and external outlook are desirable. Consider placement of windows and room orientation to suit privacy requirements and location of camera for video-conferencing to avoid glare. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
WAIT-SEC | Waiting - Secure | Mental Health | 6 | 2700 |  | 6 | 20.08.2025 | 24 hours | up to 4 | The Waiting - Secure is an area provided for visitors to a Mental Health Unit to wait in comfort prior to or during visits with consumers. Visitors will alert staff of their arrival to gain entry to the unit. | ~ The Waiting - Secure is to be located in close proximity to a reception area or staff station. Public amenities should be located in close proximity. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ Consider the location of wi-fi access points to ensure strong coverage is provided for mobile duress functions. ~ Unique considerations for Intensive Care and Child and Adolescent areas are to be confirmed at project level to suit jurisdictional policies ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere and should aim to eliminate an institutional feel. ~ Security provisions for access to the room to be considered to suit local jurisdictional policies and operational services requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
ANAES | Anaesthetic Preparation Room | Operating | 16 | 2700 | ANAE-16 | 2 | 06.05.2025 | Up to 24 hours | 1 patient; 1 parent; up to 3 staff | The Anaesthetic Preparation Room is for the holding and preparation of patients on a bed/trolley prior to their surgical procedure. Depending on operational processes, local, regional or general anaesthesia may be administered in this room or once the patient is taken into the Operating Room. Direct access to the Operating Room is required. | ~ Anaesthetic Preparation Rooms are typically provided to facilitate patient flow and support patient preparation. Provision to be determined during planning with consideration of local operational policies and patient throughput. ~ If serving an Operating Room with cardiac protected power, the Anaesthetic Preparation Room should also have cardiac protected power. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Ready access is required from the Anaesthetic Preparation Room to shared support spaces such as medication fridges and blanket warmer bays. ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Anaesthetic Preparation Room. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Spout and tap placement at the handwashing basin should provide sufficient height to allow washing up to the elbow. The selection of handwashing basins and tapware should be coordinated and approved by clinical staff as a single unit. Type of spout to handwashing basin (i.e. gooseneck, straight, etc.) to be confirmed to suit local infection prevention and control policies. ~ Provision of an articulated examination light or ceiling recessed examination light to be conﬁrmed to suit service requirements. ~ Depending on the use of x-ray equipment within the adjacent Operating Room, radiation shielding may be required to this room and is to be assessed by a Radiation Consultant. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
B-SCRUB | Bay - Scrub | Operating | 4 | 2700 | SCRB-4 | 2 | 06.05.2025 | Up to 24 hours | up to 3 staff | The Bay - Scrub room provides an area and facilities for performing surgical hand antisepsis prior to entering the Operating Room and donning sterile gloves and gowns. Surgical hand antisepsis is performed to substantially reduce the number of micro-organisms on the hands prior to performing any aseptic or surgical procedure. | ~ Number of taps and soap/hand-rub dispensers to be confirmed to suit staffing and service requirements. ~ A minimum of 900mm is required between taps to allow for sufficient space for taps to be used simultaneously. ~ Taps to be non-touch, either operated with sensor activation or elbow levers. ~ Provision of a shelf above the scrub trough to be confirmed at project level to suit service requirements (considering provision of dispensers/holders, cleaning protocols and mounting height provision to suit workplace health and safety policies). ~ Height and type of wall finish to suit local infection prevention and control policies and rigorous cleaning regimes. Provision and height of corner guards as required to provide protection from anticipated mobile equipment movement. ~ Depending on proximity of this room to the Operating room and the use of x-ray equipment during procedures, radiation shielding may be required to some walls of this room and is to be assessed by a Radiation Consultant. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
CLNUP | Clean-Up Room | Operating | 12 | 2700 | CLUP-10 | 2 | 06.05.2025 | Up to 24 hours | 1-2 staff | The Clean-Up Room provides space and amenity for gross decontamination of instruments used in Operating Rooms or Procedure Rooms, storage for cleaning supplies and equipment, as well as storage of waste prior to collection. A Clean-up Room can serve multiple Operating Rooms or Procedure Rooms and should be located nearby to support post procedure processes. | ~ Clearance around the surgical waste management system and docking station, as informed by equipment specifications, is to be maintained at all times. ~ The requirement to provide a door to this room will vary across jurisdictions and is to be confirmed to suit local infection prevention and control policies. ~ Number, size and type of bins, including sharps, to be confirmed to suit waste management policies and service requirements. ~ Provision of cleaner's sink to be confirmed to suit operational policies and service requirements. ~ Type of spout provided to handwashing basin (i.e. gooseneck, straight, etc.) to be confirmed to meet local infection prevention and control policies. ~ Backflow prevention device requirements to be confirmed for all hydraulic fixtures to suit service requirements. ~ Air-conditioning and exhaust requirements to be confirmed to suit service requirements (i.e. extent of gross decontamination of instruments occurring within this room), operational processes (e.g. frequency of waste removal), and equipment selection. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
ENPR | Procedure Room - Endoscopy | Operating | 45 | 3000 |  | 2 | 06.05.2025 | 24 hours | 1 patient; 5-8 staff | A Procedure Room - Endoscopy provides an aseptic environment in which to carry out endoscopic procedures on a patient under local, regional or general anaesthetic. The Procedure Room may be used for specialties including ENT, urology, endoscopy and other similar procedures. The Procedure Room may have direct access to a reprocessing area and, in some models, a sterile stock. | ~ The minimum critical dimension centred on the procedure zone is 6400mm clear to ensure adequate space for the procedure, circulation and equipment storage. ~ Isolated power supply is required individually to each medical services pendant, together with its associated line isolation and overload monitors. ~ Location and quantity of RCD outlets to suit overall electrical service provision and is to be confirmed by the project to suit local engineering services guidelines/policies. ~ If the room is used for Bronchoscopy procedures, negative pressure air conditioning and direct exhaust to roof is required. ~ If the room is used for bronchoscopy procedures, negative pressure air conditioning and direct exhaust to outside is required. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ If laser equipment is to be used, ‘laser in use’ warning lights are required outside all entry doors to the room. ~ If x-ray equipment is to be used, ‘x-ray in use’ warning lights are required outside all entry doors to the room. Radiation shielding will also be required and is to be assessed by a Radiation Consultant. ~ Automated doors with motion or elbow activation are provided to the Procedure Room - Endoscopy from the corridor and reprocessing areas. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Height of doors to be confirmed to suit the movement of mobile equipment such as mobile imaging devices. ~ If external windows are provided, they are to be double glazed with integral venetian blinds (with either manual or automated controls). ~ Room lights to be dimmable. Lighting control to room rights, warning signs, and operating lights to be coordinated within the room and an appropriate lighting control panel to be provided to functional requirements. ~ Configuration of services pendant (horizontal or vertical) to suit services requirements. Accessories (e.g. shelves, drawers, rails, etc.) are optional and can be selected to suit service and equipment requirements. Services allocations are indicative - type and number of services on the pendant to suit service requirements ~ Services pendant arms to have an adequate reach to be moved out of the way to allow for adequate room for movement of a patient trolley and mobile equipment. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
EXIT | Exit Bay | Operating | 11 | 2700 |  | 1 | 06.05.2025 | Up to 24 hours | staff intermittently | The Exit Bay provides area for patients and equipment to be moved from the Operating Room at the conclusion of a procedure. The Exit Bay provides space for the temporary storage of a patient bed while a procedure is in progress. Direct access to the Operating Room is required. | ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Exit Bay. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ A cupboard for digital operating room (DOR) ICT/AV equipment is indicated on the layout but is not included in the overall area measurement and the contents of the ICT/AV cupboard are not captured in this Standard Component. The size of the ICT/AV cupboard will vary depending on equipment to be accommodated. Rather than being located individually to each Operating Room, ICT/AV equipment may be consolidated in a room that is shared between a number of Operating Rooms as appropriate to suit equipment installation, testing and maintenance requirements. ~ Medical gas valve boxes for each Operating Room are typically located in the associated Exit Bay. Size and location of the medical gas valve box zone, to be kept clear of all other services, is to be confirmed by a medical gas engineering consultant. ~ Height and type of wall finish to suit local infection prevention and control policies and rigorous cleaning regimes. Provision and height of corner guards as required to provide protection from anticipated mobile equipment movement. ~ Depending on the use of x-ray equipment within the adjacent Operating Room, radiation shielding may be required to this room and is to be assessed by a Radiation Consultant. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
OR-GEN | Operating Room - General | Operating | 60 | 3000 | ORGN | 7 | 06.05.2025 | Up to 24 hours | 1 patient; 5-12 staff | An Operating Room provides an aseptic environment in which to carry out surgical procedures on a patient under local, regional or general anaesthetic. The Operating Room - General is flexibly used for various surgical procedures that require complex and large equipment. This Standard Component may be adapted for Operating Rooms dedicated to different specialties, for example neurosurgery, orthopaedics, cardiac surgery, obstetrics and trauma. | ~ The minimum critical dimension centred on the sterile zone is 7400mm clear to ensure adequate space within the sterile zone (min 3400mm wide), circulation zone (min 1000mm wide) and equipment zone (min 1000mm wide). ~ Where the Operating Room is intended to be used for cardiothoracic procedures and for some forms of hybrid operating theatres, cardiac electrical protection is required. ~ Isolated power supply is required individually to each medical services pendant, together with its associated line isolation and overload monitors. ~ Location and quantity of RCD outlets to suit overall electrical service provision and is to be confirmed by the project to suit local engineering services guidelines/policies. ~ A wall mounted medical services panel has been indicated as optional and may be provided for theatres where, for example, obstetric procedures are intended to be undertaken and the additional panel provides access to services for an infant away from the operating table if required. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ If laser equipment is to be used, ‘laser in use’ warning lights are required outside all entry doors to the room. ~ If x-ray equipment is to be used, ‘x-ray in use’ warning lights are required outside all entry doors to the room. Radiation shielding will also be required and is to be assessed by a Radiation Consultant. ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Anaesthetic Preparation Room and Exit Bay. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Height of doors to be confirmed to suit the movement of mobile equipment such as mobile imaging devices. ~ If external windows are provided, they are to be double glazed with integral venetian blinds (with either manual or automated controls). ~ Room lights to be dimmable. Lighting control to room rights, warning signs, and operating lights to be coordinated within the room and an appropriate lighting control panel to be provided to functional requirements. ~ Configuration of services pendant (horizontal or vertical) to suit services requirements. Accessories (e.g. shelves, drawers, rails, etc.) are optional and can be selected to suit service and equipment requirements. Services allocations are indicative - type and number of services on the pendant to suit service requirements ~ Services pendant arms to have an adequate reach to be moved out of the way to allow for adequate room for movement of a patient trolley and mobile equipment. ~ If not dedicated for use in a particular Operating Room, microscope(s) should be located in a nearby equipment bay in close proximity for flexible use between Operating Rooms. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
STSS | Store - Sterile Stock | Operating | 40 | 2700 | STSS-20 | 6 | 06.05.2025 | 24 hours |  | A room with an aseptic environment for storage and holding of sterile stock for use in the Operating Suite or other acute treatment areas. | ~ This Standard Component assumes direct access to Operating Rooms and that it is multiplied as a module to serve Operating Rooms that are planned in a row – with the end of the room to be enclosed once modules are combined. Where sterile stock storage is centralised and transported through corridors to Operating Rooms. This room is to be enclosed (size, FF&E, and services increased according to number of Operating Rooms to be served), and door arrangements are to be adjusted to suit. ~ Sterile stock is to be stored in shelving compliant with AS 5369, this may be provided as either static units, single mobile units and/or as a compactus. If a compactus is to be used, depending on the product selected and the materials it is made from, structural engineering advice may need to be sought to ensure adequate load-bearing capacity and potential deﬂection eﬀect on walls, doors, etc. ~ Storage solutions must support consumable items to be stored separately (i.e. in different shelving units) to reusable medical devices (RMDs) as per AS 5369. ~ The size, quantity and type of storage solution will vary to suit service requirements. Additional shelving units require an approximate area of 1m2 per unit (assumes 900W x 400D x 2100H unit with space in front to access). ~ Storage height to be limited to 520mm min below ceiling to meet ﬁre sprinkler system requirements within AS 2118.1. ~ A clearance of 1100mm is recommended to be provided for circulation spaces within Store – Sterile Stock to facilitate movement of trolleys and staff. ~ Conﬁguration of computer workstations (bench mounted, wall mounted on articulated brackets, and/or workstations on wheels) is to be conﬁrmed to suit service requirements and local ICT policies. ~ Provision of automated doors to access this store from the corridor to be confirmed by project to suit service requirements and operational policies. ~ Light ﬁxtures to be sealed and flush-mounted to minimise opportunity for dust accumulation and ensure ease of cleaning. ~ Depending on proximity of this room to the Operating room and the use of x-ray equipment during procedures, radiation shielding may be required to some walls of this room and is to be assessed by a Radiation Consultant. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-11-12 12:16
No. of Standard Components = 46
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to both sides
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | provision of cover as required to control light for eye examinations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | optional; secondary egress; provision dependent on local WHS policies; provision of cover as required to control light for eye examinations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to eye chart display screen
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 2 | 1 |  | low height, for examination chair
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, for patient monitor
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional; required for medication fridge if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to articulated examination light
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | over desk for portable devices
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to slit lamp and retinal camera
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to articulated examination light; controls may be integral to light fitting
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | optional
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 3 |  | optional; required if patient monitor is provided; with cable and accessory management items as required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin and eye wash station or an inset section of non-slip vinyl is required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart; solution to suit clinical service requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to eye washing station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYSH-106 | STATION: emergency, safety, eye wash, wall mounted | 1 | 1 |  | disposable eye wash bottles may be considered in conjunction with or instead of a fixed eye wash station depending clinical services requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin, 1 to eye washing station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; placement to ensure visibility along paths of travel
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | 1 to entry door, 1 to examination chair; placement to support quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 to entry door, 1 to examination chair; may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional; required for medication fridge if provided; for temperature monitoring BMS connection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; required if patient monitor provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to slit lamp and retinal camera
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | optional; provision dependent on clinical service requirements and local ICT policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | for storage of consumables and specialist equipment
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | optional; to shelving over computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 3 |  | optional; over computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | LIFX-113 | LIGHT: examination, articulated, ceiling mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMBE-176 | CHAIR: examination, electric | 1 | 1 |  | suitable for ENT examinations and minor treatments
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-391 | DISPLAY SCREEN: eye examination, testing chart | 1 | 1 |  | align with mirror; locate to achieve 6m distance to patient when chart is reflected
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-396 | MIRROR: eye examination, to testing chart display screen | 1 | 1 |  | align with eye chart; locate to achieve 6m distance to patient when chart is reflected
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-401 | DEVICE: eye examination, slit lamp | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-406 | DEVICE: eye examination, retinal camera | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMPH-021 | FRIDGE: medication/ vaccine, 150L nom, single door under bench | 1 | 3 |  | optional; with temperature monitoring; provision is dependent on operational models for medication management.
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 3 |  | optional; provision and configuration of monitoring to be confirmed to suit clinical services requirements
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin and eye wash station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use/charging of portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for patient bed and mattress
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to write-up area
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to recessed examination light
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | optional; may be provided in PPE bay shared between multiple bays
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with cable and accessory management items as required
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of bed; placement to ensure visibility along paths of travel
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | shared between multiple patient bays with quantity to be rationalised across the unit to suit clinical service requirements, operational models for electronic medical records, local ICT policies and staffing models
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | optional; may be provided in lieu of WOW; provision dependent on clinical service requirements, operational model for electronic medical records and local ICT policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of monitoring to be confirmed to suit clinical services requirements
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | provide if patient bay is configured with side walls
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 1 | 1 | Wall Finish 3 | provide if patient bay is configured with side walls; to be coordinated with adjacent wall protection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to ensuite side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to patient room side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to both sides
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | optional; provision dependent on frame material and finish
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 3 | optional; provision dependent on frame material and finish
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | CLTI-023.02 | CEILING: drop-in tiles, anti-microbial, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | optional; to ensuite if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 3 | optional; to anteroom if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | DOHI-144.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use/charging of portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for patient bed and mattress
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to write-up area
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to recessed examination light
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | collocate with alcohol-based hand rub
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with cable and accessory management items as required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; placement to ensure visibility along paths of travel
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | shared between multiple patient bays with quantity to be rationalised across the unit to suit clinical service requirements, operational models for electronic medical records, local ICT policies and staffing models
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | optional; may be provided in lieu of WOW; provision dependent on clinical service requirements, operational model for electronic medical records and local ICT policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1 |  | optional; if room is to be used for negative pressure isolation, supply and exhaust air locations are to be determined to suit local engineering services guidance
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of monitoring to be confirmed to suit clinical services requirements
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | WIFX-057.04 | WINDOW: fixed, internal, double glazed, sill at 900H, with integral blind | 1 | 1 | Internal - Window 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation; provision of integral blinds or extension of the privacy curtain track over window is to be determined to suit requirements for observation and patient privacy
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to recessed examination light
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | shared between multiple ambulance triage bays; size to suit clinical requirements, operational models for frequency of disposal and local IPC policies
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 3 |  | shared between multiple ambulance triage bays; size to suit clinical requirements, operational models for frequency of disposal and local IPC policies
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 3 |  | shared between multiple ambulance triage bays; size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of stretcher; placement to ensure visibility along paths of travel
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | optional; provision dependent on clinical services requirements and models of care
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | optional; required if medical air outlet is provided
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for patient recliner
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use/charging of portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to recessed examination light
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be wall mounted or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | sharps bin may alternatively wall mounted or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of recliner; placement to ensure visibility along paths of travel
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | must have ability to lay flat
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional; to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use/charging of portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for patient bed and mattress
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to recessed examination light
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | optional; may be provided in PPE bay shared between multiple bays
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1 |  | PES configuration will be dependent on operational models and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | optional; required if patient monitor is provided; with cable and accessory management items as required
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of bed; placement to ensure visibility along paths of travel
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | PES configuration will be dependent on operational models and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | with control to patient handset
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements; may alternatively be provided on a mobile stand to be shared across the unit and brought to the patient bay as required
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | optional; provision and configuration of monitoring to be confirmed to suit clinical services requirements
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | provide if patient bay is configured with side walls
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-NAC | Patient Bay - Emergency, Non Acute Treatment | Emergency | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 1 | 1 | Wall Finish 3 | provide if patient bay is configured with side walls; to be coordinated with adjacent wall protection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional; required for medication fridge if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to slave patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 8 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 4 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | optional; required if patient information and diagnostic imaging display provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | optional; required if decision support tool display screen provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 6 | 1 |  | 2 over bench; 4 distributed across the room for medical equipment
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELPR-034 | PANEL: UPS status indicator, on services pendant | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 4 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | for general room lights; to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | provided in addition to PPE bays shared between resuscitation bays
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | provided in addition to PPE bays shared between resuscitation bays
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-104 | BRACKET: suction bottle, pendant mounted | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-113 | BRACKET: sharps bin, trolley mounted | 1 | 1 |  | to resuscitation trolley
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 2 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 3 |  | optional; required if decision support tool display screen provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional; required if patient information and diagnostic imaging display provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-403 | BRACKET: patient monitor, fixed, ceiling mounted | 1 | 1 |  | to slave patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-411 | BRACKET: patient monitor, articulated, pendant mounted | 1 | 1 | Pendant 1 - Arm 1 | connected to ceiling mounted slave patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-423 | BRACKET: ventilator, pendant mounted | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIRT-091 | TRACK: IV, ceiling mounted | 1 | 1 |  | to be coordinated with procedure light and medical services pendant; may alternatively be provided as pendant mounted or mobile IV poles
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 8 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQSM-057 | PEDESTAL: mobile, 840H nominal, 4 equal wire basket drawers | 4 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | to resuscitation trolley; size to suit clinical requirements, local IPC policies and operational models for frequency of disposal
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITBU-436 | CONTROL PANEL: time and elapsed time, synchronised slave clock | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-135 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services pendant | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on services pendant | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on services pendant | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 | Pendant 1 - Arm 1 | with holder and cable management items as required
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 3 |  | optional; for decision support tool display; provision and placement dependent on clinical service requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 1 |  | optional; for patient information and diagnostic imaging display; provision and placement dependent on clinical service requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 2 | 3 |  | optional; for education and/or to enable remote assistance in small services; provision, quantity and placement is dependent on clinical services requirements and local ICT policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to slave patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-014 | OUTLET: data, single RJ45, on services pendant | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional; required for medication fridge if provided; for temperature monitoring BMS connection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; required if decision support tool display screen provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; required if patient information and diagnostic imaging display provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-034 | OUTLET: data, triple RJ45, on services pendant | 2 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | to write-up workstation; provision of articulated wall or bench mounted brackets may be considered to support ergonomics and orientation of workstation for visibility of patient.
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional; to drug safe if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-211 | BENCH SUPPORT: bracket | 3 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | LIFX-131 | LIGHT: procedure, articulated, ceiling mounted | 1 | 1 |  | to be coordinated with ceiling mounted IV track and medical services pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on services pendant | 1 | 1 | Pendant 1 - Arm 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-051 | OUTLET: scavenge, on services pendant | 1 | 1 | Pendant 1 - Arm 1 | optional; required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-061 | OUTLET: suction, on services pendant | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMGE-039 | HANGER: IV, for ceiling track | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-191 | CANNISTER: suction bottle | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-235 | DIAGNOSTIC SET: otoscope and ophthalmoscope, pendant mounted | 1 | 1 | Pendant 1 - Arm 1 | configuration of equipment to be confirmed to suit clinical services requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-296 | DEVICE: pump, syringe | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | to resuscitation trolley
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-032 | TROLLEY: resuscitation, paediatric | 1 | 3 |  | optional; may alternatively be provided in a shared area between resuscitation bays or in a dedicated resuscitation bay
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMHA-051 | DEVICE: ventilator, adult | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 3 |  | optional, may be provided in a shared area between resuscitation bays; provision in bay will be dependent on operational models for medication management
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPH-021 | FRIDGE: medication/ vaccine, 150L nom, single door under bench | 1 | 3 |  | optional, may be provided in a shared area between resuscitation bays; provision in bay will be dependent on operational models for medication management
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 | Pendant 1 - Arm 1 | configuration of monitoring to be confirmed to suit clinical services requirements; connected to ceiling mounted slave patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPM-051 | MONITOR: patient, slave | 1 | 1 |  | display from patient monitor on medical services pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMSP-102 | MEDICAL SERVICES PENDANT: single arm, vertical services head | 1 | 1 | Pendant 1 | content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-053 | TROLLEY: airway/intubation, 750W x 490D x 900H nom | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-092 | TROLLEY: procedure, 600W x 490D x 900H nom | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLPR-006.06 | WALL PROTECTION: corner guards, to 2100 AFFL | 1 | 1 | Wall Finish 4
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLPR-046.03 | WALL PROTECTION: crash rail, to 900 AFFL | 1 | 1 | Wall Protection
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
RECP-E | Reception - Emergency | Emergency | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | over counter and reception workstations
RECP-E | Reception - Emergency | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
RECP-E | Reception - Emergency | Emergency | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 3 | to bulkhead
RECP-E | Reception - Emergency | Emergency | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
RECP-E | Reception - Emergency | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | to waiting area; may be located to provide direct access to the waiting area or behind department entry doors
RECP-E | Reception - Emergency | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 2 | to department treatment areas
RECP-E | Reception - Emergency | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | optional; required if patient flow display screen is provided
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to workstation on wheels (WOW) for roaming clerk(s)
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to printer
RECP-E | Reception - Emergency | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 6 | 1 |  | 2 to each reception workstation
RECP-E | Reception - Emergency | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 3 | 1 |  | to printers
RECP-E | Reception - Emergency | Emergency | SER | ELGP-261 | GPO: double, UPS, wall mounted | 1 | 1 |  | provided for downtime connection
RECP-E | Reception - Emergency | Emergency | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | to general room lighting
RECP-E | Reception - Emergency | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
RECP-E | Reception - Emergency | Emergency | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional; provide if display screen for patient flow information is provided
RECP-E | Reception - Emergency | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
RECP-E | Reception - Emergency | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
RECP-E | Reception - Emergency | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQGE-122 | CLOCK: digital display, battery operated | 1 | 1 |  | type of clock to be confirmed at project level
RECP-E | Reception - Emergency | Emergency | FFE | FQGE-226 | DEVICE: electronic funds transfer at point of sale (EFTPOS) | 1 | 1 |  | optional; provision dependent on operational models
RECP-E | Reception - Emergency | Emergency | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQSM-081 | PEDESTAL: mobile, 660H nominal, 1 drawer and 1 printer shelf | 3 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
RECP-E | Reception - Emergency | Emergency | FFE | ITBU-470 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall mounted | 1 | 1 |  | type of clock and connection to the master clock system is to be confirmed at a project level based on clinical service requirements
RECP-E | Reception - Emergency | Emergency | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional; provision dependent on operational models and clinical service requirements
RECP-E | Reception - Emergency | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to clock; an additional power outlet may be required if power over ethernet (PoE) is not supported by the clock hardware
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 1 |  | to printers
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; required if patient flow display screen is provided
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 4 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | for roaming clerk(s)
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-311 | PRINTER: desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-316 | PRINTER: labels, small, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITSE-062 | BUTTON: security, duress, fixed, surface mounted | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 3 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | SER | ITSE-091 | BUTTON: security, perimeter lockdown, wall mounted | 1 | 1 |  | to external entry doors and department entry doors; requirements to be confirmed on security requirements and operational policies for unit lockdown
RECP-E | Reception - Emergency | Emergency | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | type and size of screen to be confirmed to suit security requirements
RECP-E | Reception - Emergency | Emergency | SER | ITSE-186 | INTERCOM: audio-visual, slave, wall mounted | 1 | 1 |  | connected to intercom at external entry doors and security observation room
RECP-E | Reception - Emergency | Emergency | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
RECP-E | Reception - Emergency | Emergency | SER | ITSE-298 | BUTTON: door release, remote activation, surface mounted | 2 | 1 |  | 1 to each reception workstation; to open external entry doors
RECP-E | Reception - Emergency | Emergency | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | to reception desk
RECP-E | Reception - Emergency | Emergency | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to shelving unit
RECP-E | Reception - Emergency | Emergency | FFE | JORS-001 | JOINERY UNIT: reception desk | 2 | 1 |  | 1 counter to be wheelchair accessible
RECP-E | Reception - Emergency | Emergency | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 3 | 1 |  | configuration of communication slot and pass through aperture to be confirmed at project level to suit clinical service requirements and operational models
RECP-E | Reception - Emergency | Emergency | FFE | JOSH-001 | SHELF UNIT: tall, adjustable shelves | 1 | 1 |  | type, extent and configuration of storage for stationery and consumables will be dependent on service requirements, local ICT policies for EMR
RECP-E | Reception - Emergency | Emergency | D+W | WIFX-008.01 | WINDOW: fixed, internal, single glazed, sill at 1050H | 1 | 3 | Internal - Window 1 | optional; may be provided to ambulance entry if collocated, to support efficient registration of patients
RECP-E | Reception - Emergency | Emergency | D+W | WIOP-009 | WINDOW: operable, sliding, internal, single glazed, sill at 1200H | 1 | 3 | Internal - Window 2 | optional; may be provided to triage assessment room if collocated, to ensure staff are not isolated in the front of house area; dependent on staffing models and WHS policies
RECP-E | Reception - Emergency | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
RECP-E | Reception - Emergency | Emergency | FIN | WLPT-031 | SCREEN: privacy divider | 1 | 1 | Wall Finish 2 | as required between reception counters to support private conversations; material to be confirmed to balance privacy requirements with waiting room observation
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-211 | GPO: double, joinery mounted | 3 | 1 |  | 1 to each workstation; over bench for portable device charging
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1 |  | to label printers
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to multi-function device
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional; provide if display screen for ambulance arrivals information is provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | optional; provide if display screen for patient flow information is provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 1 | 1 |  | 2 to each workstation (except downtime workstation), 2 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-271 | GPO: double, UPS, joinery mounted | 2 | 1 |  | to downtime computer workstation
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | to task lighting
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELSW-011 | SWITCH PLATE: light, multi-gang | 1 | 3 |  | optional; may be provided for control of general lighting in nearby areas; provision dependent on overall department layout
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FIBM-021 | WHITEBOARD: fixed, magnetic, integral to joinery | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional; provide if display screen for ambulance arrivals information is provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional; provide if display screen for patient flow information is provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FIHR-333 | BRACKET: television/AV system display screen, single, fixed, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 3 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQWS-212 | BIN: confidential document, secure, 30L | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITBU-470 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall mounted | 1 | 1 |  | type of clock and connection to the master clock system is to be confirmed at a project level based on clinical service requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional; for ambulance arrivals information; provision dependent on operational models and clinical service requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional; for emergency department patient flow information; provision dependent on operational models and clinical service requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to clock; an additional power outlet may be required if power over ethernet (PoE) is not supported by the clock hardware
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to ambulance phone
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to multi-function device
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; provide if display screen for ambulance arrivals information is provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; provide if display screen for patient flow information is provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | 1 |  | 1 to each workstation, 1 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 3 | 1 |  | 1 to each workstation
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | ambulance phone
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 3 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-302 | MULTIFUNCTION DEVICE: printer/copier/scanner/fax, floor standing | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-316 | PRINTER: labels, small, desktop | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | type and size of screen to be confirmed to suit security requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | JOBE-251 | CAP: cable access | 4 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | JORS-021 | JOINERY UNIT: staff station | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | JORS-071 | SECURITY GLAZING: to staff station | 3 | 1 |  | optional; provision to be determined at project level based on risk assessment; may include communication slots and pass through apertures; final configuration to be confirmed at project level to suit clinical service requirements and operational models.
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | LIFX-108 | LIGHT: task, integral to joinery | 4 | 1 |  | 1 to each workstation, 1 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | MMPM-092 | MONITOR: central patient monitoring station, dual display screens | 1 | 1 |  | quantity and size of display screens to suit patient monitoring requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | to be coordinated with adjacent wall protection
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLBK-012 | BULKHEAD: flush set, acoustic | 1 | 1 | Ceiling Finish 2
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 3 | to bulkhead
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 2 | 1 |  | to printers
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 1 | 1 |  | to computer workstation
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | FQSM-081 | PEDESTAL: mobile, 660H nominal, 1 drawer and 1 printer shelf | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 1 | 1 |  | to printers
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 1 | 1 |  | to computer workstation
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | provision of adjustable desk mounted brackets for computer screens may be considered at project level
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | on pedestal under bench
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | located discreetly
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | to entry for emergency department treatment areas
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | 1 to computer workstation; 1 to label printer
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | counters may be provided as standing height or seated height, or a mix of both; at least one counter to provide wheelchair access as per AS1428.1 or NZS 4121.
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 1 | 1 |  | configuration of communication slot and pass through aperture to be confirmed at project level to suit clinical service requirements and operational models
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | WLPT-031 | SCREEN: privacy divider | 1 | 1 | Wall Finish 2 | as required between triage counters to support private conversations; material to be confirmed to balance privacy requirements with waiting room observation
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | entry from waiting room; extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to all-in-one computer and display screen
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for patient recliner
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | optional; required if recessed examination light provided
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with cable and accessory management items as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 2 | 1 |  | 1 to entry door from waiting room; 1 to treatment areas within the unit
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to window facing waiting room; provision of integral blinds or provision of privacy curtain track is to be determined to suit requirements for observation and patient privacy
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | 1 to entry door from waiting room; 1 to treatment areas within the unit
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 3 |  | to window facing waiting room; provision of integral blinds or provision of privacy curtain track is to be determined to suit requirements for observation and patient privacy
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart; solution to suit clinical service requirements and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry from treatment areas; placement to ensure visibility along paths of travel
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to all-in-one computer and display screen
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | write-up function may be provided by a wall mounted computer workstation, a desk/bench with computer, or a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1 |  | to all-in-one computer and display screen
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | optional; provision dependent on clinical service requirements; light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | must have ability to lay flat
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of monitoring to be confirmed to suit clinical services requirements
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMTR-062 | TROLLEY: dressing, 600W x 490D x 900H nom | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation; provision of integral blinds or provision of privacy curtain track is to be determined to suit requirements for observation and patient privacy
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLPR-006.06 | WALL PROTECTION: corner guards, to 2100 AFFL | 1 | 1 | Wall Finish 4
TRIAGE-RM (TEST) | Triage - Emergency, Assessment Room (TEST) | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
TRIAGE-RM (TEST) | Triage - Emergency, Assessment Room (TEST) | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
TRIAGE-RM (TEST) | Triage - Emergency, Assessment Room (TEST) | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | entry from waiting room; extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | DOSL-073.02 | DOOR: sliding, 1 leaf, 900 clear opening, fully glazed, framed with mid-rail, with integral blinds | 1 | 1 | Internal - Door 2 | optional, to support patient observation; provision is to be confirmed at project level and will be dependent on staffing models and local IPC policies/risk assessment
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | DOST-074.01 | DOOR: stacking, 2 leaves + 1 fixed panel, 1800 clear opening, fully glazed, framed with mid-rail | 1 | 1 | Internal - Door 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | to staff write-up if provided outside room
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 2 | to staff write-up if provided outside room
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 3 | to adjacent room to support patient observation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIOP-256.02 | WINDOW: operable, jockey sash, external, double glazed, sill at 750H, with integral blind | 1 | 1 | External - Window 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 2 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQBS-282 | RECLINER: visitor, clinical areas, fold out bed | 1 | 1 |  | selected item to suit clinical services requirements, operational models and local IPC policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | a privacy curtain is provided to the glazed door and panel and staff workstation at the front of the room; the use of integral blinds or switchable glass may be considered at project level based on assessment of maintenance, product lifecycle and downtime requirements
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 6 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | ability to turn off/dim display to be considered to respond to patient preferences/needs
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | ability for screen to duplicate patient monitoring information for added visibility in emergency situations to be considered
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | alternative arrangement on ceiling mounted articulated arm may be considered at project level to suit clinical requirements and operational models for write-up and observation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | LIFX-113 | LIGHT: examination, articulated, ceiling mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-116 | BED: patient, electric, with mattress, intensive care | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMGE-381 | MACHINE: dialysis | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMGE-386 | PROCESSOR: water treatment, dialysis, reverse osmosis (RO), mobile | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMHA-051 | DEVICE: ventilator, adult | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMTR-002.02 | TROLLEY: stainless steel, 600W x 490D x 900H nom, 2 tier | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMTR-092 | TROLLEY: procedure, 600W x 490D x 900H nom | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLPR-006.02 | WALL PROTECTION: corner guards, to 1050 AFFL | 1 | 1 | Wall Protection | coordinated with adjacent wall protection and observation windows
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 8 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 8 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Pendant 1 - Arm 2 | to night lights; to be coordinated with switch on wall
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELSW-021 | SWITCH: light, dimmer | 1 | 1 | Pendant 1 - Arm 2 | to general room lights; to be coordinated with switch on wall
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, pendant mounted | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, pendant mounted | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | FIHR-411 | BRACKET: patient monitor, articulated, pendant mounted | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-135 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services pendant | 1 | 1 | Pendant 1 - Arm 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on services pendant | 1 | 1 | Pendant 1 - Arm 1 | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on services pendant | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on services pendant | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on services pendant | 1 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on services pendant | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on services pendant | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, pendant mounted | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, pendant mounted | 1 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMSP-212 | MEDICAL SERVICES PENDANT: double arm, vertical services head / vertical services head | 1 | 1 | Pendant 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMSP-212.01 | SERVICES HEAD: vertical, to arm 1 | 1 | 1 | Pendant 1 - Arm 1 | shown to patient's right (services head R); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMSP-212.02 | SERVICES HEAD: vertical, to arm 2 | 1 | 1 | Pendant 1 - Arm 2 | shown to patient's left (services head L); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to patient lifter track
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to carer's area
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 2 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | to UPS outlets on medical services pendant
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 2 | 1 |  | quantity and type to be confirmed to suit final power provisions
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | to night lights; to be coordinated with switch on medical services pendant
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights; to be coordinated with switch on medical services pendant
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-104 | TUNDISH: in wall, with viewing panel | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-157 | TRAP: cooling pit, with sealed lid | 1 | 1 |  | optional, required if dialysis wall box is provided; to support cooling of wastewater from heat disinfection of dialysis machines and portable RO machines
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYGE-082 | WALL BOX: renal dialysis, integral tundish, with 1 water supply connection and 2 drain connections | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | LIFX-151 | LIGHT: night, wall mounted | 2 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to patient lifter track
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 8 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 8 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to carer's area
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 2 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | to UPS outlets on medical services pendant
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 2 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | to night lights; to be coordinated with switch on medical services pendant
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Pendant 1 - Arm 2 | to night lights; to be coordinated with switch on wall
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights; to be coordinated with switch on medical services pendant
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELSW-021 | SWITCH: light, dimmer | 1 | 1 | Pendant 1 - Arm 2 | to general room lights; to be coordinated with switch on wall
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, pendant mounted | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, pendant mounted | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 2 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | FIHR-411 | BRACKET: patient monitor, articulated, pendant mounted | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQBS-282 | RECLINER: visitor, clinical areas, fold out bed | 1 | 1 |  | selected item to suit clinical services requirements, operational models and local IPC policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | a privacy curtain is provided to the glazed door and panel and staff workstation at the front of the room; the use of integral blinds or switchable glass may be considered at project level based on assessment of maintenance, product lifecycle and downtime requirements
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 6 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-104 | TUNDISH: in wall, with viewing panel | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-157 | TRAP: cooling pit, with sealed lid | 1 | 1 |  | optional, required if dialysis wall box is provided; to support cooling of wastewater from heat disinfection of dialysis machines and portable RO machines
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYGE-082 | WALL BOX: renal dialysis, integral tundish, with 1 water supply connection and 2 drain connections | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | ability to turn off/dim display to be considered to respond to patient preferences/needs
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-135 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services pendant | 1 | 1 | Pendant 1 - Arm 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on services pendant | 1 | 1 | Pendant 1 - Arm 1 | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on services pendant | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | ability for screen to duplicate patient monitoring information for added visibility in emergency situations to be considered
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on services pendant | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on services pendant | 1 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | alternative arrangement on ceiling mounted articulated arm may be considered at project level to suit clinical requirements and operational models for write-up and observation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | LIFX-113 | LIGHT: examination, articulated, ceiling mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | LIFX-151 | LIGHT: night, wall mounted | 2 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on services pendant | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on services pendant | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-116 | BED: patient, electric, with mattress, intensive care | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMGE-019 | CHAIR: patient | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, pendant mounted | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, pendant mounted | 1 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMGE-381 | MACHINE: dialysis | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMGE-386 | PROCESSOR: water treatment, dialysis, reverse osmosis (RO), mobile | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMHA-051 | DEVICE: ventilator, adult | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMSP-212 | MEDICAL SERVICES PENDANT: double arm, vertical services head / vertical services head | 1 | 1 | Pendant 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMSP-212.01 | SERVICES HEAD: vertical, to arm 1 | 1 | 1 | Pendant 1 - Arm 1 | shown to patient's right (services head R); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMSP-212.02 | SERVICES HEAD: vertical, to arm 2 | 1 | 1 | Pendant 1 - Arm 2 | shown to patient's left (services head L); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMTR-002.02 | TROLLEY: stainless steel, 600W x 490D x 900H nom, 2 tier | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMTR-092 | TROLLEY: procedure, 600W x 490D x 900H nom | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | to adjacent room to support patient observation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 2 | to adjacent room to support patient observation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | D+W | WIOP-256.02 | WINDOW: operable, jockey sash, external, double glazed, sill at 750H, with integral blind | 1 | 1 | External - Window 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | WLPR-006.02 | WALL PROTECTION: corner guards, to 1050 AFFL | 1 | 1 | Wall Protection | coordinated with adjacent wall protection
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to equipment room side
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to imaging room side
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
CTIR | CT Imaging Room | Medical Imaging | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | to support bed movement, delayed action closing
CTIR | CT Imaging Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
CTIR | CT Imaging Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
CTIR | CT Imaging Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
CTIR | CT Imaging Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to CT equipment room if provided
CTIR | CT Imaging Room | Medical Imaging | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 2 | to control room (see CTIR-CTRL)
CTIR | CT Imaging Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | from corridor
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to clock
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional - to patient observation camera, in front of gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient observation camera, behind gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | for foot pedal recharge
CTIR | CT Imaging Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 6 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | ELGP-176 | GPO: single, UPS, on services panel | 2 | 1 | Panel 1 | extent of UPS to be confirmed to suit service and equipment requirements
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to patient monitor on mobile stand
CTIR | CT Imaging Room | Medical Imaging | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1
CTIR | CT Imaging Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control room entry
CTIR | CT Imaging Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FIHR-030 | HOOK: equipment, patient slide | 1 | 1 |  | optional - provide if patient slide required
CTIR | CT Imaging Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
CTIR | CT Imaging Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
CTIR | CT Imaging Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
CTIR | CT Imaging Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FQSN-214 | SHELVING UNIT: floor standing, adjustable shelves, 600D x 900W x 2100H nominal | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
CTIR | CT Imaging Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above medical services panel
CTIR | CT Imaging Room | Medical Imaging | MSP | ITCL-353 | DISPLAY SCREEN: patient treatment information, touch screen | 1 | 1 | Pendant 1
CTIR | CT Imaging Room | Medical Imaging | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | optional - in front of gantry, location as required for adequate patient observation
CTIR | CT Imaging Room | Medical Imaging | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | location as required for adequate patient observation
CTIR | CT Imaging Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to patient observation camera, in front of gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to patient observation camera, behind gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor on mobile stand
CTIR | CT Imaging Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | D+W | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 | Internal - Door 1 | to support bed movement
CTIR | CT Imaging Room | Medical Imaging | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
CTIR | CT Imaging Room | Medical Imaging | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 5 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
CTIR | CT Imaging Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | outside all room entries, to automatically turn on when modality is in use
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MICT-001 | IMAGING DEVICE: computerised tomography (CT), gantry | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MICT-006 | TABLE: patient, computerised tomography (CT) | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MIGE-053 | INJECTOR: contrast, ceiling mounted | 1 | 1 |  | mobile and table mounted injectors are also acceptable
CTIR | CT Imaging Room | Medical Imaging | FFE | MMBE-031 | SLIDE: patient transfer | 1 | 1 |  | optional - patient transfer methods and equipment to meet local WHS policies
CTIR | CT Imaging Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MMPM-012 | MONITOR: patient, medium acuity, on stand, mobile | 1 | 1 |  | may be wall mounted
CTIR | CT Imaging Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MMSP-104 | MEDICAL SERVICES PENDANT: single arm, display screen | 1 | 1 | Pendant 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1 |  | for phantoms
CTIR | CT Imaging Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room (see CTIR-CTRL)
CTIR | CT Imaging Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
CTIR | CT Imaging Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
CTIR | CT Imaging Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to control room side
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to imaging room side
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side, extent dependent on movement of beds and mobile equipment
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | optional - staff entry from corridor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 1 | to imaging room
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | to slave patient monitor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | optional - to display screen for physiological monitoring if provided
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 7 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | to control console, extent of UPS to be confirmed to suit service and equipment requirements
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to each door
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to CT control CPU, 1 to PACS CPU
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to display/processing workstation
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-341 | BRACKET: television/AV system display screen, single, articulated, wall mounted | 1 | 1 |  | optional - to display screen for physiological monitoring if provided
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | to slave patient monitor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 3 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | optional - for anaesthetic assist
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITCL-381 | DISPLAY SCREEN: patient observation | 1 | 1 |  | optional - for physiological monitoring
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to slave patient monitor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to display screen for physiological monitoring if provided
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | display/processing workstation, on dual arm bracket
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-311 | PRINTER: desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-341 | SCANNER: desktop, document, flatbed, desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOBE-071 | BENCH: 800D, laminate | 1 | 1 |  | bench height to be confirmed; adjustable height desks may be considered depending on WHS policies and coordination with services and observation window
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOBE-211 | BENCH SUPPORT: bracket | 3 | 1 |  | leg support is also acceptable
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 4 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | to imaging room entries, to automatically turn on when modality is in use
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MICT-011 | CONTROL CONSOLE: computerised tomography (CT), dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MICT-016 | COMPUTER: computerised tomography (CT), central processing unit (CPU) | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to ensuite side
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to imaging room side
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | to support bed movement, delayed action closing
FLUO | Fluoroscopy Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
FLUO | Fluoroscopy Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
FLUO | Fluoroscopy Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
FLUO | Fluoroscopy Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to accessible ensuite if provided
FLUO | Fluoroscopy Room | Medical Imaging | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 2 | to control room (see FLUO-CTRL)
FLUO | Fluoroscopy Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | from corridor
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to clock
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-176 | GPO: single, UPS, on services panel | 1 | 1 | Panel 1 | optional - extent of UPS to be confirmed to suit service and equipment requirements
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | 1 to bench, 1 to workstation on wheels, 1 under control room window
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 1 | optional - provide if UPS required
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 3 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | optional - to accessible ensuite if provided
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control room entry
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-136 | HOLDER: PPE, lead goggles, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
FLUO | Fluoroscopy Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
FLUO | Fluoroscopy Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
FLUO | Fluoroscopy Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 2 | inset section of contrasting colour to fluoroscopy machine area, indicates clear zone as mobile items may be crushed when the table is tilted
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | optional - for patient access to fluoroscopy table, provision dependent on adjustable height range of table
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-237 | BIN: clinical waste, 120L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | to bench
FLUO | Fluoroscopy Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to sink
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYTP-182 | TAPWARE: sink, tap set, wall mounted, lever handles | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin, 1 to sink
FLUO | Fluoroscopy Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin, 1 to sink
FLUO | Fluoroscopy Room | Medical Imaging | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above medical services panel
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to patient monitor
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | 1 to bench, 1 to workstation on wheels
FLUO | Fluoroscopy Room | Medical Imaging | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | D+W | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 | Internal - Door 1 | to support bed movement
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | for storage of positioning aids
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 2 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | outside all room entries, to automatically turn on when modality is in use
FLUO | Fluoroscopy Room | Medical Imaging | FFE | LIPO-021 | LIGHT: examination, articulated, mobile | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-001 | IMAGING DEVICE: fluoroscopy/screening, with patient table | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-012 | CONTROL CONSOLE: fluoroscopy/screening, single display screen, control unit, mobile | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-023 | BOARD: electrical distribution (EDB), fluoroscopy/screening | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-025 | GENERATOR: fluoroscopy/screening | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-051 | RACK: fluoroscopy/screening, table mounted shields, mobile | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MIFL-062 | DISPLAY SCREEN: fluoroscopy/screening, pendant mounted | 2 | 1 | Pendant 1 | quantity dependent on equipment set up
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MIGE-005 | SHIELD: radiation, pendant mounted | 1 | 1 | Pendant 2
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIGE-051 | INJECTOR: contrast, pedestal | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-001 | IMAGING DEVICE: general x-ray, tube head, ceiling suspended | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-005 | IMAGING DEVICE: general x-ray, wall bucky, fixed | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-023 | BOARD: electrical distribution (EDB), general x-ray | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-025 | GENERATOR: general x-ray, floor standing | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-026 | GENERATOR: general x-ray, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | wall mounted, may be on mobile stand
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-105 | MEDICAL SERVICES PENDANT: single arm, dual display screens | 1 | 1 | Pendant 1 | on ceiling track, reach of arm to ensure screen positioning is possible to both sides of the table
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-108 | MEDICAL SERVICES PENDANT: single arm, radiation shield | 1 | 1 | Pendant 2
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MMTR-063 | TROLLEY: dressing, 750W x 490D x 900H nom | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room (see FLUO-CTRL)
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to bench
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to control room side
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to imaging room side
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side, extent dependent on movement of beds and mobile equipment
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | optional - staff entry from corridor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | DOHI-013.05 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass | 1 | 1 | Internal - Door 1 | to imaging room
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | over desk for portable devices
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to contrast warmer
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | to control console, extent of UPS to be confirmed to suit service and equipment requirements
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to each door, 1 optional - to staff entry if provided
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to display/processing workstation
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 1 | 1 |  | for communication with patient, may be integral to control unit provided by MME vendor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | display/processing workstation, on dual arm bracket
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | bench height to be confirmed; adjustable height desks may be considered depending on WHS policies and coordination with services and observation window
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-211 | BENCH SUPPORT: bracket | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | leg support is also acceptable
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | to imaging room entry, to automatically turn on when modality is in use
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MIFL-011 | CONTROL CONSOLE: fluoroscopy/screening, dual display screens, keyboard and mouse, control unit, desktop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MIFL-016 | COMPUTER: fluoroscopy/screening, central processing unit (CPU) | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
MAMMO | Mammography Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
MAMMO | Mammography Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
MAMMO | Mammography Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
MAMMO | Mammography Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
MAMMO | Mammography Room | Medical Imaging | D+W | DOHI-104.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, shielded | 1 | 1 | Internal - Door 1
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
MAMMO | Mammography Room | Medical Imaging | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to imaging equipment and control console
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1 |  | to workstation
MAMMO | Mammography Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lighting
MAMMO | Mammography Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
MAMMO | Mammography Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
MAMMO | Mammography Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
MAMMO | Mammography Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
MAMMO | Mammography Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FQSM-057 | PEDESTAL: mobile, 840H nominal, 4 equal wire basket drawers | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
MAMMO | Mammography Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
MAMMO | Mammography Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
MAMMO | Mammography Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above services panel
MAMMO | Mammography Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | to imaging equipment and control console
MAMMO | Mammography Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to workstation
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | to workstation
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
MAMMO | Mammography Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies
MAMMO | Mammography Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
MAMMO | Mammography Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | outside all room entries, to automatically turn on when modality is in use
MAMMO | Mammography Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | FFE | MIMM-001 | IMAGING DEVICE: mammography | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MIMM-011 | CONTROL CONSOLE: mammography, single display screen, keyboard and mouse, control unit | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MIMM-046 | RACK: mammography paddles, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MMBE-086 | CHAIR: patient | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
MAMMO | Mammography Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
MAMMO | Mammography Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
MAMMO | Mammography Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
MRI | MRI Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | MRI compatible, to both sides of door
MRI | MRI Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
MRI | MRI Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
MRI | MRI Room | Medical Imaging | FIN | CLFS-012 | CEILING: flush set, suspended, acoustic | 1 | 1 | Ceiling Finish 1 | ceiling tiles are also acceptable, grid must be MRI compatable
MRI | MRI Room | Medical Imaging | D+W | DOSP-141 | DOOR: hinged, 1 leaf, 1200 clear opening, radio frequency shielding, MRI imaging room | 1 | 1 | Internal - Door 1
MRI | MRI Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to clock
MRI | MRI Room | Medical Imaging | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | optional - to laser positioning light if provided
MRI | MRI Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 2 | 1 |  | to patient observation cameras
MRI | MRI Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 2 | 1 |  | optional - 1 to slave patient monitor, 1 to FMRI monitor
MRI | MRI Room | Medical Imaging | MSP | ELGP-176 | GPO: single, UPS, on services panel | 2 | 1 | Panel 1 | extent of UPS to be confirmed to suit service and equipment requirements
MRI | MRI Room | Medical Imaging | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
MRI | MRI Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1 | 1 to emergency power circuit, 1 to UPS circuit
MRI | MRI Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lighting
MRI | MRI Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
MRI | MRI Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | FIHR-341 | BRACKET: television/AV system display screen, single, articulated, wall mounted | 1 | 1 |  | optional - to functional MRI display screen if provided, MRI compatible
MRI | MRI Room | Medical Imaging | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | optional - to slave patient monitor if provided, MRI compatible
MRI | MRI Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Finish 1
MRI | MRI Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Skirting
MRI | MRI Room | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | ITAV-151 | SPEAKER: AV system, ceiling mounted | 1 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | ITBU-443 | CLOCK: analogue display, electric, MRI compatible, wall mounted | 1 | 1
MRI | MRI Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above medical services panel
MRI | MRI Room | Medical Imaging | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 1 |  | optional - for functional MRI, MRI compatible
MRI | MRI Room | Medical Imaging | FFE | ITCL-437 | CAMERA: patient observation, MRI compatible, wall mounted | 2 | 1
MRI | MRI Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | to patient observation cameras
MRI | MRI Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | optional - 1 to slave patient monitor, 1 to FMRI monitor
MRI | MRI Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
MRI | MRI Room | Medical Imaging | FFE | JOCU-021 | CUPBOARD: tall, double door | 5 | 1 |  | all materials and hardware to be MRI compatible
MRI | MRI Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1
MRI | MRI Room | Medical Imaging | SER | MEGE-061 | SENSOR: oxygen depletion | 1 | 1 |  | connection to BMS to be confirmed by project
MRI | MRI Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
MRI | MRI Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
MRI | MRI Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | MIGE-052 | INJECTOR: contrast, MRI compatible, pedestal | 1 | 1
MRI | MRI Room | Medical Imaging | FFE | MIMR-001 | IMAGING DEVICE: MRI, gantry | 1 | 1 |  | refer to manufacturer's requirements for quench pipes and other associated equipment
MRI | MRI Room | Medical Imaging | FFE | MIMR-006 | TABLE: patient, MRI | 1 | 1 |  | mobile table with electronic docking capability, detachable table also acceptable, use of detachable table may negate need for additional MRI compatible patient transport trolley
MRI | MRI Room | Medical Imaging | FFE | MIMR-036 | PIPE: quench, MRI | 1 | 1 |  | installed to manufacturer's specifications with minimal bends
MRI | MRI Room | Medical Imaging | FFE | MIMR-041 | TROLLEY: patient, transport, MRI compatible | 1 | 1
MRI | MRI Room | Medical Imaging | FFE | MIMR-046 | MACHINE: anaesthetic, MRI compatible | 1 | 1
MRI | MRI Room | Medical Imaging | FIN | MIMR-101 | CABIN: radio frequency shielding, faraday cage, MRI | 1 | 1 | Wall Finish 4
MRI | MRI Room | Medical Imaging | FIN | MIMR-112 | ACCESS PANEL: penetration, waveguide port, MRI | 1 | 1 | Wall Finish 3 | 2 to control room, 2 to anaesthetic preparation area
MRI | MRI Room | Medical Imaging | D+W | MIMR-121 | BARRIER: MRI, retractable belt, wall mounted | 1 | 1 | Internal - Door 1
MRI | MRI Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave | 1 | 1 |  | optional - depending on service requirements, MRI compatible
MRI | MRI Room | Medical Imaging | FFE | MMRA-042 | LASER: patient positioning, radiotherapy, overhead, MRI compatible | 1 | 1 |  | optional - as required for radiotherapy planning
MRI | MRI Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | D+W | WIFX-008.04 | WINDOW: fixed, internal, single glazed, sill at 1050H, radio frequency shielding | 1 | 1 | Internal - Window 1 | for observation from control room (see MRI-CTRL)
MRI | MRI Room | Medical Imaging | D+W | WIFX-008.04 | WINDOW: fixed, internal, single glazed, sill at 1050H, radio frequency shielding | 1 | 1 | Internal - Window 2 | for observation from anaesthetic preparation area
MRI | MRI Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
MRI | MRI Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2
MRI-CTRL | MRI Control Room | Medical Imaging | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional - to CCTV display screen if provided
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | to slave patient monitor
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to printer
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 6 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | to control console, extent of UPS to be confirmed to suit service and equipment requirements
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to each door
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat | 2 | 1 |  | optional
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to MRI control CPU, 1 to PACS CPU
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to display/processing workstation
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-341 | BRACKET: television/AV system display screen, single, articulated, wall mounted | 1 | 1 |  | optional - to CCTV display screen if provided
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | to slave patient monitor
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 3 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQSN-341 | LOCKER: floor standing, 4 door | 2 | 1 |  | optional
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | HYGE-351 | CONTROL PANEL: water pump, cooling | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | vendor supplied sound system
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | optional - for anaesthetic assist
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITCL-381 | DISPLAY SCREEN: patient observation | 1 | 1 |  | optional - for physiological monitoring
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to slave patient monitor
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to CCTV display screen if provided
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 3 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | display/processing workstation, on dual arm bracket
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-311 | PRINTER: desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | optional
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | bench height to be confirmed; adjustable height desks may be considered depending on WHS policies and coordination with services and observation window
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | leg support is also acceptable
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | leg support is also acceptable
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 3 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | MEGE-081 | ALARM: oxygen depletion | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIMR-011 | CONTROL CONSOLE: MRI, dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIMR-016 | COMPUTER: MRI, central processing unit (CPU) | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIMR-032 | BUTTON: quench, MRI | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | MIMR-112 | ACCESS PANEL: penetration, waveguide port, MRI | 1 | 1 | Wall Finish 2
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | D+W | WIFX-008.04 | WINDOW: fixed, internal, single glazed, sill at 1050H, radio frequency shielding | 1 | 1 | Internal - Window 1 | for observation of patient from control room
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
OPG | OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
OPG | OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides of door
OPG | OPG Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
OPG | OPG Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
OPG | OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | to imaging area
OPG | OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | to control workstation area
OPG | OPG Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
OPG | OPG Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
OPG | OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to imaging equipment
OPG | OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation
OPG | OPG Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | to imaging device
OPG | OPG Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lighting
OPG | OPG Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
OPG | OPG Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
OPG | OPG Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
OPG | OPG Room | Medical Imaging | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | optional - for storage of consumables and PPE items to meet service requirements
OPG | OPG Room | Medical Imaging | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | located close to medical services panel
OPG | OPG Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
OPG | OPG Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
OPG | OPG Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
OPG | OPG Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
OPG | OPG Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
OPG | OPG Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
OPG | OPG Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | as required for imaging device connection to remote activation panel
OPG | OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to imaging device
OPG | OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation
OPG | OPG Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-341 | SCANNER: desktop, document, flatbed, desktop | 1 | 1
OPG | OPG Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | 1 close to imaging device, 1 to control workstation area
OPG | OPG Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 2 | 1
OPG | OPG Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | outside all room entries, to automatically turn on when modality is in use
OPG | OPG Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | FFE | MIOC-001 | IMAGING DEVICE: orthopantomogram (OPG) | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | MIOC-011 | CONTROL PANEL: orthopantomogram (OPG), remote activation | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
OPG | OPG Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | FFE | MMTR-001.02 | TROLLEY: stainless steel, 490W x 490D x 900H nom, 2 tier | 1 | 1
OPG | OPG Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
OPG | OPG Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
OPG | OPG Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
REPR | Reporting Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
REPR | Reporting Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor, coordinated with adjacent wall protection, to suit mobile equipment and patient trolley movement
REPR | Reporting Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
REPR | Reporting Room | Medical Imaging | FIN | CLTI-022 | CEILING: drop-in tiles, acoustic, prefinished | 1 | 1 | Ceiling Finish 1
REPR | Reporting Room | Medical Imaging | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | cover to vision panel provided as required to reduce transfer of light from corridor
REPR | Reporting Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | optional - to x-ray viewer if provided
REPR | Reporting Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
REPR | Reporting Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 3 | 1 |  | 1 to general room lighting, 1 to each workstation to indirect lighting
REPR | Reporting Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | optional
REPR | Reporting Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat | 2 | 1 |  | optional
REPR | Reporting Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | FIHR-231 | BRACKET: computer display screen, triple, articulated, bench/desk mounted | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
REPR | Reporting Room | Medical Imaging | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting | aluminium skirting is also acceptable
REPR | Reporting Room | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1
REPR | Reporting Room | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | optional - one additional chair per workstation for consultation and training
REPR | Reporting Room | Medical Imaging | FFE | FQDW-165.07 | WORKSTATION: straight, adjustable height, electric, 720H nom, 800D x 2200W | 2 | 1
REPR | Reporting Room | Medical Imaging | FFE | FQGE-109 | SCREEN: privacy, acoustic, floor standing | 1 | 1 |  | as required to reduce noise transfer between workstations
REPR | Reporting Room | Medical Imaging | FFE | FQSN-287 | CABINET: floor standing, 1800H nominal, tambour unit | 1 | 1 |  | optional - type and size of storage solutions to suit service requirements
REPR | Reporting Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
REPR | Reporting Room | Medical Imaging | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 1
REPR | Reporting Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 2 | 1 |  | optional - 1 to each workstation to connect desktop computers to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ITIN-171 | DESK BOX: power and data outlets, softwired, surface mounted | 2 | 1 |  | 1 to each workstation, for charging/power to portable devices, number and type of power/AV outlets to be confirmed to suit ICT requirements
REPR | Reporting Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | optional - large wall mounted display screen for collaborative image reviewing
REPR | Reporting Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-241 | RECORDER: dictation | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-251 | CAMERA: webcam, display screen mounted | 2 | 1 |  | optional
REPR | Reporting Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | optional - provision dependent on location of room in relation to public/patient areas and local WHS policies
REPR | Reporting Room | Medical Imaging | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional - provision to ensure staff only access, requirement dependent on location of room in relation to public/patient areas
REPR | Reporting Room | Medical Imaging | SER | LIFX-079 | LIGHT: linear, indirect, wall mounted | 2 | 1 |  | dimmable, 1 to each workstation, to be coordinated with general room lighting to suit reporting task requirements
REPR | Reporting Room | Medical Imaging | FFE | MMGE-151 | LIGHT BOX: x-ray viewer, wall mounted | 1 | 1 |  | optional
REPR | Reporting Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
REPR | Reporting Room | Medical Imaging | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 1 | 1 | Wall Finish 2 | as required to reduce noise transfer between workstations
REPW | Reporting Workstation | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
REPW | Reporting Workstation | Medical Imaging | FIN | CLTI-022 | CEILING: drop-in tiles, acoustic, prefinished | 1 | 1 | Ceiling Finish 1
REPW | Reporting Workstation | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
REPW | Reporting Workstation | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
REPW | Reporting Workstation | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to indirect lighting
REPW | Reporting Workstation | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FIHR-231 | BRACKET: computer display screen, triple, articulated, bench/desk mounted | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
REPW | Reporting Workstation | Medical Imaging | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting | aluminium skirting is also acceptable
REPW | Reporting Workstation | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | optional - additional chair for consultation and training
REPW | Reporting Workstation | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FQDW-165.07 | WORKSTATION: straight, adjustable height, electric, 720H nom, 800D x 2200W | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FQGE-109 | SCREEN: privacy, acoustic, floor standing | 2 | 1 |  | as required to reduce noise transfer between workstations
REPW | Reporting Workstation | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
REPW | Reporting Workstation | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1
REPW | Reporting Workstation | Medical Imaging | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 1 | 1 |  | optional - to connect desktop computers to wall mounted display screen (shared between multiple workstations) if provided
REPW | Reporting Workstation | Medical Imaging | SER | ITIN-171 | DESK BOX: power and data outlets, softwired, surface mounted | 1 | 1 |  | for charging/power to portable devices, number and type of power/AV outlets to be confirmed to suit ICT requirements
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 2 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-241 | RECORDER: dictation | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-251 | CAMERA: webcam, display screen mounted | 1 | 1 |  | optional
REPW | Reporting Workstation | Medical Imaging | SER | LIFX-079 | LIGHT: linear, indirect, wall mounted | 1 | 1 |  | dimmable, to be coordinated with general room lighting to suit reporting task requirements
REPW | Reporting Workstation | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
REPW | Reporting Workstation | Medical Imaging | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 1 | 1 | Wall Finish 2 | as required to reduce noise transfer between workstations
ULTR | Ultrasound Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
ULTR | Ultrasound Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | or wall trim fixing for ceiling tiles
ULTR | Ultrasound Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ULTR | Ultrasound Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | ceiling tiles are also acceptable
ULTR | Ultrasound Room | Medical Imaging | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR | Ultrasound Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 8 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for examination trolley
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to workstation
ULTR | Ultrasound Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | SER | ELSW-022 | SWITCH: light, dimmer, 2-gang | 1 | 1 |  | to general room lighting and indirect lighting
ULTR | Ultrasound Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
ULTR | Ultrasound Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FIHR-333 | BRACKET: television/AV system display screen, single, fixed, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR | Ultrasound Room | Medical Imaging | FFE | FIHR-481 | BRACKET: sling, arm support, ceiling mounted | 1 | 1 |  | optional
ULTR | Ultrasound Room | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
ULTR | Ultrasound Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
ULTR | Ultrasound Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
ULTR | Ultrasound Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQDW-164.02 | WORKSTATION: straight, adjustable height, electric, 720H nom, 750D x 1200W | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
ULTR | Ultrasound Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | optional - for patient access to examination trolley, provision dependent on adjustable height range of trolley
ULTR | Ultrasound Room | Medical Imaging | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
ULTR | Ultrasound Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | ITCL-362 | DISPLAY SCREEN: medical equipment, slave | 1 | 1 |  | for viewing ultrasound imaging by patient, may also be wall mounted
ULTR | Ultrasound Room | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to workstation
ULTR | Ultrasound Room | Medical Imaging | SER | ITIN-061 | OUTLET: data, HDMI, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR | Ultrasound Room | Medical Imaging | MSP | ITIN-065 | OUTLET: data, HDMI, on services panel | 2 | 1 | Panel 1 | for connecting ultrasound machine to slave display screen on ceiling, type of AV outlet to be confirmed to suit equipment requirements
ULTR | Ultrasound Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies
ULTR | Ultrasound Room | Medical Imaging | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
ULTR | Ultrasound Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MIUS-011 | RACK: ultrasound probes, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MIUS-021 | DEVICE: warmer, ultrasound gel, benchtop | 1 | 1 |  | may be integral to ultrasound machine
ULTR | Ultrasound Room | Medical Imaging | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | selection to suit service requirements, may require cut out section for cardiac scans
ULTR | Ultrasound Room | Medical Imaging | FFE | MMGE-056 | POLE: patient positioning support handle, bed mounted | 1 | 1 |  | optional
ULTR | Ultrasound Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MMTR-001.02 | TROLLEY: stainless steel, 490W x 490D x 900H nom, 2 tier | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ULTR | Ultrasound Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2
ULTR | Ultrasound Room | Medical Imaging | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Finish 3
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 8 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for examination trolley
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to workstation
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to pathology area for microscope
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELSW-022 | SWITCH: light, dimmer, 2-gang | 1 | 1 |  | to general room lighting and indirect lighting
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-026 | HOOK: coat | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-113 | BRACKET: sharps bin, trolley mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-333 | BRACKET: television/AV system display screen, single, fixed, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-481 | BRACKET: sling, arm support, ceiling mounted | 1 | 1 |  | optional
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQDW-164.02 | WORKSTATION: straight, adjustable height, electric, 720H nom, 750D x 1200W | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | optional - for patient access to examination trolley, provision dependent on adjustable height range of trolley
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | ITCL-362 | DISPLAY SCREEN: medical equipment, slave | 1 | 1 |  | for viewing ultrasound imaging by clinicians for procedures, may also be wall mounted
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to workstation
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITIN-061 | OUTLET: data, HDMI, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITIN-065 | OUTLET: data, HDMI, on services panel | 2 | 1 | Panel 1 | for connecting ultrasound machine to slave display screen on ceiling, type of AV outlet to be confirmed to suit equipment requirements
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional - provided if reticulated nitrous oxide provided, provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MIUS-011 | RACK: ultrasound probes, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MIUS-021 | DEVICE: warmer, ultrasound gel, benchtop | 1 | 1 |  | may be integral to ultrasound machine
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | selection to suit service requirements, may require cut out section for cardiac scans
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMGE-056 | POLE: patient positioning support handle, bed mounted | 1 | 1 |  | optional
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMTR-002.07 | TROLLEY: stainless steel, 600W x 490D x 900H nom, 5 drawer | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Finish 3
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to change room side
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control workstation side
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side, extent dependent on movement of beds and mobile equipment
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
XRAY | General X-Ray Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
XRAY | General X-Ray Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
XRAY | General X-Ray Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | optional - to control workstation area
XRAY | General X-Ray Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to change room if provided
XRAY | General X-Ray Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | to imaging area
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 3 | 1 |  | to control workstation area, extent of UPS to be confirmed to suit service and equipment requirements
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-312 | ISOLATOR: three phase, with socket outlet, wall mounted | 1 | 1 |  | to generator cabinet, power requirements to be confirmed with MME vendor
XRAY | General X-Ray Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | to control workstation area, main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
XRAY | General X-Ray Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-030 | HOOK: equipment, patient slide | 1 | 1 |  | optional - provide if patient slide required
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to PACS CPU, 1 to x-ray CPU
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
XRAY | General X-Ray Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
XRAY | General X-Ray Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
XRAY | General X-Ray Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 above medical services panel, 1 to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
XRAY | General X-Ray Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 1 | 1 |  | on dual arm bracket
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | on dual arm bracket
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | 1 close to imaging device, 1 to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
XRAY | General X-Ray Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 2 | 1
XRAY | General X-Ray Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | outside all room entries, to automatically turn on when modality is in use
XRAY | General X-Ray Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-001 | IMAGING DEVICE: general x-ray, tube head, ceiling suspended | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-005 | IMAGING DEVICE: general x-ray, wall bucky, fixed | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-009 | TABLE: patient, general x-ray | 1 | 1 |  | may be floating top or elevating table
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-012 | CONTROL CONSOLE: general x-ray, dual display screens, keyboard and mouse, control unit, desktop | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-016 | COMPUTER: general x-ray, central processing unit (CPU) | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-023 | BOARD: electrical distribution (EDB), general x-ray | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-025 | GENERATOR: general x-ray, floor standing | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-026 | GENERATOR: general x-ray, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-033 | HOLDER: general x-ray, detector, floor standing | 1 | 1 |  | to control workstation area, under bench, for storage of charged imaging plates
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-034 | CHARGER: general x-ray, detector, battery, desktop | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-041 | STAND: general x-ray, image stitching, lead ruler, mobile | 1 | 1 |  | optional - may be shared between multiple rooms
XRAY | General X-Ray Room | Medical Imaging | FFE | MMBE-031 | SLIDE: patient transfer | 1 | 1 |  | optional - patient transfer methods and equipment to meet local WHS policies
XRAY | General X-Ray Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | if this room is located within an emergency department the quantity of services may need to align with acute treatment bays to support use with trauma patients
XRAY | General X-Ray Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
XRAY | General X-Ray Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
XRAY | General X-Ray Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
XRAY | General X-Ray Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to change room side
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control workstation side
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides of door
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side, extent dependent on movement of beds and mobile equipment
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | optional - to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to change room if provided
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | to imaging area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 3 | 1 |  | to control workstation, to x-ray control, extent of UPS to be confirmed to suit service and equipment requirements
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to OPG imaging device
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-312 | ISOLATOR: three phase, with socket outlet, wall mounted | 1 | 1 |  | to generator cabinet, power requirements to be confirmed with MME vendor
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | to OPG imaging device
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 2 | 1 |  | to control workstation area, 1 to x-ray, 1 to OPG, main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 2 | 1 |  | 1 to x-ray area, 1 to OPG area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-030 | HOOK: equipment, patient slide | 1 | 1 |  | optional - provide if patient slide required
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | 1 to x-ray MSP, 1 to OPG MSP
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | located close to OPG MSP
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 3 | 1 |  | 1 to OPG PACS CPU, 1 to x-ray PACS CPU, 1 to x-ray control CPU
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 above x-ray medical services panel, 1 to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to control workstation, as required for OPG imaging device connection to remote activation panel
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to OPG imaging device
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 1 | 1 |  | to control workstation, to x-ray control, on dual arm bracket
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | to control workstation, to x-ray control, on dual arm bracket
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-341 | SCANNER: desktop, document, flatbed, desktop | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | 1 between imaging devices, 1 to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 3 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | outside all room entries, to automatically turn on when modality is in use
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIOC-001 | IMAGING DEVICE: orthopantomogram (OPG) | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIOC-011 | CONTROL PANEL: orthopantomogram (OPG), remote activation | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-001 | IMAGING DEVICE: general x-ray, tube head, ceiling suspended | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-005 | IMAGING DEVICE: general x-ray, wall bucky, fixed | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-009 | TABLE: patient, general x-ray | 1 | 1 |  | may be floating top or elevating table
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-012 | CONTROL CONSOLE: general x-ray, dual display screens, keyboard and mouse, control unit, desktop | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-016 | COMPUTER: general x-ray, central processing unit (CPU) | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-023 | BOARD: electrical distribution (EDB), general x-ray | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-025 | GENERATOR: general x-ray, floor standing | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-026 | GENERATOR: general x-ray, wall mounted | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-033 | HOLDER: general x-ray, detector, floor standing | 1 | 1 |  | to control workstation area, under bench, for storage of charged imaging plates
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-034 | CHARGER: general x-ray, detector, battery, desktop | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-041 | STAND: general x-ray, image stitching, lead ruler, mobile | 1 | 1 |  | optional - may be shared between multiple rooms
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MMBE-031 | SLIDE: patient transfer | 1 | 1 |  | optional - patient transfer methods and equipment to meet local WHS policies
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | 1 to x-ray MSP, 1 to OPG MSP
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to x-ray area, if this room is located within an emergency department the quantity of services may need to align with acute treatment bays to support use with trauma patients
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to OPG area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MMTR-001.02 | TROLLEY: stainless steel, 490W x 490D x 900H nom, 2 tier | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room to x-ray area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 2 | for observation from control room to OPG area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 3 | Internal - Door 1 | optional; provision dependent on leaf material and finish
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | DOHI-002.03 | DOOR: hinged, 1 leaf, 850 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-MH-IN); with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | DOHI-017.12 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, anti-ligature and anti-barricade, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1 | inclusion and size of vision panel to be confirmed to suit service requirements; controls for integral blind to be provided to both bedroom and corridor sides of the vision panel; switchable glass may be provided in lieu of integral blind; additional requirements for glazing in vision panel to be confirmed to suit the mental health environment
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | low height, for bed
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | 1 to bedhead, 1 to bench
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | 2 for general room lights (1 to entry and 1 to bedhead), 1 for ensuite lights, 1 for light over bench
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELSW-002 | SWITCH: light, 2-gang | 1 | 1 |  | optional; required for reading light and night light if provided; to bedhead
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FIBM-057 | NOTICEBOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1 |  | to bench; material and method for attaching items to be confirmed to suit operational models
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FIBM-107 | MIRROR: fixed, safety glass, toughened and laminated, frameless, recessed, tamper proof, anti-ligature | 1 | 3 |  | optional
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | FLVY-102 | FLOOR FINISH: vinyl, seamless, standard slip resistance, cushioned | 1 | 1 | Floor Finish 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQSN-107 | BEDSIDE TABLE: fixed, patient locker, tamper proof, anti-ligature | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQSN-123 | SAFE: small, integral to joinery | 1 | 1 |  | optional; to wardrobe; provision dependent on operational models for property storage
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ITCL-127 | BUTTON: nurse call, patient to staff call, with cancel, joinery mounted | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; outside door for card/wristband swipe access; provision dependant clinical service requirements and operational models; door mounted hardware is also acceptable
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOBE-011 | BENCH: 500D, laminate | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOBH-022 | BEDHEAD: full height, tamper proof, anti-ligature | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOCU-406 | WARDROBE: built-in, open, fixed shelves, tamper proof, anti-ligature | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to wardrobe
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | LIFX-156 | LIGHT: night, wall recessed, tamper proof, anti-ligature | 1 | 3 |  | optional; control to bedhead; an additional control may be provided outside the bedroom to support staff observation (restriction of access to external light control must be considered)
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | LIFX-168 | LIGHT: reading, ceiling recessed, tamper proof, anti-ligature | 1 | 1 |  | optional; may alternatively be integrated into the bedhead if provided
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | MMBE-141 | BED: patient, electric, with mattress, mental health | 1 | 1 |  | may alternatively be provided as a fixed plinth type bed depending on service requirements
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | WIOP-255.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 600H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 1 | operability (jockey sash) as required to allow maintenance of integral blind; additional requirements for glazing to be confirmed to suit the mental health environment
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 3 | Internal - Door 1 | optional; provision dependent on leaf material and finish
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | DOHI-002.03 | DOOR: hinged, 1 leaf, 850 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-MH-IN); with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | DOHI-017.12 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, anti-ligature and anti-barricade, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1 | inclusion and size of vision panel to be confirmed to suit service requirements; controls for integral blind to be provided to both bedroom and corridor sides of the vision panel; switchable glass may be provided in lieu of integral blind; additional requirements for glazing in vision panel to be confirmed to suit the mental health environment
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | low height, for bed
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | 1 to bedhead, 1 to bench
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | 2 for general room lights (1 to entry and 1 to bedhead), 1 for ensuite lights, 1 for light over bench
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELSW-002 | SWITCH: light, 2-gang | 1 | 1 |  | optional; required for reading light and night light if provided; to bedhead
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FIBM-057 | NOTICEBOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1 |  | to bench; material and method for attaching items to be confirmed to suit operational models
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FIBM-107 | MIRROR: fixed, safety glass, toughened and laminated, frameless, recessed, tamper proof, anti-ligature | 1 | 3 |  | optional
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | FLVY-102 | FLOOR FINISH: vinyl, seamless, standard slip resistance, cushioned | 1 | 1 | Floor Finish 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQSN-107 | BEDSIDE TABLE: fixed, patient locker, tamper proof, anti-ligature | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQSN-123 | SAFE: small, integral to joinery | 1 | 1 |  | optional; to wardrobe; provision dependent on operational models for property storage
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ITCL-127 | BUTTON: nurse call, patient to staff call, with cancel, joinery mounted | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; outside door for card/wristband swipe access; provision dependant clinical service requirements and operational models; door mounted hardware is also acceptable
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOBE-011 | BENCH: 500D, laminate | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOBH-022 | BEDHEAD: full height, tamper proof, anti-ligature | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOCU-406 | WARDROBE: built-in, open, fixed shelves, tamper proof, anti-ligature | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to wardrobe
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | LIFX-156 | LIGHT: night, wall recessed, tamper proof, anti-ligature | 1 | 3 |  | optional; control to bedhead; an additional control may be provided outside the bedroom to support staff observation (restriction of access to external light control must be considered)
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | LIFX-168 | LIGHT: reading, ceiling recessed, tamper proof, anti-ligature | 1 | 1 |  | optional; may alternatively be integrated into the bedhead if provided
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | MMBE-141 | BED: patient, electric, with mattress, mental health | 1 | 1 |  | may alternatively be provided as a fixed plinth type bed depending on service requirements
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | WIOP-255.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 600H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 1 | operability (jockey sash) as required to allow maintenance of integral blind; additional requirements for glazing to be confirmed to suit the mental health environment
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | 1 to fridge, 1 to boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | optional; to be coordinated with lighting controls for adjacent area
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQCA-401 | FRIDGE: domestic, 120L nom, single door, under bench | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | size, type and quantity of waste bins will be dependent on service requirements and operational models for waste management
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | size, type and quantity of waste bins will be dependent on service requirements and operational models for waste management
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | filter unit to be in lockable cupboard; ventilation requirements to be confirmed to suit selection
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | to boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | optional; extent of storage to be confirmed to suit service requirements; lockable
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | lockable; confirm ventilation requirements for boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 2 | 1 |  | lockable
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | optional; to wall mounted cupboards if provided
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 1 | 1 | Wall Finish 3 | to be coordinated with adjacent wall protection
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 1 | with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside room
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIBM-107 | MIRROR: fixed, safety glass, toughened and laminated, frameless, recessed, tamper proof, anti-ligature | 1 | 1 |  | material to be confirmed at project level to suit service requirements
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-257 | DISPENSER: soap, wall mounted, anti-ligature | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-283 | HOLDER: soap/shampoo, wall recessed, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-302 | DISPENSER: toilet paper, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIHR-027 | HOOK: coat, collapsible, tamper proof, anti-ligature | 2 | 1 |  | optional; some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-066 | TRACK: curtain, shower, recessed/collapsible, anti-ligature | 1 | 1 |  | optional
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-124 | GRAB RAIL: toilet, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-154 | GRAB RAIL: shower, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting | to be tiles if tiled floor provided
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQGE-102 | CURTAIN: shower | 1 | 1 |  | optional
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYBA-152 | BASIN: type C, handwashing, anti-ligature, tamper proof, with integral single shelf | 1 | 1 |  | location of thermostatic mixing valve to be determined based on need to restrict consumer access and ability to share with nearby fittings
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature, tamper proof | 2 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-082 | DRAIN: clear out, round, tamper proof, anti-ligature, tamper proof | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYSH-006 | SHOWER: fixed rose, wall mounted, anti-ligature, tamper proof | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-002 | FLUSH BUTTON: toilet suite | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-069 | TAPWARE: basin, tap set, wall mounted, anti-ligature, tamper proof | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-263 | TAPWARE: shower, tap set, anti-ligature, tamper proof | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYWC-036.02 | TOILET SUITE: patient, anti-ligature, tamper proof, concealed cistern | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | to toilet
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 1 | with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside room
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIBM-107 | MIRROR: fixed, safety glass, toughened and laminated, frameless, recessed, tamper proof, anti-ligature | 1 | 1 |  | material to be confirmed at project level to suit service requirements
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIDI-257 | DISPENSER: soap, wall mounted, anti-ligature | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIDI-283 | HOLDER: soap/shampoo, wall recessed, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIDI-302 | DISPENSER: toilet paper, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIHR-027 | HOOK: coat, collapsible, tamper proof, anti-ligature | 2 | 1 |  | optional; some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIRT-066 | TRACK: curtain, shower, recessed/collapsible, anti-ligature | 1 | 1 |  | optional
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIRT-124 | GRAB RAIL: toilet, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIRT-154 | GRAB RAIL: shower, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting | to be tiles if tiled floor provided
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FQGE-102 | CURTAIN: shower | 1 | 1 |  | optional
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYBA-152 | BASIN: type C, handwashing, anti-ligature, tamper proof, with integral single shelf | 1 | 1 |  | location of thermostatic mixing valve to be determined based on need to restrict consumer access; typically provided behind a lockable panel in external corridor
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature, tamper proof | 2 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYDR-082 | DRAIN: clear out, round, tamper proof, anti-ligature, tamper proof | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYSH-006 | SHOWER: fixed rose, wall mounted, anti-ligature, tamper proof | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYTP-002 | FLUSH BUTTON: toilet suite | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYTP-069 | TAPWARE: basin, tap set, wall mounted, anti-ligature, tamper proof | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYTP-263 | TAPWARE: shower, tap set, anti-ligature, tamper proof | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYWC-036.02 | TOILET SUITE: patient, anti-ligature, tamper proof, concealed cistern | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | to toilet
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | based on a risk assessment tiles may also be acceptable
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDFI-026 | DOOR GLAZING FINISH: vision panel, privacy film | 1 | 1 | Internal - Door 1 | optional; as required to suit privacy requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to room side
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side as required
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to corridor side as required
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 3 | External - Window 1
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | if tamper proof and anti-ligature finish required, flush set ceiling to be provided
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | secondary egress
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FIBM-020 | WHITEBOARD: fixed, magnetic, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FIBM-057 | NOTICEBOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQDW-104.02 | WORKSTATION: straight, fixed height, 720H, 750D x 1200W | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 3
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2 | optional; provision to suit security and egress requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; provision to suit security and egress requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 3 | External - Window 1 | optional; natural light and external outlook is desirable; consider placement and room orientation for patient privacy; requirements for glazing to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to both sides
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | optional; provision dependent on frame material and finish
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 3 | Internal - Door 2 | optional; secondary egress; provision dependent on local WHS policies; requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | 1 to washing machine; 1 to dryer
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-101 | WASHING MACHINE: laundry, domestic, front loading | 1 | 1 |  | quantity to suit service requirements
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-111 | DRYER: laundry, domestic | 1 | 1 |  | quantity to suit service requirements
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-121 | PLINTH: washing machine, domestic | 1 | 1 |  | for improved reaching height to machine opening; as required to suit configuration and machines selected; washing machine may alternatively be floor standing
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-141 | STACKING KIT: washing machine and dryer, domestic | 1 | 1 |  | as required to suit configuration and machines selected; dryer may alternatively be on a plinth or floor standing
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on service requirements, operational models for waste management and local IPC policies
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | HYBA-411 | SINK: laundry, single bowl | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby fixtures
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature, tamper proof | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | HYTP-184 | TAPWARE: sink, tap set, wall mounted, anti-ligature, tamper proof | 1 | 1 |  | selection of sink and tapware should be coordinated to ensure compatibility
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | to washing machine
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-432 | OUTLET: water, hot | 1 | 1 |  | to washing machine
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | lockable
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | lockable
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOSH-105 | SHELF UNIT: wall mounted, pigeonholes | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | WIFX-009.01 | WINDOW: fixed, internal, single glazed, sill at 1200H | 1 | 1 | Internal - Window 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2
SECL | Seclusion Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | optional; to corridor side if provided; provision dependent on leaf material and finish
SECL | Seclusion Room | Mental Health | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 3 | Internal - Door 1 | optional; to room side if provided; provision dependent on leaf material and finish
SECL | Seclusion Room | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
SECL | Seclusion Room | Mental Health | FIN | CLFS-014 | CEILING: flush set, suspended, impact resistant | 1 | 1 | Ceiling Finish 1 | consider plywood backing to ceiling finish
SECL | Seclusion Room | Mental Health | D+W | DOHI-019.12 | DOOR: hinged, 1 leaf, 1200 clear opening, solid, anti-ligature and anti-barricade, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1
SECL | Seclusion Room | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to staff observation area
SECL | Seclusion Room | Mental Health | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to staff observation area
SECL | Seclusion Room | Mental Health | FFE | FIBM-112 | MIRROR: fixed, convex, tamper proof, anti-ligature | 1 | 1
SECL | Seclusion Room | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
SECL | Seclusion Room | Mental Health | FIN | FLVY-102 | FLOOR FINISH: vinyl, seamless, standard slip resistance, cushioned | 1 | 1 | Floor Finish 1
SECL | Seclusion Room | Mental Health | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 2 | 3 |  | optional; connection requirements to be confirmed; music source to be controlled from device in staff observation area
SECL | Seclusion Room | Mental Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | to staff observation area
SECL | Seclusion Room | Mental Health | FFE | MMBE-184 | MATTRESS: patient, tamper proof, anti-ligature, with sealed seams | 1 | 1
SECL | Seclusion Room | Mental Health | D+W | WIFX-057.04 | WINDOW: fixed, internal, double glazed, sill at 900H, with integral blind | 1 | 1 | Internal - Window 1 | for observation from staff area; control for blinds external to room
SECL | Seclusion Room | Mental Health | D+W | WIOP-262.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 1650H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 1 | blinds controlled from staff area
SECL | Seclusion Room | Mental Health | D+W | WIOP-262.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 1650H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 2 | blinds controlled from staff area
SECL | Seclusion Room | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
STPP | Store - Patient Property | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
STPP | Store - Patient Property | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
STPP | Store - Patient Property | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
STPP | Store - Patient Property | Mental Health | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
STPP | Store - Patient Property | Mental Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1
STPP | Store - Patient Property | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
STPP | Store - Patient Property | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
STPP | Store - Patient Property | Mental Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
STPP | Store - Patient Property | Mental Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
STPP | Store - Patient Property | Mental Health | FFE | FQSN-214 | SHELVING UNIT: floor standing, adjustable shelves, 600D x 900W x 2100H nominal | 5 | 1 |  | type, extent and configuration of storage to suit service requirements and operational policies for method of property separation and volume of property to be stored per person
STPP | Store - Patient Property | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
STPP | Store - Patient Property | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to room side
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | optional; provision dependent on frame material and finish
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
TRBNL | Tribunal Hearing Room | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
TRBNL | Tribunal Hearing Room | Mental Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 2
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to AV display screen and CPU
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-226 | GPO: double, in floor box | 2 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to each door
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FIHR-332 | BRACKET: television/AV system display screen, single, fixed, joinery mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FQBS-142 | CHAIR: meeting room, stackable | 12 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FQTA-125.04 | TABLE: rectangular, 750H, 1500L x 750W, folding, on casters | 4 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-103 | CONTROL PANEL: AV system, joinery mounted | 1 | 1 |  | may alternatively be provided as a wall mounted or portable item
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-134 | CAMERA: AV system, video conferencing, surface mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-147 | MICROPHONE: AV system, portable | 1 | 1 |  | may alternatively be provided as ceiling recessed item
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | optional
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional; to room booking system if provided
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 1 | 1 |  | to AV display screen and CPU
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 1 | 1 |  | integral to 1 folding table as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | to suit security and egress requirements
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 2 | 1 |  | lockable
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-125 | CUPBOARD: wall mounted, double door, for audio-visual equipment | 1 | 1 |  | lockable; with ventilation as required to suit AV equipment
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-201 | CUPBOARD: under bench, single door | 2 | 1 |  | lockable
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-225 | CUPBOARD: under bench, double door, for audio-visual equipment | 1 | 1 |  | lockable; with ventilation as required to suit AV equipment
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | WIFX-056.04 | WINDOW: fixed, internal, double glazed, sill at 750H, with integral blind | 1 | 1 | Internal - Window 1 | to observation area as required
TRBNL | Tribunal Hearing Room | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional; provision dependent on frame material and finish
WAIT-SEC | Waiting - Secure | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
WAIT-SEC | Waiting - Secure | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | D+W | DOHI-144.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel, with integral blind | 1 | 1 | Internal - Door 1 | from external corridor
WAIT-SEC | Waiting - Secure | Mental Health | D+W | DOHI-144.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel, with integral blind | 1 | 1 | Internal - Door 2 | to mental health unit; provision of tamper proof, anti-ligature and anti-barricade hardware to be confirmed to suit service requirements
WAIT-SEC | Waiting - Secure | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment display screen and CPU
WAIT-SEC | Waiting - Secure | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQTA-202 | TABLE: square, 450H, 600L | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | 1 to each intercom
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to patient entertainment display screen and CPU
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 2 | 1 |  | to doors
WAIT-SEC | Waiting - Secure | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
WAIT-SEC | Waiting - Secure | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2
WAIT-SEC | Waiting - Secure | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ANAES | Anaesthetic Preparation Room | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2
ANAES | Anaesthetic Preparation Room | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
ANAES | Anaesthetic Preparation Room | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
ANAES | Anaesthetic Preparation Room | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
ANAES | Anaesthetic Preparation Room | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ANAES | Anaesthetic Preparation Room | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ANAES | Anaesthetic Preparation Room | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
ANAES | Anaesthetic Preparation Room | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to operating room (see OR-GEN), cover required to vision panel if laser is to be used
ANAES | Anaesthetic Preparation Room | Operating | D+W | DOSL-212.01 | DOOR: sliding, bi-parting, 2 leaves, 1600 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | to corridor
ANAES | Anaesthetic Preparation Room | Operating | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 3 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 3 | 1 |  | to bench
ANAES | Anaesthetic Preparation Room | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-251 | DISPENSER: alcohol-based hand rub, surgical, antimicrobial, chlorhexidine, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 5 | 1
ANAES | Anaesthetic Preparation Room | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
ANAES | Anaesthetic Preparation Room | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-072 | BIN: recycling, commingled, 30L | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-237 | BIN: clinical waste, 120L | 1 | 1 |  | optional - provision dependent on waste management policy
ANAES | Anaesthetic Preparation Room | Operating | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | HYTP-076 | TAPWARE: basin, sensor, wall mounted | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
ANAES | Anaesthetic Preparation Room | Operating | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | flush to wall
ANAES | Anaesthetic Preparation Room | Operating | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITCL-211 | BUTTON: nurse call, orderly / porter, with cancel, wall mounted | 1 | 1 |  | optional - depending on operational processes
ANAES | Anaesthetic Preparation Room | Operating | MSP | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to telephone
ANAES | Anaesthetic Preparation Room | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to bench
ANAES | Anaesthetic Preparation Room | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | computer may alternatively be on a bench top or wall mounted
ANAES | Anaesthetic Preparation Room | Operating | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
ANAES | Anaesthetic Preparation Room | Operating | FFE | LIFX-122 | LIGHT: procedure, minor, articulated, ceiling mounted | 1 | 1 |  | a recessed ceiling examination light may be provided in lieu of small procedure light to suit service requirements
ANAES | Anaesthetic Preparation Room | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 1 | 1 |  | controlled from operating room
ANAES | Anaesthetic Preparation Room | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | controlled from operating room
ANAES | Anaesthetic Preparation Room | Operating | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGFP-051 | ADAPTER: scavenge | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMOP-161 | MACHINE: anaesthetic | 1 | 1 |  | optional - may be provided within the anaesthetic preparation room or within the operating room (see OR-GEN)
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | optional - drug safe may alternatively be located in the operating room; with card reader, safe location and type of medication stored is dependent on the operational policies and medication management regulations in different jurisdictions
ANAES | Anaesthetic Preparation Room | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMTR-013.01 | TROLLEY: stainless steel, wire mesh drawers, 900W x 490D x 900H nom, 3 drawers | 3 | 1
ANAES | Anaesthetic Preparation Room | Operating | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ANAES | Anaesthetic Preparation Room | Operating | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2
B-SCRUB | Bay - Scrub | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
B-SCRUB | Bay - Scrub | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
B-SCRUB | Bay - Scrub | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | 900H x 450W, at 900H AFFL
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | for non-sterile gloves
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-131 | HOLDER: PPE, goggles, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-201 | DISPENSER: scrub brush, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-251 | DISPENSER: alcohol-based hand rub, surgical, antimicrobial, chlorhexidine, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-266.01 | DISPENSER: hand wash, surgical, antimicrobial, chlorhexidine, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-266.02 | DISPENSER: hand wash, surgical, antimicrobial, povidone-iodine (PVI), wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-271 | DISPENSER: moisturiser, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
B-SCRUB | Bay - Scrub | Operating | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10 / pendulum P3 or agreed equivalent
B-SCRUB | Bay - Scrub | Operating | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
B-SCRUB | Bay - Scrub | Operating | FFE | HYBA-112 | SCRUB TROUGH: type A, handwashing, floor mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to scrub trough
B-SCRUB | Bay - Scrub | Operating | FFE | HYTP-121 | TAPWARE: scrub trough, sensor tap and plate, trough mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 3 | 1 |  | 1 to each sensor tap spout
B-SCRUB | Bay - Scrub | Operating | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | flush to wall
B-SCRUB | Bay - Scrub | Operating | FFE | JOSH-402 | SHELF: wall mounted, stainless steel | 1 | 1 |  | optional; mounted above scrub trough
B-SCRUB | Bay - Scrub | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1
B-SCRUB | Bay - Scrub | Operating | FIN | WLPR-006.07 | WALL PROTECTION: corner guards, full height | 1 | 1 | Wall Finish 2
CLNUP | Clean-Up Room | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both side of the door leaf
CLNUP | Clean-Up Room | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
CLNUP | Clean-Up Room | Operating | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
CLNUP | Clean-Up Room | Operating | D+W | DOHI-015.01 | DOOR: hinged, 1 leaf, 1000 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | sliding door may also be acceptable dependent on infection prevention and control and work health and safety policies, provision of manual hold open device to be confirmed to suit operational requirements
CLNUP | Clean-Up Room | Operating | SER | ELGP-133 | GPO: single, emergency power, wall mounted, waterproof | 1 | 1 |  | optional - to surgical waste docking station if provided
CLNUP | Clean-Up Room | Operating | SER | ELSW-001 | SWITCH: light | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FIHR-039 | RACK: broom/mop, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIHR-143 | RACK: bottle, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
CLNUP | Clean-Up Room | Operating | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10 / pendulum P3 or agreed equivalent
CLNUP | Clean-Up Room | Operating | FFE | FQCL-052 | BUCKET: cleaner, mopping | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | quantity is dependent on service requirements (e.g. use of single use drapes)
CLNUP | Clean-Up Room | Operating | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1 |  | optional - for laparoscopic sharps as required
CLNUP | Clean-Up Room | Operating | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1 |  | optional - to laparoscopic sharps bin if provided
CLNUP | Clean-Up Room | Operating | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FQWS-063 | BIN: general waste, slimline, 90L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
CLNUP | Clean-Up Room | Operating | FFE | FQWS-103 | BIN: recycling, paper/cardboard, slimline, 90L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-123 | BIN: recycling, plastics, slimline, 90L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-131 | BIN: recycling, soft plastics, 20L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-143 | BIN: recycling, soft plastics, slimline, 90L | 1 | 1 |  | for sterile wraps
CLNUP | Clean-Up Room | Operating | FFE | FQWS-151 | BIN: recycling, glass, 20L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-171 | BIN: recycling, metal, 20L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYBA-301 | SINK: single bowl | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYBA-451 | SINK: cleaner, with grate, wall mounted | 1 | 1 |  | optional - depending on operating room cleaning equipment and procedures
CLNUP | Clean-Up Room | Operating | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1
CLNUP | Clean-Up Room | Operating | SER | HYDR-103 | TUNDISH: wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | SER | HYDR-151 | TRAP: plaster | 1 | 1 |  | optional
CLNUP | Clean-Up Room | Operating | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to sink
CLNUP | Clean-Up Room | Operating | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYTP-066 | TAPWARE: basin, tap set, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYTP-182 | TAPWARE: sink, tap set, wall mounted, lever handles | 1 | 1
CLNUP | Clean-Up Room | Operating | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin, 1 to sink
CLNUP | Clean-Up Room | Operating | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink
CLNUP | Clean-Up Room | Operating | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | with integral stainless steel splashback
CLNUP | Clean-Up Room | Operating | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | JOSH-403 | SHELF: wall mounted, wire | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | LIFX-122 | LIGHT: procedure, minor, articulated, ceiling mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | MMIC-496 | TROLLEY: transfer, instruments, dirty | 1 | 1 |  | optional - depending on RMD sterilizing transport processes, stored in room prior to transfer to sterilising unit
CLNUP | Clean-Up Room | Operating | FFE | MMOP-401 | MACHINE: surgical waste management system | 1 | 1 |  | optional - machine and docking station may be required only in a selection of clean up rooms across the unit (i.e. approx. 1 per 4 OR's)
CLNUP | Clean-Up Room | Operating | FFE | MMOP-406 | DOCKING STATION: surgical waste management system | 1 | 1 |  | optional, direct connect waste outlet to sewer system; docking station may be required only in a selection of clean up rooms across the unit (i.e. approx. 1 per 4 OR's)
ENPR | Procedure Room - Endoscopy | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
ENPR | Procedure Room - Endoscopy | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 3 | to both sides
ENPR | Procedure Room - Endoscopy | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 2 | to both sides
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 3
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 2
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 3
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 2
ENPR | Procedure Room - Endoscopy | Operating | FIN | CLFI-003 | CEILING FINISH: paint, sterile areas | 1 | 1 | Ceiling Finish 2
ENPR | Procedure Room - Endoscopy | Operating | FIN | CLFS-012 | CEILING: flush set, suspended, acoustic | 1 | 1 | Ceiling Finish 1 | finish to be suitable for sterile environments, refer to local engineering services guidance for acoustic performance (i.e. reverberation time control, sound absorption class, etc.)
ENPR | Procedure Room - Endoscopy | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 3 | optional - to dirty scope room if floor plan supports direct access
ENPR | Procedure Room - Endoscopy | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | optional - to clean scope room if floor plan supports direct access
ENPR | Procedure Room - Endoscopy | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to corridor, cover required to vision panel if laser is to be used
ENPR | Procedure Room - Endoscopy | Operating | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 3 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 12 | 1 | Pendant 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-176 | GPO: single, UPS, on services panel | 3 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 4 | 1 | Pendant 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-318 | ISOLATOR: three phase, with socket outlet, on services pendant | 1 | 1 | Pendant 1 | optional - depending on equipment requirements, may be wall mounted
ENPR | Procedure Room - Endoscopy | Operating | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | to UPS power outlets on medical services pendants
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-034 | PANEL: UPS status indicator, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | SER | ELSW-042 | SWITCH: light, laser in use | 1 | 1 |  | optional - to be provided if laser to be used, may be integrated on lighting control panel
ENPR | Procedure Room - Endoscopy | Operating | SER | ELSW-043 | SWITCH: light, x-ray in use | 1 | 1 |  | optional - to be provided if x-ray to be used, may be integrated on lighting control panel
ENPR | Procedure Room - Endoscopy | Operating | SER | ELSW-051 | CONTROL PANEL: lighting | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIHR-327 | BRACKET: keyboard and mouse, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | to digital operating room (DOR) display screen
ENPR | Procedure Room - Endoscopy | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
ENPR | Procedure Room - Endoscopy | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQWS-005 | BIN: sharps, clinical, extra large | 1 | 1 |  | on cart
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQWS-396 | TROLLEY: waste bag | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITBU-436 | CONTROL PANEL: time and elapsed time, synchronised slave clock | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITCL-213 | BUTTON: nurse call, orderly / porter, with cancel, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITIN-014 | OUTLET: data, single RJ45, on services pendant | 4 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 3 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
ENPR | Procedure Room - Endoscopy | Operating | FFE | JOCU-023 | CUPBOARD: tall, double door, glazed | 3 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | plasterboard bulkhead is also acceptable
ENPR | Procedure Room - Endoscopy | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 3 | 1 |  | located outside doors, optional - to be provided if laser to be used
ENPR | Procedure Room - Endoscopy | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | located outside doors, optional - to be provided if x-ray to be used
ENPR | Procedure Room - Endoscopy | Operating | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1 |  | for removal of anaesthetic gases, rectilinear or triangular ducts are also acceptable
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-001 | OUTLET: carbon dioxide (CO2), on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-002 | OUTLET: carbon dioxide (CO2), on services panel | 1 | 1 | Panel 2 | for endoscopy stack
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on services pendant | 1 | 1 | Pendant 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-051 | OUTLET: scavenge, on services pendant | 1 | 1 | Pendant 1 | optional; required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-061 | OUTLET: suction, on services pendant | 3 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMBE-151 | TROLLEY: patient, transport | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMIC-301 | CABINET: endoscope, drying and storage, single door, pass-through | 1 | 1 |  | optional - to clean scope room if floor plan supports direct access, interlocking mechanisms requried
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-123 | STOOL: mobile, surgeon | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-162 | MACHINE: anaesthetic, with patient monitor, high acuity | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-166 | TROLLEY: anaesthetic | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-171 | MACHINE: electrosurgical, diathermy | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-202 | STAND: bowl, single | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-211 | KICKBUCKET: with stand | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-242 | CAMERA: endoscopic | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-252 | DEVICE: processor, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-262 | DEVICE: light source, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-272 | DEVICE: insufflator, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-282 | TROLLEY: endoscopy stack, equipment | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-297 | CONTAINER: endoscope, transport | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-302 | DISPLAY SCREEN: digital operating room (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMOP-303 | DISPLAY SCREEN: digital operating room (DOR) integration, pendant mounted | 1 | 1 | Pendant 3 - Arm 2
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-311 | CAMERA: patient observation, digital operating room (DOR) integration, ceiling mounted | 1 | 1 |  | optional
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-331 | SPEAKER: digital operating room (DOR) integration, ceiling recessed | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-341 | CONTROL PANEL: digital operating room (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | MMOP-346 | CONTROL PANEL: operating lights, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-351 | PATCH PANEL: digital room operating (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMOP-352 | PATCH PANEL: digital room operating (DOR) integration, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | SER | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 |  | to wall mounted display screen
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 | Panel 2 | for connection of endoscopy stack to digital operating room (DOR) system
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-371 | SYSTEM CABINET: digital integration in operating rooms (DOR) | 1 | 1 |  | located in ICT/AV cupboard (see EXIT)
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | with card reader
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-091 | LIGHT HEAD: operating, articulated arm, pendant mounted | 1 | 1 | Pendant 3 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-101 | MEDICAL SERVICES PENDANT: single arm, horizontal services head | 1 | 1 | Pendant 1 | ergonomic control handles required; configuration (horizontal or vertical) to suit services requirements; services allocations are indicative - type and number of services on the pendant to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-224 | MEDICAL SERVICES PENDANT: double arm, 1 light head, operating / display screen | 1 | 1 | Pendant 3
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-052 | TROLLEY: airway/intubation, 600W x 490D x 900H nom | 1 | 1 |  | difficult airway (DVA)
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | endoscope clean/dirty transport
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-072 | TROLLEY: equipment, 600W x 490D x 900H nom | 1 | 1 |  | endoscope equipment and accessories
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-077 | TROLLEY: instruments, 600W x 490D x 900H nom | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | for biopsies, with drawers
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-096 | TROLLEY: scout, 490W x 490D x 900H nom | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-108 | TROLLEY: set-up, table 1250W x 800D x 900H nom | 1 | 1 |  | with drawers
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-123 | TROLLEY: gowns/scrubs, 1220W x 610D x 1830H nominal | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-171 | TROLLEY: mayo table | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | alternative impermeable seamless materials may also be acceptable, confirm material selection to suit infection prevention and control requirements
EXIT | Exit Bay | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2
EXIT | Exit Bay | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides of door
EXIT | Exit Bay | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
EXIT | Exit Bay | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
EXIT | Exit Bay | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
EXIT | Exit Bay | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
EXIT | Exit Bay | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
EXIT | Exit Bay | Operating | D+W | DOHI-001.01 | DOOR: hinged, 1 leaf, 800 clear opening, solid | 1 | 1 | Internal - Door 2 | to ICT/AV cupboard
EXIT | Exit Bay | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to operating room (see OR-GEN), cover required to vision panel if laser is to be used
EXIT | Exit Bay | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1
EXIT | Exit Bay | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
EXIT | Exit Bay | Operating | FFE | FIHR-030 | HOOK: equipment, patient slide | 1 | 1
EXIT | Exit Bay | Operating | FFE | FIHR-171 | BRACKET: gas cylinder, single, wall mounted | 1 | 1 |  | clear space above the bracket for loading/unloading of the cylinder
EXIT | Exit Bay | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
EXIT | Exit Bay | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
EXIT | Exit Bay | Operating | SER | MGFP-011 | VALVE BOX: medical gases | 1 | 1
EXIT | Exit Bay | Operating | FFE | MGGE-011.01 | CYLINDER: medical gas, C size, oxygen | 1 | 1
EXIT | Exit Bay | Operating | FFE | MMBE-031 | SLIDE: patient transfer | 1 | 1
EXIT | Exit Bay | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1
EXIT | Exit Bay | Operating | FIN | WLPR-006.07 | WALL PROTECTION: corner guards, full height | 1 | 1 | Wall Finish 2
OR-GEN | Operating Room - General | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
OR-GEN | Operating Room - General | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 2 | to both sides
OR-GEN | Operating Room - General | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 3 | to both sides
OR-GEN | Operating Room - General | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 3
OR-GEN | Operating Room - General | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
OR-GEN | Operating Room - General | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 2 | to allow for opening either one or both leaves of the door
OR-GEN | Operating Room - General | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
OR-GEN | Operating Room - General | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 2 | delayed action closing
OR-GEN | Operating Room - General | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 3
OR-GEN | Operating Room - General | Operating | FIN | CLFI-003 | CEILING FINISH: paint, sterile areas | 1 | 1 | Ceiling Finish 2
OR-GEN | Operating Room - General | Operating | FIN | CLFS-012 | CEILING: flush set, suspended, acoustic | 1 | 1 | Ceiling Finish 1 | finish to be suitable for sterile environments, refer to local engineering services guidance for acoustic performance (i.e. reverberation time control, sound absorption class, etc.)
OR-GEN | Operating Room - General | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 3 | to store - sterile stock, access provided for stock delivery where sterile stock is not directly adjacent to operating room
OR-GEN | Operating Room - General | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to anaesthetic preparation room (see ANAES), cover required to vision panel if laser is to be used
OR-GEN | Operating Room - General | Operating | D+W | DOHI-213.03 | DOOR: hinged, 2 leaves, 1700 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | to exit bay (see EXIT), cover required to vision panel if laser is to be used
OR-GEN | Operating Room - General | Operating | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | for recharging equipment
OR-GEN | Operating Room - General | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 2 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 12 | 1 | Pendant 1 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 12 | 1 | Pendant 2 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | ELGP-176 | GPO: single, UPS, on services panel | 4 | 1 | Panel 2 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 4 | 1 | Pendant 1 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 4 | 1 | Pendant 2 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1
OR-GEN | Operating Room - General | Operating | MSP | ELGP-318 | ISOLATOR: three phase, with socket outlet, on services pendant | 1 | 1 | Pendant 2 | optional - depending on equipment requirements, may be wall mounted
OR-GEN | Operating Room - General | Operating | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | to UPS power outlets on medical services pendants
OR-GEN | Operating Room - General | Operating | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | MSP | ELPR-034 | PANEL: UPS status indicator, on services pendant | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | SER | ELSW-042 | SWITCH: light, laser in use | 1 | 1 |  | optional - to be provided if laser to be used, may be integrated on lighting control panel
OR-GEN | Operating Room - General | Operating | SER | ELSW-043 | SWITCH: light, x-ray in use | 1 | 1 |  | optional - to be provided if x-ray to be used, may be integrated on lighting control panel
OR-GEN | Operating Room - General | Operating | SER | ELSW-051 | CONTROL PANEL: lighting | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | optional - to medical services panel if provided
OR-GEN | Operating Room - General | Operating | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | FFE | FIHR-327 | BRACKET: keyboard and mouse, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | to digital operating room (DOR) display screen
OR-GEN | Operating Room - General | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
OR-GEN | Operating Room - General | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
OR-GEN | Operating Room - General | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 2 | inset section of contrasting colour to sterile zone
OR-GEN | Operating Room - General | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FQWS-005 | BIN: sharps, clinical, extra large | 1 | 1 |  | on cart
OR-GEN | Operating Room - General | Operating | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FQWS-396 | TROLLEY: waste bag | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ITBU-436 | CONTROL PANEL: time and elapsed time, synchronised slave clock | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on services pendant | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on services pendant | 1 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on services pendant | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on services pendant | 1 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | SER | ITCL-211 | BUTTON: nurse call, orderly / porter, with cancel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-213 | BUTTON: nurse call, orderly / porter, with cancel, on services pendant | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-213 | BUTTON: nurse call, orderly / porter, with cancel, on services pendant | 1 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | ITIN-014 | OUTLET: data, single RJ45, on services pendant | 4 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | ITIN-014 | OUTLET: data, single RJ45, on services pendant | 4 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
OR-GEN | Operating Room - General | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 3 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1
OR-GEN | Operating Room - General | Operating | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | workstation on wheels (WOW) may be provided depending on workflows
OR-GEN | Operating Room - General | Operating | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | FFE | ITNE-224 | INPUT DEVICE: bar code scanner, wireless, with charging dock, medical grade, washable | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
OR-GEN | Operating Room - General | Operating | FFE | JOBE-002 | BENCH: 450D, stainless steel | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 3 | 1 |  | located outside doors, optional - to be provided if laser to be used
OR-GEN | Operating Room - General | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | located outside doors, optional - to be provided if x-ray to be used
OR-GEN | Operating Room - General | Operating | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 4 | 1 |  | for removal of anaesthetic gases, rectilinear or triangular ducts are also acceptable
OR-GEN | Operating Room - General | Operating | MSP | MGAS-001 | OUTLET: carbon dioxide (CO2), on services pendant | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-001 | OUTLET: carbon dioxide (CO2), on services pendant | 1 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 1 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | MGAS-022 | OUTLET: medical air, on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on services pendant | 1 | 1 | Pendant 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on services pendant | 1 | 1 | Pendant 2 | optional; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGAS-051 | OUTLET: scavenge, on services pendant | 1 | 1 | Pendant 1 | optional; required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-051 | OUTLET: scavenge, on services pendant | 1 | 1 | Pendant 2 | optional; required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-061 | OUTLET: suction, on services pendant | 3 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-061 | OUTLET: suction, on services pendant | 3 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGAS-071 | OUTLET: tool air, integral control panel, on services pendant | 1 | 1 | Pendant 1 | optional - depending on medical equipment to be used, may also be wall mounted
OR-GEN | Operating Room - General | Operating | MSP | MGAS-071 | OUTLET: tool air, integral control panel, on services pendant | 1 | 1 | Pendant 2 | optional - depending on medical equipment to be used, may also be wall mounted
OR-GEN | Operating Room - General | Operating | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | FFE | MMGE-045 | POLE: IV, mobile | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | optional - to medical services panel if provided
OR-GEN | Operating Room - General | Operating | FFE | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMGE-367 | DEVICE: patient warming, air blanket | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-106 | TABLE: operating, mobile, electric | 1 | 1 |  | type of operating table to suit service requirements
OR-GEN | Operating Room - General | Operating | FFE | MMOP-121 | STOOL: mobile, operating | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-123 | STOOL: mobile, surgeon | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-162 | MACHINE: anaesthetic, with patient monitor, high acuity | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-166 | TROLLEY: anaesthetic | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-171 | MACHINE: electrosurgical, diathermy | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-173 | MACHINE: smoke plume evacuation system | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-201 | STAND: bowl, double | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-202 | STAND: bowl, single | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-211 | KICKBUCKET: with stand | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-302 | DISPLAY SCREEN: digital operating room (DOR) integration, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MMOP-303 | DISPLAY SCREEN: digital operating room (DOR) integration, pendant mounted | 1 | 1 | Pendant 3 - Arm 2
OR-GEN | Operating Room - General | Operating | MSP | MMOP-303 | DISPLAY SCREEN: digital operating room (DOR) integration, pendant mounted | 1 | 1 | Pendant 4 - Arm 2
OR-GEN | Operating Room - General | Operating | FFE | MMOP-311 | CAMERA: patient observation, digital operating room (DOR) integration, ceiling mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MMOP-316 | CAMERA: surgical field, digital operating room (DOR) integration, integral to operating light | 1 | 1 | Pendant 3 - Arm 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-331 | SPEAKER: digital operating room (DOR) integration, ceiling recessed | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-341 | CONTROL PANEL: digital operating room (DOR) integration, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | MMOP-346 | CONTROL PANEL: operating lights, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-351 | PATCH PANEL: digital room operating (DOR) integration, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MMOP-352 | PATCH PANEL: digital room operating (DOR) integration, on services pendant | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | SER | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 |  | to wall mounted display screen
OR-GEN | Operating Room - General | Operating | MSP | MMOP-363 | OUTLET: digital operating room (DOR) integration, on services pendant | 1 | 1 | Pendant 1 | optional - for connection of image capture device to digital operating room (DOR) system
OR-GEN | Operating Room - General | Operating | MSP | MMOP-363 | OUTLET: digital operating room (DOR) integration, on services pendant | 1 | 1 | Pendant 2 | optional - for connection of image capture device to digital operating room (DOR) system
OR-GEN | Operating Room - General | Operating | FFE | MMOP-371 | SYSTEM CABINET: digital integration in operating rooms (DOR) | 1 | 1 |  | located in ICT/AV cupboard (see EXIT)
OR-GEN | Operating Room - General | Operating | FFE | MMPH-002 | SAFE: dangerous drugs, wall mounted, medium | 1 | 1 |  | optional - drug safe may alternatively be located in the anaesthetic preparation room; with card reader, safe location and type of medication stored is dependent on the operational policies and medication management regulations in different jurisdictions
OR-GEN | Operating Room - General | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | optional - provided for theatres where obstetric procedures are undertaken or services are otherwise required separately to those in the medical services pendants
OR-GEN | Operating Room - General | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | MSP | MMSP-091 | LIGHT HEAD: operating, articulated arm, pendant mounted | 1 | 1 | Pendant 3 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MMSP-091 | LIGHT HEAD: operating, articulated arm, pendant mounted | 1 | 1 | Pendant 4 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MMSP-101 | MEDICAL SERVICES PENDANT: single arm, horizontal services head | 1 | 1 | Pendant 1 | ergonomic control handles required; configuration (horizontal or vertical) to suit services requirements; services allocations are indicative - type and number of services on the pendant to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | MMSP-101 | MEDICAL SERVICES PENDANT: single arm, horizontal services head | 1 | 1 | Pendant 2 | ergonomic control handles required; configuration (horizontal or vertical) to suit services requirements; services allocations are indicative - type and number of services on the pendant to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | MMSP-224 | MEDICAL SERVICES PENDANT: double arm, 1 light head, operating / display screen | 1 | 1 | Pendant 3
OR-GEN | Operating Room - General | Operating | MSP | MMSP-224 | MEDICAL SERVICES PENDANT: double arm, 1 light head, operating / display screen | 1 | 1 | Pendant 4
OR-GEN | Operating Room - General | Operating | FFE | MMTR-003.02 | TROLLEY: stainless steel, 750W x 490D x 900H nom, 2 tier | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-108 | TROLLEY: set-up, table 1250W x 800D x 900H nom | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-123 | TROLLEY: gowns/scrubs, 1220W x 610D x 1830H nominal | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-171 | TROLLEY: mayo table | 1 | 1
OR-GEN | Operating Room - General | Operating | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | optional, to store - sterile stock
OR-GEN | Operating Room - General | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | alternative impermeable seamless materials may also be acceptable, confirm material selection to suit infection prevention and control requirements
STSS | Store - Sterile Stock | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side, to be coordinated with corridor wall protection
STSS | Store - Sterile Stock | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to room side
STSS | Store - Sterile Stock | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 2 | to both sides
STSS | Store - Sterile Stock | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 2
STSS | Store - Sterile Stock | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 2
STSS | Store - Sterile Stock | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
STSS | Store - Sterile Stock | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
STSS | Store - Sterile Stock | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
STSS | Store - Sterile Stock | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | to operating room
STSS | Store - Sterile Stock | Operating | D+W | DOHI-114.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1 | to corridor, large leaf to open 170 degrees
STSS | Store - Sterile Stock | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to computer workstation
STSS | Store - Sterile Stock | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to area for workstation on wheels
STSS | Store - Sterile Stock | Operating | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | to general room lighting, controlled from 3 entry points
STSS | Store - Sterile Stock | Operating | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 3 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1
STSS | Store - Sterile Stock | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
STSS | Store - Sterile Stock | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
STSS | Store - Sterile Stock | Operating | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | FQSM-205 | SHELVING UNIT: mobile, adjustable shelves, 400D x 1200W x 2100H nominal | 1 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | FFE | FQSM-211 | SHELVING UNIT: mobile, adjustable shelves, 600D x 400W x 2100H nominal | 7 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | FFE | FQSN-141 | COMPACTUS: rail mounted | 1 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to area for workstation on wheels
STSS | Store - Sterile Stock | Operating | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | optional, to bench or wall mounted
STSS | Store - Sterile Stock | Operating | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | ITNE-223 | INPUT DEVICE: bar code scanner, medical grade, washable | 2 | 1 |  | 1 for data for tray tracking, 1 for H tracking
STSS | Store - Sterile Stock | Operating | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1
STSS | Store - Sterile Stock | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 1 | 1 |  | controlled from operating room
STSS | Store - Sterile Stock | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | controlled from operating room
STSS | Store - Sterile Stock | Operating | FFE | MMIC-491 | TROLLEY: transfer, instruments, clean | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | MMTR-104 | TROLLEY: set-up, 900W x 490D x 900H nom | 4 | 1
STSS | Store - Sterile Stock | Operating | FIN | WLFI-003 | WALL FINISH: paint, sterile areas | 1 | 1 | Wall Finish 1
STSS | Store - Sterile Stock | Operating | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 1
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.