## Room Template Data
AusHFG Standard Components - File for Import
2026-04-07
No. of Standard Components = 212
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | Full AHIA Review | 18.5 | 2700 | 1BR-BA | 2 | 15.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff intermittently (with up to 4 additional staff as required) | The 1-Bed Room - Bariatric provides space and amenities for accommodating one bariatric patient and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Bariatric (ENS-BAR), and the ensuite and bedroom should be planned as a unit. | ~ Bariatric bedrooms and ensuites are to be designed to accommodate patients up to 250kgs. The provision of super bariatric bedrooms and ensuites, for the management of patients up to 450kg, is generally restricted in jurisdictions to selected healthcare facilities only. This is to ensure that safe and effective care can be provided. Refer to HPU 340 Adult Acute Inpatient Unit for more information. ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1500mm clear is provided to the side of the bed closest to the entry door, with 1500mm clear able to be achieved to the other side of the bed with only minimal repositioning of the bed. 1500mm clear is also required to the foot of the bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ Patient lifting track requirements are to be confirmed at project level to suit clinical service requirements, patient cohort and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store, noting that bariatric cassette motors often differ to standard cassette motors so may be dedicated to and stored in bariatric bedrooms. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | Translation and QA Only | 20 | 2700 | 1BR-SP-B | 6 | 31.01.2024 |  | 24 hours | 1 patient; 1-2 visitors; up to 4 staff intermittently | A 1 Bed Room - CCU will accommodate one patient and support the delivery of a range of clinical care, minor procedures and diagnostic tests, with clinical staff requiring access to both sides of the bed. | ~ 1 Bed Room - CCU may vary in configuration to suit different Ensuite options including inboard, outboard and stacked (also known as 'back-to-back' or 'nested') configurations. In each configuration, sufficient clearance is required for equipment and staff to access both sides of the bed. ~ Glazed doors and observation windows may be provided for visibility of high acuity patients and monitoring equipment. The provision of observation windows and the use of interstitial blinds or privacy curtains is to be supported by operational models for observation as well as support for patient privacy. ~ The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring and diagnostic equipment. ~ Natural light and outlook is essential and the patient will need to have an external outlook from either the chair or the bed, preferably both. | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | Full AHIA Review | 19 | 2700 |  | 1 | 15.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff intermittently (with up to 2 additional staff as required) | The 1-Bed Room - Carer Overnight, Outboard Ensuite, Type 1 provides space and amenities for accommodating one patient, as well as one carer/family member to stay overnight, and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Inboard/Outboard (ENS-IN-OU), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to both sides of the patient bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A patient lifting track is shown as optional in this Standard Component. Provision of a lifting track, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ Furniture to accommodate a carer within the room is to be confirmed at project level, including consideration of anticipated length of stay, operational models for provision of linen, provision of carer property storage, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use. Fixed joinery items may be considered to provide this function; however, freestanding furniture is recommended where flexibility is required. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | Full AHIA Review | 19 | 2700 |  | 1 | 15.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff intermittently (with up to 2 additional staff as required) | The 1-Bed Room - Carer Overnight, Outboard Ensuite, Type 2 provides space and amenities for accommodating one patient, as well as one carer/family member to stay overnight, and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Inboard/Outboard (ENS-IN-OU), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to both sides of the patient bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A patient lifting track is shown as optional in this Standard Component. Provision of a lifting track, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ Furniture to accommodate a carer within the room is to be confirmed at project level, including consideration of anticipated length of stay, operational models for provision of linen, provision of carer property storage, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use. Fixed joinery items may be considered to provide this function; however, freestanding furniture is recommended where flexibility is required. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | Full AHIA Review | 25 | 3000 | 1BR-IC | 2 | 12.11.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff (with up to 6 additional staff as required) | The 1 Bed Room - Intensive Care provides an acuity adaptable, enclosed room for a patient requiring intensive medical treatment, nursing care and monitoring for potentially life threatening conditions. | ~ Visual access to the room from a Staff Station is required. ~ In planning of the overall department, room layouts should not be mirrored. Layout are to be "handed", with any specific items being "mirrored" to be confirmed at project level to suit clinical service requirements. ~ The dialysis machine, RO water machine, and the dialysis wall box and its associated large cooling water trap with sealed lid are optional. These items may not be provided in all services or to all bedrooms/bays within a service. Provision is dependent on the clinical service requirements in relation to the delivery of dialysis. The various dialysis therapies will have specific implications for plumbing and pipework in relation to flushing, maintenance and wastewater/effluent handling. See HPU 360 Intensive Care for more information. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door is to be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) isolation rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms refer to ‘AusHFG Part D: Infection Prevention and Control’ and ‘AusHFG Isolation Room- Engineering and Design Requirements’. ~ Overall content and configuration of the medical services pendants is to be confirmed at project level, including type and quantity of medical gases, power and data. The final arrangement will be dependent on clinical service requirements and will vary depending on clinical needs and the selection of mobile vs pendant mounted equipment. Pendants may be provided as one pendant with two arms on a single mounting point, or as single arms on multiple mounting points to increase the reach around the bed space (e.g. when the bed is located as shown or rotated 90 degrees) to support clinical care. Tertiary facilities that act as ECMO retrieval centres or otherwise perform a significant number of ECMO procedures may consider including a pendant located at the foot of the bed to enhance delivery of this treatment by supporting femoral access and connection to the required medical equipment. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from the patient bed. Clear access for bed movement must also be considered when positioning the basin; Refer to Part D Section 4.1.2-5 for more information. ~ Access to natural light and outlook is essential (with non-reflected light and views preferred). To balance this requirement with clinical requirements, the room should provide the ability to provide care with the bed in various orientations. This Standard Component shows the bed oriented vertically on the page with the head of the bed toward the window, supporting quick access by staff to either side from the entry to the room. The bed may be re-oriented to provide views to the window as a patient’s clinical state improves. The reach of the arms of the pendant should support provision of clinical care when the bed is turned 90 degrees. ~ Design to suit local cultural requirements to be considered at project level and supported by community consultation. For more information refer to ‘AusHFG Culturally Sensitive Planning and Design’ and local policies and guidance on culturally responsive design. ~ Requirements for staff notetaking/write-up within the room, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. Configurations such as a ceiling mounted arm at the foot of the bed with a computer and keyboard mounting bracket, or provision of a computer based on a fixed bench as an alternative to a workstation on wheels (WoW), may be considered and assessed at project level. Provision may be dependent on alignment with local ICT strategies, policies and workflows as well as cost impact. ~ A write-up workstation with observation windows is currently indicated directly outside the bed room (area not included calculation for the area of this Standard Component). Provision of this write up area is dependent on models of care for observation/write-up and is to be confirmed at project level. ~ Connection of the patient monitor to a central monitoring system is required. ~ Additional ICT requirements, particularly in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. ~ The configuration of the patient lifter track (i.e. linear track, H-track, pendant mounted, etc.), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) are to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Coordination of the lifter track with room lighting, pendants, examination light, patient entertainment system and any ceiling mounted services is to be carefully considered. ~ Patient entertainment systems may be mounted on the wall or ceiling. Configuration of the patient entertainment (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall or ceiling is required for mounting the patient entertainment system. ~ The ability for slave monitoring (i.e. mirror content from the pendant mounted patient monitor) to be provided through the screen for the patient entertainment system for added visibility of information in emergency situations is to be considered to suit project requirements. Where slave monitoring is not possible through patient entertainment system display screen, and is required to suit models of care, an additional slave display screen and associated services may be required. ~ A wall clock should be visible in all patient rooms. Clocks can support orientation of patients to the time of day, helping to reduce confusion and delirium. However, it has been noted they may also cause distress (e.g. from a sense of time passing too slowly or losing chunks of time). Clock products with the ability to turn off/dim the display may be considered to flexibly respond to patient preferences/needs. The placement of the clock within the room and type of clock provided, including connections to a master clock system, is to be confirmed at a project level. ~ Automation of entry doors is not recommended. As automatic doors are only able to be fully open or closed and are not designed to be kept open. This results in staff feeling isolated from support. ~ A privacy curtain is provided to the glazed door and fixed glazed panel. The use of integral blinds or switchable glass in this area may be considered at project level. In particular, the consideration of provision of switchable glass in lieu of integral blinds throughout the room would be based on an assessment of maintenance, product lifecycle and downtime requirements. For longevity of the product, switchable glass must be turned off (i.e. be opaque) for a period of time each day; this must be considered in relation to where this product is intended to be used to ensure the downtime requirement does not compromise patient observation. ~ Operational models, work health and safety requirements and IPC policies regarding the changing/laundering of privacy curtains is to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient spaces is to suit local security and WHS policies and operational service requirements. ~ Furniture to accommodate a carer within the room is to be confirmed at project level, including consideration of anticipated length of stay, operational models for provision of linen, provision of carer property storage, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use. Fixed joinery items may be considered to provide this function; however, freestanding furniture is recommended where flexibility is required. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ Lighting is to be designed support clinical observation of patients (e.g. accurate colour rendering, appropriate colour temperature, etc.) as per AS/NZS 1680. Consideration of lighting systems that are automated to support circadian rhythms (e.g. through intensity tuning, color tuning, etc.) may be considered at project level. ~ Positioning of light fixtures is to be coordinated with ceiling mounted equipment (e.g. pendant, examination light, patient lifter track, display screen, etc.) to ensure appropriate, uniform illumination of the patient for observation when needed. It is recommended to avoid direct of light fittings over the patient’s head (noting that the bed is movable and may be arranged in different configurations to meet clinical needs and equipment set-up). ~ A dedicated power outlet, clearly separate from outlets for clinical use, is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | Full AHIA Review | 16.5 | 2700 | 1BR-ST-A1, 1BR-ST-A | 6 | 15.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff intermittently (with up to 2 additional staff as required) | The 1-Bed Room - Inboard Ensuite, Type 1 provides space and amenities for accommodating one patient and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Inboard / Outboard (ENS-IN-OU), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to both sides of the patient bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A patient lifting track is shown as optional in this Standard Component. Provision of a lifting track, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | Full AHIA Review | 16.5 | 2700 | 1BR-ST-A2 | 6 | 15.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff intermittently (with up to 2 additional staff as required) | The 1-Bed Room - Inboard Ensuite, Type 2 provides space and amenities for accommodating one patient and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Inboard / Outboard (ENS-IN-OU), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to both sides of the patient bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A patient lifting track is shown as optional in this Standard Component. Provision of a lifting track, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | Full AHIA Review | 16.5 | 2700 | 1BR-IS-N2 | 2 | 15.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff intermittently (with up to 4 additional staff as required) | The 1 Bed Room - Isolation, Negative Pressure (N-Class) provides space and amenities for accommodating one patient requiring respiratory isolation to prevent the transmission of infection, and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Anteroom (ANTE) and Ensuite - Nested (ENS-NE), and the anteroom, ensuite and bedroom should be planned as a unit. | ~ Air distribution systems must provide highly effective ventilation to promote containment. Patient comfort must also be a primary consideration (i.e. room temperature, humidity, noise and air flow). The ventilation system should be designed to ensure the air flows from less contaminated areas to more contaminated areas and supply air should be provided so that air turbulence is minimised near the patient. The exhaust air flow however should be maximised near the patient to capture contaminated air. ~ It is no longer recommended that exhaust is indicated at a low level behind the bed, and it is best located over the patient on the ceiling. Locating the exhaust on the ceiling above the patient at the head of the bed with the supply air diffuser located on the ceiling close to the wall at the foot of the bed (with air directed to the walls and away from the door rather than directed towards the patient) has been shown through Computational fluid dynamics (CFD) analysis to be effective in capturing aerosols rising from a patient. Refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. - The recommended supply and exhaust locations indicated in this Standard Component are based on expert mechanical engineering advice and evidence established through CFD studies. It is acknowledged that this does not align with that suggested in AS1668.2 2024'. It is recommended that designers seek updated advice in line with the evidence noted in this guideline and pursue a performance solution where required. ~ An interlock system has been indicated to the anteroom, requiring one door to be closed before the next door is able to be opened. This reduces the potential for escape of infectious respiratory particles. This should not impact staff workflows given the time required to don or doff PPE. An emergency break glass release switch is provided to mitigate the risk of staff being entrapped within the anteroom. ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to both sides of the patient bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A patient lifting track is shown as optional in this Standard Component. Provision of a lifting track, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | Full AHIA Review | 15 | 2700 | 1BR-MH-A | 7 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/1-bed-room-mental-health-inboard-ensuite/?fullscreen=true&utm_source=project-link&rev=7 | 24 hours | 1 patient;; 1-2 staff intermittently | The 1 Bed Room - Mental Health, Inboard Ensuite provides a single occupancy bedroom for consumers in a mental health inpatient unit. The inboard ensuite layout is used in conjunction with the Ensuite - Mental Health, Inboard (ENS-MH-IN). Alternatively, a nested ensuite layout may be provided (see 1BR-MH-NE). | ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Window size and minimum sill height are to be confirmed at project level to ensure access to natural daylight and external views from the bed and seating areas within the room. The type of window covering (e.g. integral venetians, integral blackout, etc.) and associated controls are also to be confirmed at project level. ~ Doors should be selected to support safety, dignity and wellbeing. Selections should be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ The inclusion of door top or side anti-ligature alarms connected to the emergency call/duress systems may be considered and assessed at project level to confirm if these systems suit service requirements. ~ A vision panel is indicated in the door leaf for supporting observation checks by staff, which are discussed as part of care planning in consultation with the consumer. Inclusion and size of vision panel to be confirmed to suit service requirements. Controls for the integral blind to be provided to both bedroom and corridor sides of the vision panel. Switchable glass may be provided in lieu of an integral blind. Height and positioning of the vision panel is to be confirmed to support requirements for observation. ~ Rooms are to be lockable from the bedroom side, to support patient autonomy, privacy and sense of safety, with staff override/master key access from the outside for use as required. The provision of access control devices, such as card/wristband readers, is optional and provision is dependent on service requirements and operational models. Support for programming and provision of devices is required for implementation. ~ The ergonomic operation of the door hardware/handles is to be considered when doors are being selected as some products are difficult to grip for those with limited hand function. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (beds, chairs, ottomans, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ Co-ordination of the services on the ceiling is important as it is ideal to reduce visual clutter over the bed and place services out of reach from raised fixed surfaces (e.g. the bed or desk). To reduce the number of services fixtures that need to be provided on the ceiling within the bedroom, removal/relocation of emergency warning equipment such as speakers/strobes may be considered (with confirmation required by the project’s building code consultant as a performance solution). All ceiling mounted services fixtures (lights, air conditioning grilles, smoke detectors, wireless access points) are to be designed as tamper proof and anti-ligature and installed as per manufacturer's instructions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Where caulking is required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ A mirror is indicated as optional. If provided, the material of the mirror is to be confirmed at project level to suit service requirements. To ensure item is installed to be secure, tamper proof and anti-ligature, it is to be glued to a backing material and screw fixed (or equivalent installation method). ~ An adjustable height electric bed is indicated in the Standard Component. The bed may alternatively be provided as a fixed plinth type, depending on service requirements. Clearances around bed to be maintained. ~ The configurations and size of the wardrobe and bedside table for patient clothing and property storage are to be confirmed at project level to suit storage requirements and operational models for patient property storage and laundry. ~ Provision of a safe within the wardrobe joinery is optional and provision is dependent on operational models for property storage. Where a safe is provided, shelves will need to be reinforced and installation of the safe is to ensure that no gaps or ligature points are created. ~ Requirements for lighting types (general room, reading, task, night lights, sensory lighting, etc.) configuration, and controls (in-room, external controls, etc.) are to be confirmed at project level to suit requirements. ~ In this Standard Component a Patient to Staff call button has been indicated. However, staff assist and emergency call buttons have not been included on the assumption that portable call duress devices are provided to staff. Projects must confirm nurse call system requirements based on the unit’s service requirements and operational models. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The provision of USB outlets for device charging may be considered at project level in line with local policies on maintenance and electrical services provisions. ~ Provision of a wall mounted television/patient entertainment system may be considered at project level to suit local jurisdictional and operational service requirements. If provided, ensure that the screen is recessed and/or within a tamper proof and anti-ligature enclosure with appropriate fittings and sufficient ventilation. ~ Provision of sensors e.g. to detect falls and monitor high risk behaviour patterns may be considered at project level to suit service requirements and in line with local policies. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | Full AHIA Review | 15 | 2700 | 1BR-MH-C | 7 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/1-bed-room-mental-health-nested-ensuite/?fullscreen=true&utm_source=project-link&rev=7 | 24 hours | 1 patient;; 1-2 staff intermittently | The 1 Bed Room - Mental Health, Nested Ensuite provides a single occupancy bedroom for consumers in a mental health inpatient unit. The nested ensuite layout is used in conjunction with the Ensuite - Mental Health, Nested (ENS-MH-NE). Alternatively, an inboard ensuite layout may be provided (see 1BR-MH-IN). | ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Window size and minimum sill height are to be confirmed at project level to ensure access to natural daylight and external views from the bed and seating areas within the room. The type of window covering (e.g. integral venetians, integral blackout, etc.) and associated controls are also to be confirmed at project level. ~ Doors should be selected to support safety, dignity and wellbeing. Selections should be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ The inclusion of door top or side anti-ligature alarms connected to the emergency call/duress systems may be considered and assessed at project level to confirm if these systems suit service requirements. ~ A vision panel is indicated in the door leaf for supporting observation checks by staff, which are discussed as part of care planning in consultation with the consumer. Inclusion and size of vision panel to be confirmed to suit service requirements. Controls for the integral blind to be provided to both bedroom and corridor sides of the vision panel. Switchable glass may be provided in lieu of an integral blind. Height and positioning of the vision panel is to be confirmed to support requirements for observation. ~ Rooms are to be lockable from the bedroom side, to support patient autonomy, privacy and sense of safety, with staff override/master key access from the outside for use as required. The provision of access control devices, such as card/wristband readers, is optional and provision is dependent on service requirements and operational models. Support for programming and provision of devices is required for implementation. ~ The ergonomic operation of the door hardware/handles is to be considered when doors are being selected as some products are difficult to grip for those with limited hand function. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (beds, chairs, ottomans, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ Co-ordination of the services on the ceiling is important as it is ideal to reduce visual clutter over the bed and place services out of reach from raised fixed surfaces (e.g. the bed or desk). To reduce the number of services fixtures that need to be provided on the ceiling within the bedroom, removal/relocation of emergency warning equipment such as speakers/strobes may be considered (with confirmation required by the project’s building code consultant as a performance solution). All ceiling mounted services fixtures (lights, air conditioning grilles, smoke detectors, wireless access points) are to be designed as tamper proof and anti-ligature and installed as per manufacturer's instructions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Where caulking is required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ A mirror is indicated as optional. If provided, the material of the mirror is to be confirmed at project level to suit service requirements. To ensure item is installed to be secure, tamper proof and anti-ligature, it is to be glued to a backing material and screw fixed (or equivalent installation method). ~ An adjustable height electric bed is indicated in the Standard Component. The bed may alternatively be provided as a fixed plinth type, depending on service requirements. Clearances around bed to be maintained. ~ The configurations and size of the wardrobe and bedside table for patient clothing and property storage are to be confirmed at project level to suit storage requirements and operational models for patient property storage and laundry. ~ Provision of a safe within the wardrobe joinery is optional and provision is dependent on operational models for property storage. Where a safe is provided, shelves will need to be reinforced and installation of the safe is to ensure that no gaps or ligature points are created. ~ Requirements for lighting types (general room, reading, task, night lights, sensory lighting, etc.) configuration, and controls (in-room, external controls, etc.) are to be confirmed at project level to suit requirements. ~ In this Standard Component a Patient to Staff call button has been indicated. However, staff assist and emergency call buttons have not been included on the assumption that portable call duress devices are provided to staff. Projects must confirm nurse call system requirements based on the unit’s service requirements and operational models. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The provision of USB outlets for device charging may be considered at project level in line with local policies on maintenance and electrical services provisions. ~ Provision of a wall mounted television/patient entertainment system may be considered at project level to suit local jurisdictional and operational service requirements. If provided, ensure that the screen is recessed and/or within a tamper proof and anti-ligature enclosure with appropriate fittings and sufficient ventilation. ~ Provision of sensors e.g. to detect falls and monitor high risk behaviour patterns may be considered at project level to suit service requirements and in line with local policies. ~ Leakage protection devices (LPDs) such as residual current devices (RCDs) that cover the electrical services within this Standard Component are assumed to be provided in a central area within the unit (e.g. at a staff station). Location is to be confirmed at project level. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | Full AHIA Review | 17.5 | 2700 | 1BR-ST-D | 2 | 15.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff intermittently (with up to 2 additional staff as required) | The 1-Bed Room - Nested Ensuite provides space and amenities for accommodating one patient and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Nested (ENS-NE), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to both sides of the patient bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A patient lifting track is shown as optional in this Standard Component. Provision of a lifting track, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | Full AHIA Review | 29 | 2700 | 2BR-ST-A2 | 2 | 15.12.2025 |  | 24 hours | 2 patients; up to 4 visitors; 1-2 staff intermittently (with up to 4 additional staff as required) | The 2-Bed Room - Inboard Ensuite provides space and amenities for accommodating two patients and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Inboard/Outboard (ENS-IN-OU), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panels reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to the side of the patient bed adjacent to a wall, while a minimum of 950mm is provided to the side of the bed where a curtain separates the two beds. ~ This room may be utilised as a standard pressure (S-Class) isolation room to cohort infectious patients. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in wall mounted dispensers or in holders that can be attached to the end of the patient beds. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panels (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of document holders within the bedroom (typically hung on the end of the beds) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where patient monitors are provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitors. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ Patient lifting tracks are shown as optional in this Standard Component. Provision of lifting tracks, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of wardrobes and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located at the end of each bed outside the curtain and to be coordinated with lights in the corridor as required, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | Full AHIA Review | 60 | 2700 | 4BR-ST | 6 | 15.12.2025 |  | 24 hours | 4 patients; up to 8 visitors; 1-2 staff intermittently (with up to 4 additional staff as required) | The 4-Bed Room - Inboard Ensuites provides space and amenities for accommodating four patients and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Inboard/Outboard (ENS-IN-OU), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panels reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to the side of the patient bed adjacent to a wall, while a minimum of 950mm is provided to the side of the bed where a curtain separates the two beds. ~ This room may be utilised as a standard pressure (S-Class) isolation room to cohort infectious patients. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in wall mounted dispensers or in holders that can be attached to the end of the patient beds. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panels (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of document holders within the bedroom (typically hung on the end of the beds) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where patient monitors are provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitors. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ Patient lifting tracks are shown as optional in this Standard Component. Provision of lifting tracks, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of wardrobes and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located at the end of each bed outside the curtain and to be coordinated with lights in the corridor as required, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE
ADLB | ADL Bathroom | Allied Health | Translation and QA Only | 12 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff | The ADL Bathroom provides a toilet, basin with vanity, shower and bath for the training and assessment of patients in Activities of Daily Living (ADL) tasks. | ~ The room is to provide domestic facilities with grab rails and other assistive devices to be included to reflect reasonable home modifications and equipment utilised by patients. The entrance of the room is to be flush with the adjoining corridor. The door is to be fitted with escape hardware for the door to open outwards if required. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ The shower area may include a fixed raised hob to simulate a domestic scenario depending on service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ADLD | ADL Dining | Allied Health | Translation and QA Only | 12 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 patients;; 1-2 staff | The ADL Dining provides a flexible space for the training and assessment of patients in Activities of Daily Living (ADL) tasks. Typically collocated with the ADL Kitchen, the Dining room supports small group discussions and demonstrations between both rooms and provides a space for debriefing after training and assessment of ADL tasks in the Kitchen. | ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. ~ External outlook and access to natural light is desirable. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ADLK | ADL Kitchen | Allied Health | Translation and QA Only | 12 | 2700 | ADLK-OP | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 patients;; 1-2 staff | The ADL Kitchen provides an accessible space for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The space is to be functional for a range of patients including wheelchair users. | ~ The kitchen can include a combination of fittings and appliances such as a sink, cooktop, oven/grill, microwave and refrigerator to support common ADL training and assessment tasks as per service requirements. Room exhaust to be provided to range hood over cooktop. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. ~ The room may be enclosed with a lockable door depending on security requirements. ~ External outlook and access to natural light is desirable. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ADLL | ADL Laundry | Allied Health | Translation and QA Only | 8 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1 staff | The ADL Laundry provides domestic facilities for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The room will include a domestic washing machine and dryer which, if front loading models are selected, may be placed on plinths to raise machines to an accessible height to support common ADL training and assessment tasks as per service requirements. A laundry tub and storage for ironing equipment are also provided. | ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. ~ The space may be provided as an open bay that is collocated with other ADL rooms. If open, the impact of noise on adjacent areas must be considered. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
AHBF | After Hours Blood Fridge | Pathology | Translation and QA Only | 8 | 2700 | AHBBF | 4 | 07.04.2026 |  | 24 hours | 1-2 staff intermittently | The After Hours Blood Fridge is a discreet area for refrigerated storage of blood and blood products for access by authorised personnel after hours where a 24 hour pathology service is not available. | ~ This room is typically located on the periphery of a Pathology unit and may have direct, secure access to the Pathology laboratory with ready access to the transfusion service area. ~ Refrigerator temperature monitoring is required and is to be connected to the building management system (BMS). The alarm is to provide alerts where 24-hour monitoring is undertaken, within the unit and/or remotely. Temperature monitoring is to meet ANZSBT guidelines. ~ Additional fridges/freezers or lockable sections within the after hours fridge may be provided to support Pathology laboratory workflows. ~ Provision of smart fridges for blood product tracking and other ICT requirements will be based on local policies and service requirements. ~ Door width to allow for installation of fridge, including considerations for future proofing as equipment is replaced. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
AHDR | After Hours Drug Store | Clinical Support Set 1 | Translation and QA Only | 5 | 2700 |  | 4 | 07.04.2026 |  | 24 hours | 1-2 staff intermittently | The After Hours Drug Store is a secure room for the storage of medications that may be required after hours. Stock is replenished by pharmacy personnel and, depending on the location of the room, there may be direct access from within the pharmacy. | ~ Secure access to the room for authorised personnel is required. ~ A duress alarm may be required if room accessed from a public or patient care area. ~ Refrigerated storage will be required for some medications. ~ Refer to project specific requirements for automated medication management systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | Translation and QA Only | 12 | 2700 |  | 3 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | The Airlock, 12m2 is a transitional space, typically associated with an entry area or waiting/reception area, which provides wind/weather protection and supports efficient temperature regulation within the building. Final configuration of the airlock will be dependent on site, internal layout and access requirements. | ~ The Airlock is intended to be used by a wide range of people including fully ambulant people, persons using a wide range of walking aids and persons in wheelchairs. ~ The Airlock may need to support the movement of beds/trolleys (e.g. at an ambulance or transit lounge entry) requiring a configuration that provides a relatively straight path of travel. ~ Additional area to accommodate door movement and circulation will be required if entry from multiple directions provided. ~ Extent of glazing to entry doors and airlock walls to be confirmed at project level to suit façade requirements and visual access from nearby reception or security areas. Wall materials shown are indicative and will be dependent on facade design and internal layout. ~ Motorisation of doors to be confirmed by project team to suit access requirements. ~ Access control may require the provision of swipe card readers, keypads, intercoms, push to open buttons (e.g. to exit after hours), door release buttons from nearby security or reception, etc. Provision of these items will depend on security requirements and operational policies (e.g. for after-hours access). Lockdown and emergency egress requirements must also be considered. A hold open function to the internal door will also typically be required for cleaning. ~ Flooring in the Airlock typically supports the capture of dirt and moisture at the building entry to reduce cleaning requirements. Floor finishes are to be specified/detailed to reduce the risk of trips, slips and falls, (e.g. minimise changes in finished height at transitions). Drainage requirements to floor matting must be considered. ~ Depending on layout and alignment of openings when the doors are open, an air curtain may be required to prevent the entry of draughts, insects, odours, etc. ~ At public/patient entries, the provision of culturally appropriate artwork (e.g. with film on glazing) may be considered to create a welcoming atmosphere. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby upon entry in line with local infection prevention and control (IPC) policies. It is not recommended that these items are provided within the airlock so the need for users to stop within the airlock is avoided and the path of travel is kept clear. ~ A small amount of concise signage may be required within the airlock. However, it is recommended that extensive wayfinding information is made readily accessible upon entry so the need for users to stop within the airlock is avoided and the path of travel is kept clear. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | Translation and QA Only | 6 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | The Airlock, 6m2 is a transitional space, typically associated with an entry area or waiting/reception area, which provides wind/weather protection and supports efficient temperature regulation within the building. Final configuration of the airlock will be dependent on site, internal layout and access requirements. | ~ The Airlock is intended to be used by a wide range of people including fully ambulant people, persons using a wide range of walking aids and persons in wheelchairs. ~ Additional area and a layout with a relatively straight path of travel is required if the movement of beds/trolleys is to be supported. ~ Additional area to accommodate door movement and circulation will be required if entry from multiple directions provided. ~ Extent of glazing to entry doors and airlock walls to be confirmed at project level to suit façade requirements and visual access from nearby reception or security areas. Wall materials shown are indicative and will be dependent on facade design and internal layout. ~ Motorisation of doors to be confirmed by project team to suit access requirements. ~ Access control may require the provision of swipe card readers, keypads, intercoms, push to open buttons (e.g. to exit after hours), door release buttons from nearby security or reception, etc. Provision of these items will depend on security requirements and operational policies (e.g. for after-hours access). Lockdown and emergency egress requirements must also be considered. A hold open function to the internal door will also typically be required for cleaning. ~ Flooring in the Airlock typically supports the capture of dirt and moisture at the building entry to reduce cleaning requirements. Floor finishes are to be specified/detailed to reduce the risk of trips, slips and falls, (e.g. minimise changes in finished height at transitions). Drainage requirements to floor matting must be considered. ~ Depending on layout and alignment of openings when the doors are open, an air curtain may be required to prevent the entry of draughts, insects, odours, etc. ~ At public/patient entries, the provision of culturally appropriate artwork (e.g. with film on glazing) may be considered to create a welcoming atmosphere. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby upon entry in line with local infection prevention and control (IPC) policies. It is not recommended that these items are provided within the airlock so the need for users to stop within the airlock is avoided and the path of travel is kept clear. ~ A small amount of concise signage may be required within the airlock. However, it is recommended that extensive wayfinding information is made readily accessible upon entry so the need for users to stop within the airlock is avoided and the path of travel is kept clear. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ANAES | Anaesthetic Preparation Room | Operating | Full AHIA Review | 16 | 2700 | ANAE-16 | 2 | 06.05.2025 |  | Up to 24 hours | 1 patient; 1 carer / support persons; up to 3 staff | The Anaesthetic Preparation Room is for the holding and preparation of patients on a bed/trolley prior to their surgical procedure. Depending on operational processes, local, regional or general anaesthesia may be administered in this room or once the patient is taken into the Operating Room. Direct access to the Operating Room is required. | ~ Anaesthetic Preparation Rooms are typically provided to facilitate patient flow and support patient preparation. Provision to be determined during planning with consideration of local operational policies and patient throughput. ~ If serving an Operating Room with cardiac protected power, the Anaesthetic Preparation Room should also have cardiac protected power. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Ready access is required from the Anaesthetic Preparation Room to shared support spaces such as medication fridges and blanket warmer bays. ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Anaesthetic Preparation Room. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Spout and tap placement at the handwashing basin should provide sufficient height to allow washing up to the elbow. The selection of handwashing basins and tapware should be coordinated and approved by clinical staff as a single unit. Type of spout to handwashing basin (i.e. gooseneck, straight, etc.) to be confirmed to suit local infection prevention and control policies. ~ Provision of an articulated examination light or ceiling recessed examination light to be conﬁrmed to suit service requirements. ~ Depending on the use of x-ray equipment within the adjacent Operating Room, radiation shielding may be required to this room and is to be assessed by a Radiation Consultant. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
ANTE | Anteroom | Inpatient Accommodation | Full AHIA Review | 6 | 2700 | ANRM | 6 | 15.12.2025 |  | 24 hours | 1-2 staff / visitors intermittently | The Anteroom provides the space and amenities for staff and visitors to don personal protective equipment (PPE) before entering an isolation room and to doff and dispose of PPE after exiting an isolation room. The Anteroom also supports the maintenance of air pressurisation in the adjacent isolation room. | ~ Transport of trolleys and equipment through the anteroom, including large mobile items such as mobile x-ray machines, is to be confirmed to suit clinical service requirements to ensure adequate clearance is provided. Operational models for cleaning trolleys and equipment after use within the isolation room are to be confirmed at project level. ~ Provision of an intercom connected to the patient handset is to be confirmed at project level to support models of care for patient observation and communication. Intercoms may be provided within the anteroom and/or in the corridor near an observation window into the bedroom. ~ Type and quantity of PPE to be stored, and therefore the extent and configuration of the storage solution for PPE, is to be confirmed at project level to meet clinical service requirements and local infection prevention and control (IPC) policies. Storage options include trolleys, wall mounted dispensers, custom joinery or freestanding/mobile shelving/storage units. The selected storage solution must support operational models for decentralised stocking of PPE and/or decanting from a central clean store room. ~ Where seismic activity is a concern, selection of storage solutions should include consideration of elements that reduce risk of injury to persons present in the event of an earthquake (e.g. horizontal rails or lipped shelves to reduce potential for items falling, use of drawers that latch, ability to secure freestanding storage items to the building structure, whether the storage solution selected will maintain stability when subjected to certain loads/movement, etc.). Refer to relevant building codes, seismic design guidance/standards and local WHS policies. ~ The layout shown in this Standard Component does not support the movement of beds/stretchers to the bedroom via the anteroom. It assumes movement of the patient on a bed or in a wheelchair occurs through the bedroom door directly to the corridor as required. ~ Interlocking anteroom doors will reduce the escape of infectious respiratory particles by not allowing both doors to be opened at the same time. This should not impact staff workflows given the time for health care workers to don and doff their PPE. An emergency break glass release switch will mitigate the potential for staff being entrapped within the patient room or anteroom. Refer to 'Isolation Rooms - Engineering and Design Requirements' for more information. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
AUD-CR | Audiology Control Room | Allied Health | Translation and QA Only | 9 | 2700 |  | 1 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | 1 staff | The Audiology Control Room may be provided adjacent to the Audiology Testing Room to support the administering of tests that require discrete observation, result verification by a second clinician and/or remote control of equipment. The room will require a workspace and visibility of the Testing Room via an observation window. | ~ The floor of the Control Room should be flush with the floor of the Treatment Room and the adjacent corridor for access by patients in wheelchairs. Portable equipment may be shared between the Control Room and the Treatment Room. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
AUD-TR | Audiology Testing Room | Allied Health | Translation and QA Only | 14 | 2700 | AUDIO | 4 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | 1 patient; 1 carer / support person; 1-2 staff | The Audiology Testing Room provides an acoustically treated, soundproof space for clinical assessments to be carried out under controlled conditions. | ~ Testing Rooms may be modular proprietary items or constructed in situ and are generally designed as rooms within rooms in order to isolate the Testing Room from the rest of the building as much as possible. All designs should be reviewed and confirmed by an acoustic design expert. ~ The Audiology Testing Room currently indicates a layout (with an adjacent control room) that is suitable for paediatric testing. Layouts will vary to suit service requirements and the provided layout will need to be altered to suit services for older children and adults. ~ The audiometric booth is to be ventilated and connected to air-conditioning, power and data. Noise from mechanical services is to be minimised with air-conditioning to be designed for low noise operation to meet ambient noise requirements for testing. ~ The floor of the Treatment Room should be flush with the floor of the Control Room, or the adjacent corridor where a Control Room is not provided, for access by patients in wheelchairs. | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BATH | Bathroom | Sanitary Facilities | Translation and QA Only | 15 | 2700 |  | 5 | 07.04.2026 |  | 24 hours | 1 patient;; 1-2 staff assisting | The Bathroom provides facilities for assisted bathing, dressing and grooming of patients. | ~ The layout is to allow for maneuvering of a patient on a lifting device, commode chair, wheelchair or shower trolley. ~ A height adjustable bath may be provided instead of a shower trolley depending on service requirements. ~ The location of the toilet should provide sufficient space on each side to allow for staff to provide assistance from either/both sides. ~ Grab rails are to be securely fixed to the wall with the structural support required to meet weight ratings/SWL that must be confirmed at project level (generally accommodating patients up to 150kg for standard patient spaces). Provision of structural support and FF&E that is suitable for supporting bariatric patients (typically up to 250kgs) may be considered and confirmed at a project level. ~ Signage with tactile Braille nominating 'Bathroom' required to room. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BBEV | Bay - Beverage | Logistics / Support Services | Translation and QA Only | 4 | 2700 | BBEV-OP | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 persons intermittently;;; | The Beverage Bay is an area for preparation (including heating as required) of refreshments, snacks and small meals, washing some utensils, storing small mounts of food and drink and disposing of food waste (in accordance with food hygiene requirements). | ~ Beverage bays may allocated to patient care areas, staff areas and meeting/education facilities. ~ Ready access to a handwashing basin is recommended. ~ If an instantaneous boiling water tap/unit is provided, it should be hardwired and access restricted to the unit e.g. within cupboard. If system is located within a joinery unit, ensure appropriate ventilation is provided. ~ A side approach to the sink for wheelchair access has been shown; front access may be required depending on local/jurisdictional policies and service requirements. ~ The Beverage Bay should be adequately recessed to avoid encroachment into the corridor. If the space is to be enclosed and/or access is restricted, an increase in area is required. The door will require an observation panel. ~ Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. ~ Fridge dimensions will vary depending on selection and service requirements; clear area provided for the fridge is to allow for adequate ventilation and full opening of door ~ Provision and type of ice machine will be dependent on service requirements and local infection prevention and control policies. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | Full AHIA Review | 4 | 2700 |  | 2 | 31.03.2026 |  | Up to 24 hours | 1-2 patients / visitors intermittently;; 1 staff assisting as required | The Bay - Beverage, Mental Health is provided to allow consumers and support persons access to self-serve facilities for cold drinks and snacks (as determined by operational models for food service), including 24-hour access to chilled water. | ~ The Beverage Bay - Mental Health is typically collocated with consumer dining and lounge areas. ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ The temperature of hot water, if made available, should be suitable to prepare tea and coffee, with safety/locking mechanisms to control and staff only access to the water unit itself. ~ A side approach to the sink for wheelchair access has been shown; front access may be required and is to be determined at project level. ~ It is recommended that joinery is designed will finger pull edges for opening in lieu of fixed handles. Requirements for locks to cupboards and drawers are to be confirmed at project level to suit service requirements. ~ Locking/restricting access to beverage bays should be avoided where possible, but may be required depending on the service requirements of the unit. If access to the space is to be restricted, provision of an appropriate solution to enclose and lock the bay (such as roller shutter) is to be considered. Where roller shutters are provided, robustness must be considered, and design is to meet local work health and safety (WHS) requirements for manual handling of the door curtain. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ Size, type and quantity of waste bins is dependent on service requirements and environmental management policies for waste stream separation and frequency of waste removal. ~ Fridge dimensions will vary depending on the number of consumers, service requirements, operational models for food service and item selection. Adequate clear area must be provided for the fridge to allow for ventilation and full opening of door. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
BBLD | Bay - Blood Fridge | Pathology | Translation and QA Only | 2 | 2700 | BLST | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Bay - Blood Fridge is an area provided within a secure, staff only area for the storage of blood products. This bay is typically provided in critical care and operating theatre units where the pathology department is not located nearby. | ~ A pass-through layout may be developed depending on service requirements and location (e.g. in relation to limiting access to the clean area of operating theatres). ~ Refrigerator temperature monitoring is required and is to be connected to the building management system (BMS). The alarm is to provide alerts where 24-hour monitoring is undertaken, within the unit and/or remotely. Temperature monitoring is to meet ANZSBT guidelines. ~ Requirements for accurate record keeping are to be supported through operational policies and service workflows. ~ Provision of smart fridges to support blood product tracking and other ICT requirements will be based on local policies and service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BBW | Bay - Blanket / Fluid Warmer | Perioperative | Translation and QA Only | 1 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | The Bay - Blanket / Fluid Warmer provides clear area and services for a single warming cabinet. The warming cabinet may be for fluids only, blankets only or a combination of fluids and blankets. | ~ Collocation of blanket warming cabinets with linen bays is common and supports efficient workflows. ~ Locating the bay with ready access to patient areas or operating/procedure areas is recommended. ~ The capacity of warming cabinets varies and must be considered in relation to the area/number of patients to be served. The throughput of patients must also be considered as a higher turnover will require higher capacity/additional cabinets. ~ Warming cabinet sizes vary and the clear area of the bay is to suit the dimensions of the equipment selected as well as ensuring adequate space for ventilation as per manufactures specifications. The bay should deep enough to ensure that the warming cabinet itself does not impede adjacent corridor circulation. Clearance to be provided in adjacent circulation space to allow for opening of the door for intermittent use and restocking. Where fluids are kept, processes for labelling fluids need to be accommodated without impeding circulation. ~ Various cabinet configurations, including benchtop, under bench, freestanding, mobile and built-in cabinets may be selected. See manufacturer's specifications for installation requirements. ~ Temperatures for fluids need to be monitored. A data outlet, or alternative connection to suit project/equipment requirements, may be required for connection the Building Management System (BMS) depending on provision of fluid warming. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BES | Bay - Emergency Shower | Pathology | Translation and QA Only | 1 | 2700 |  | 3 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 person intermittently;;; | An unobstructed and accessible area with an emergency shower and eye wash equipment for staff who have been contaminated with toxic and/or corrosive substances. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BHW | Bay - Height/ Weight | Ambulatory Care | Translation and QA Only | 2 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient intermittently;; 1 staff intermittently | An open bay for measuring and recording the height and weight of patients. Standing scales and a stadiometer are typically provided. | ~ Chair scales may be used here or may be stored here to be used elsewhere in the department as required. ~ The type of scales and provision for bariatric patients will be dependent on service requirements. ~ The bay should deep enough to ensure that equipment does not impede adjacent corridor circulation. Design and location of bay should allow for intermittent use without significant disruption to circulation in adjacent corridor. ~ Grab rails for patient stability may be provided and may be either integral to the scales or wall mounted. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | Translation and QA Only | 1 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 person intermittently;;; | The Bay - Handwashing, Type A provides handwashing facilities for staff use in areas requiring clinical handwashing prior to undertaking selected procedures and where handwashing up to the elbow may be necessary. | ~ The basin is to be a large, wall-mounted, 'scrub' type, with hands-free taps that may be wall-mounted elbow operated, foot/knee operated or operated with electronic sensor taps. ~ Warm and cold water are to be delivered by a common spout. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | Translation and QA Only | 1 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 person intermittently;;; | The Bay - Handwashing, Type B provides handwashing facilities for staff use before and after every patient contact and visitor use as required. | ~ The basin is to be a medium, wall-mounted type, with hands-free taps that may be either wall-mounted or basin-mounted elbow operated taps. ~ Warm and cold water are to be delivered by a common spout. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BIRM-A | Birthing Room, Without Pool | Maternity | Translation and QA Only | 34 | 2700 | BIRM | 5 | 07.04.2026 |  | 24 hours | 1 mother; 1-2 support persons; up to 4 staff | The Birthing Room - Without Pool provides area and amenities for the entire birthing process including mother's preparation, active birthing exercises, relaxation and analgesia during labour, birthing, infant resuscitation, postnatal recovery and observation. The room includes an active birthing/bed zone, an area to accommodate a support person, a staff observation and write up area, an infant resuscitation area, an equipment store, and a hand hygiene area with type A handwashing basin. | ~ The room will have direct access to an Ensuite - Birthing. ~ Air should not be recirculated to other areas from the Birthing Room. Negative pressure air conditioning is required for clearance of anaesthetic gases. ~ Clinical items such as medical gases and services as well as neonatal resuscitation equipment may be concealed to support the provision of a calm environment. Even while concealed, items are to be within easy reach of the active birthing zone. ~ The availability of proprietary items for in-room infant resuscitation may change and this can inform the use of built in or mobile equipment. Overall dimensions and configuration of storage for the resuscitaire equipment are to be evaluated based on the selection of equipment and it is recommended that a test-fit is conducted, ensuring appropriate clearances are provided for emergency procedures to be undertaken, in order to confirm room layout requirements. ~ Equipment storage to be configured to suit service requirements including models for sharing equipment between multiple rooms. ~ Storage requirements within the room will vary between facilities depending on models of centralising or decanting and restocking consumables. Configuration and extent of storage to be determined based on service requirements. ~ Various supportive fixtures for active birthing are to be considered, for example, a wall mounted ladder, bench or mantlepiece for support and leaning, or ceiling mounted hooks for supportive fabrics to be hung. Consider mounting heights and providing support for various postures at multiple heights. A mother's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. ~ A fixed workstation for staff write-up and observation has been shown. Sufficient space for dual monitors may be provided as required to suit operational, EMR and ICT requirements. A workstation on wheels is also acceptable. ~ An examination light is required for suturing and small procedures. It is preferred that the light be as unobtrusive as possible and be able to be pushed away so that it is not dominating the area. ~ Lighting options to be provided, including dimmable room lighting, reading lights and night lights to provide flexible lighting across the space. Coloured lighting and calming light artworks may be considered by projects. ~ Systems, including portable items, to facilitate the selection and control of music by the mother are to be considered. Acoustics treatment may be required to support this without disruption to adjacent rooms. ~ Provision of a telephone for patient use will be dependent on the operational model for transferring calls. ~ Natural light and outlook essential. Window sill to be low enough to see view while laying in bed. Treatment, to windows to allow blinds to be kept open as desired but privacy to be maintained, may need to be considered depending on overlook from nearby buildings. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BIRM-B | Birthing Room, With Pool | Maternity | Translation and QA Only | 40.5 | 2700 |  | 2 | 07.04.2026 |  | 24 hours | 1 mother; 1-2 support persons; up to 4 staff | The Birthing Room - With Pool provides area and amenities for the entire birthing process including mother's preparation, active birthing exercises, water immersion during labour, relaxation and analgesia during labour, birthing, infant resuscitation, postnatal recovery and observation. The room includes an active birthing/bed zone, birthing pool an area to accommodate a support person, a staff observation and write up area, an infant resuscitation area, an equipment store, and a hand hygiene area with type A handwashing basin. | Birthing Pool: ~ The use of birthing pools should be based on local policies and protocols for water immersion during labour and birth. ~ Birthing pools can vary significantly in shape and the pool shown on the RLS is indicative only. Final selection may have implications for required area and clearances. ~ The birthing pool must be deep and wide enough for effective water immersion for pain relief during labour and birth. ~ Ergonomic assessment of birthing pool options should be undertaken prior to selection, including the height of the pool for mothers getting into and out of the pool, as well as access for staff assisting the mother from the side of the pool. The location of grabrails and supports, including those integral with the bath design are to be considered to support transfers without impeding access to the mother by staff. ~ Pools may be installed with steps built around them to provide easy access into the pool from a seated position. Provision of stairs is to be assessed to ensure they do not limit access with floatation transfer devices in the event of an emergency. Handrails to be provided to stairs to reduce risk of slips in wet area around the pool. ~ A ceiling mounted hoist has not been included as there are better and more timely ways to remove a mother from the birthing pool should her condition deteriorate. ~ Consideration for ready access to floatation devices for transfer from the pool is required. ~ The tapware and drain for the birthing pool are to be carefully considered. Taps need to allow the bath to be filled rapidly. Water also needs to be able to be drained quickly, preferably without needing to reach into the bath after birthing. Other Considerations: ~ The room will have direct access to an Ensuite - Birthing. ~ Air should not be recirculated to other areas from the Birthing Room. Negative pressure air conditioning is required for clearance of anaesthetic gases. ~ Clinical items such as medical gases and services as well as neonatal resuscitation equipment may be concealed to support the provision of a calm environment. Even while concealed, items are to be within easy reach of the active birthing zone. ~ The availability of proprietary items for in-room infant resuscitation may change and this can inform the use of built in or mobile equipment. Overall dimensions and configuration of storage for the resuscitaire equipment are to be evaluated based on the selection of equipment and it is recommended that a test-fit is conducted, ensuring appropriate clearances are provided for emergency procedures to be undertaken, in order to confirm room layout requirements. ~ Equipment storage to be configured to suit service requirements including models for sharing equipment between multiple rooms. ~ Storage requirements within the room will vary between facilities depending on models of centralising or decanting and restocking consumables. Configuration and extent of storage to be determined based on service requirements. ~ Various supportive fixtures for active birthing are to be considered, for example, a wall mounted ladder, bench or mantlepiece for support and leaning, or ceiling mounted hooks for supportive fabrics to be hung. Consider mounting heights and providing support for various postures at multiple heights. A mother's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. ~ A fixed workstation for staff write-up and observation has been shown. Sufficient space for dual monitors may be provided as required to suit operational, EMR and ICT requirements. A workstation on wheels is also acceptable. ~ An examination light is required for suturing and small procedures. It is preferred that the light be as unobtrusive as possible and be able to be pushed away so that it is not dominating the area. ~ Lighting options to be provided, including dimmable room lighting, reading lights and night lights to provide flexible lighting across the space. Coloured lighting and calming light artworks may be considered by projects. ~ Systems, including portable items, to facilitate the selection and control of music by the mother are to be considered. Acoustics treatment may be required to support this without disruption to adjacent rooms. ~ Provision of a telephone for patient use will be dependent on the operational model for transferring calls. ~ Natural light and outlook essential. Window sill to be low enough to see view while laying in bed. Treatment, to windows to allow blinds to be kept open as desired but privacy to be maintained, may need to be considered depending on overlook from nearby buildings. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BLIN | Bay - Linen | Logistics / Support Services | Translation and QA Only | 2 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | The Bay - Linen is a recessed bay to accommodate a clean linen supply or exchange trolley. | ~ The bay may be enclosed with hinged doors, sliding doors or a roller shutter where items need to be secured or enclosed. An open bay is acceptable if a covered trolley is supplied (as required by local infection control policies). ~ Where lockable, hinged doors are provided, hold open hardware may be required to support easy movement of the trolley in and out of the bay. Door protection to suit movement of beds and equipment in adjacent area. ~ Where a roller shutter is provided, the weight of the shutter, manual handling requirements and minimising the noise of the shutter when opening are to be considered. ~ If bay is enclosed, a light switch or sensor may be required to provide adequate lighting when linen stock is accessed. ~ Storage for additional items such as pillows, shower curtains, privacy curtains, etc. may be provided as either joinery, a modular shelving system, a wall mounted panel with wire baskets or a mobile trolley. The storage solution will be dependent on items to be stored and if items need to be secured or covered due to infection control requirements. Inclusion of storage should consider size and manoeuvrability of the linen trolley to be used to ensure adequate clearance. ~ Linen trolleys can vary in height and often require a cover that is lifted from the top. In this instance, shelving above the trolley is not recommended. If the trolley is of a suitable height and a shelf is provided, it is to be mounted no higher than 1800AFFL and the reach over trolley is to be considered. ~ Hooks may be provided for clean linen bags and may be differentiated for clinical, general and patient's personal linen. Linen bags on hooks should be able to be accessed without moving the trolley. ~ Bay - Linen may sometimes be combined with Bay - Blanket / Fluid Warmer (see Standard Component BBW for additional space, FF&E and services requirements). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | Translation and QA Only | 4 | 2700 | BMEQ-4 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | An open bay for storage and recharging frequently used mobile equipment. Equipment may include wheelchairs, mobile scales, commode chairs, patient lifting devices or observation/diagnostic equipment. | ~ The bay should deep enough to ensure that equipment does not impede adjacent corridor circulation; a depth range from 800mm to 1500mm is recommended. Consider the manoeuverability of equipment to be stored as some items may have large turning circles and will need to be parked perpendicular, requiring a deeper bay. Power outlets may be located on the sides of deeper bays to be accessible when equipment is parked. ~ If portable imaging equipment is to be stored additional area may be required. Data outlets may be required depending on equipment. ~ Equipment may be recharged while stored in this space; provision of appropriately located power outlets is required. ~ Items may be hung in this bay, e.g. a patient slide, and appropriate in-wall supports are required for mounting hooks. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | Translation and QA Only | 3 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 staff intermittently | The Bay - Multifunction Device, 3m² provides an open bay with the space and amenities to support printing, scanning and photocopying, storage of stationery, and waste management for paper recycling and secure document disposal. | ~ Ventilation requirements for multifunction device to be confirmed at project level to suit selected equipment. ~ Clearance area around the multifunction device is required to allow users to easily open panels on the equipment, e.g. for refilling paper, changing ink and clearing paper jams. Clearance requirements will be dependent on selected equipment specifications. ~ Adjacent circulation space must allow for intermittent use and restocking of the bay. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | Translation and QA Only | 7 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Bay - Multifunction Device, 7m² provides an open bay with the space and amenities to support printing, scanning and photocopying, storage of stationery, and waste management for paper recycling and secure document disposal. | ~ Ventilation requirements for multifunction device to be confirmed at project level to suit selected equipment. ~ Clearance area around the multifunction device is required to allow users to easily open panels on the equipment, e.g. for refilling paper, changing ink and clearing paper jams. Clearance requirements will be dependent on selected equipment specifications. ~ Adjacent circulation space must allow for intermittent use and restocking of the bay. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BMT | Bay - Meal Trolley | Logistics / Support Services | Translation and QA Only | 4 | 2700 | BMT-4 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | The Bay - Meal Trolley is a recessed bay to accommodate meal trolleys during meal delivery and collection times. | ~ The size and type of meal trolleys to be accommodated will be dependent on service requirements and food service models (re-thermalisation, cook fresh, cook chill, mid-meals, etc.) and will need to be confirmed to inform spatial and services requirements. ~ Consider manoeuvrability of the meal trolley to be used to ensure adequate clearance. Most meal trolleys have 2 x fixed and 2 x swivel wheels which limit movement to position in the bay. Bay may be designed without one end wall to improve trolley access and reduce WHS risks from push/pull movements with certain types of trolleys. ~ The Bay should be deep enough to ensure trolleys do not impede corridor circulation; minimum recommended depth is 1200mm, however, the depth may need to increase to 1500mm depending on the trolley selected. ~ Special power may be required for re-thermalisation trolleys. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | Translation and QA Only | 3 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Bay - Pathology Point of Care Testing (POCT) provides the area and facilities for the preparation and testing of specimens close to patient care areas allowing for rapid results to improve clinical decision making and patient care. | ~ Two benchtop POCT devices have been indicated, with additional devices requiring added space and services. The devices shown are placeholders as there are many POCT devices available and various combinations of devices may be provided depending on the service requirements of the unit in which this bay is located. ~ Ready access to handwashing bay is recommended. ~ Ready access may be required to a pneumatic tube bay that is in a staff supervised area. ~ If providing wall mounted joinery over the bench consider clearance heights for benchtop machines, including for futureproofing. ~ Weight requirements for machines should be considered to ensure adequate support is provided to the bench. ~ POCT devices should not to be located in direct sunlight as they can overheat. ~ Refrigerator temperature monitoring may be required and is to be connected to the building management system (BMS). The alarm is to provide alerts where 24-hour monitoring is undertaken, within the unit and/or remotely. ~ Type and extent of storage to suit testing requirements, including ambient temperature storage for cartridges. ~ Ensure adequate lighting over workspace. ~ Power requirements (type/quantity) to be considered to suit equipment and service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BPROP | Bay - Property, Staff | Staff Amenities | Translation and QA Only | 2 | 2700 | PROP-2 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 staff intermittently | The Bay - Property, Staff provides the space and fit-out for the secure storage of property including clothing, bags and personal effects. The number of lockers provided will be dependent on staff complement per shift. | ~ Approximately 1m2 will be required for each additional 3 x tiers of lockers. Each tier may provide up to 4 lockers. ~ Lockers may be provided as freestanding items or built-in joinery. ~ A proportion (minimum 2%) of lockers may be required to be accessible with locking devices located between 900mm to 1100mm AFFL. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BPTS | Bay - Pneumatic Tube Station | Pathology | Translation and QA Only | 1 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed by staff intermittently | The Bay - Pneumatic Tube Station (PTS) provides an area for dispatching and receiving of items via the pneumatic tube system. | ~ This Standard Component represents a department based bay and additional area, FFE and services will be required for a central receiving and processing area in a pathology or pharmacy department. ~ To be collocated or located with clear oversite from a staff station or within a staff only area. ~ Arrival notification alarms must be programmable for different times and scenarios depending on service requirements. ~ Security requirements are to be considered. If the station is to receive deliveries from Pharmacy or is in an area accessed by the public then secure access to a lockable receiving basket may be required depending on location of the bay. ~ Station may be a pass through or end station and receive/dispatch through the floor or ceiling depending on location and system configuration. ~ Radio frequency identification (RFID) technology may be considered by projects to reduce errors, improve traceability and to enable dynamic/intuitive routing to reduce "traffic jams". This technology involves embedded RFID tags in cannisters that are read by receivers at tube stations on dispatch/arrival and at interchange points in the system. ~ Where multiple services send/receive products via the pneumatic tube system, e.g. pathology and pharmacy, colour coding the cannisters for the different streams is recommended. Colour coding to differentiate between cannisters from high priority areas, e.g. emergency and intensive care vs general wards may also be considered. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | Translation and QA Only | 1.5 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | A open bay to provide supervised holding of the resuscitation trolley and associated equipment. The bay should be located close to a Staff Station. Rapid access to the trolley and from this bay to patient areas is essential. | ~ Requirements for specialised resuscitation trolleys should be considered (e.g. specific trolleys are required for paediatric and neonatal departments and non-magnetic trolleys are required for some medical imaging modalities). ~ If a department requires more than one type of resuscitation trolley to be accommodated in their bay (e.g. both adult and paediatric trolleys) additional area will be required. ~ Additional equipment, such as ECG machines, may be accommodated in this bay in some departments. ~ The bay shall be a minimum depth of 800mm to ensure that equipment does not impede adjacent corridor circulation. ~ A patient slide may need to be readily available if the resuscitation trolley is required and may be provided within this bay. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
B-SCRUB | Bay - Scrub | Operating | Full AHIA Review | 4 | 2700 | SCRB-4 | 2 | 06.05.2025 |  | Up to 24 hours | up to 3 staff | The Bay - Scrub room provides an area and facilities for performing surgical hand antisepsis prior to entering the Operating Room and donning sterile gloves and gowns. Surgical hand antisepsis is performed to substantially reduce the number of micro-organisms on the hands prior to performing any aseptic or surgical procedure. | ~ Number of taps and soap/hand-rub dispensers to be confirmed to suit staffing and service requirements. ~ A minimum of 900mm is required between taps to allow for sufficient space for taps to be used simultaneously. ~ Taps to be non-touch, either operated with sensor activation or elbow levers. ~ Provision of a shelf above the scrub trough to be confirmed at project level to suit service requirements (considering provision of dispensers/holders, cleaning protocols and mounting height provision to suit workplace health and safety policies). ~ Height and type of wall finish to suit local infection prevention and control policies and rigorous cleaning regimes. Provision and height of corner guards as required to provide protection from anticipated mobile equipment movement. ~ Depending on proximity of this room to the Operating room and the use of x-ray equipment during procedures, radiation shielding may be required to some walls of this room and is to be assessed by a Radiation Consultant. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
BVM | Bay - Vending Machine | Public Areas | Translation and QA Only | 2 | 2700 | BVM-3 | 6 | 07.04.2026 |  | Available 24 hours (dependent on unit operating hours) | 1-2 persons intermittently;;; | The Bay - Vending Machine provides the space and services for vending machines in public and staff areas. The area may be in a recessed bay along a corridor or in an open area and should be located to ensure adjacent circulation paths are not impeded with intermittent use. | ~ Each additional vending machine will require approximately 1.5m2 of additional area as well as associated services. ~ Sufficient clearance is required around the machines for manoeuvring in the case of removal for maintenance, repair or replacement. Bulkheads and joinery surrounds may be provided to prevent users from tipping or shaking machines but should be designed to allow for access for repairs and maintenance or be removable. ~ Vending machines for products other than food and drink, such as for toiletries, phone charging accessories, etc. that may be useful to patients, visitors, and staff, e.g. for unexpected overnight stays, and at end of trip areas for staff, may also be considered. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby in line with local infection prevention and control (IPC) policies. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BWC | Bay - Wheelchair Park | Ambulatory Care | Translation and QA Only | 4 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | An open bay for storing wheelchairs. Typically located in close proximity to the main entrance or department entry. | ~ The bay should be deep enough to ensure that wheelchairs do not impede adjacent circulation space ~ A minimum depth of 1300mm is recommended. ~ The ability to secure wheelchairs (e.g. with locks or by enclosing the bay) to be considered as required. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
BWTR | Bay - Water Fountain | Public Areas | Translation and QA Only | 1 | 2700 | BWD-1 | 4 | 07.04.2026 |  | Available 24 hours (dependent on unit operating hours) | 1 person intermittently;;; | The Bay - Water Fountain is typically associated with a main entry lobby or waiting area, and provides area, fittings and services connections for a drinking water fountain. | ~ The water fountain may be in a recessed bay or in an open area and should be located to ensure adjacent circulation paths are not impeded by intermittent use. ~ A water dispenser with a spout to fill disposable cups or refill drink bottles is recommended. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby in line with local infection prevention and control (IPC) policies. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CHPT | Change Cubicle - Patient | Sanitary Facilities | Translation and QA Only | 2 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient intermittently;; | The Change Cubicle - Patient provides the area and amenities required for ambulant patients to change into a hospital gown or appropriate clothes prior to physical therapy, examination, diagnostic imaging, treatment, procedures or surgery, and to re-dress afterwards. The cubicle should provide facilities for temporarily hanging clothes and a bench seat or chair for the patient to sit on whilst changing. | ~ Provision of a door, cubicle partition system, or privacy curtain to enclose the change cubicle is to be determined to suit patient cohort and service requirements. Where possible, the cubicle should be located so the entry opening is discreet and not facing into high traffic areas. ~ Where door is provided it must swing outward. For door to swing inward, additional area for circulation and emergency release hardware is required. In both cases it is required that the door can be opened from the outside in an emergency. ~ The selection of door hardware, namely handles and locks/privacy latches, must ensure usability by people with limited dexterity and motor skills. ~ Lighting control may be provided external to the change cubicle to serve a number of change cubicles in an area, particularly where cubicle systems or privacy curtains are provided. Enclosed change cubicles may have individual light switches or motion controlled lighting. ~ Where two-way access is provided, e.g. from a corridor and directly from a treatment or imaging room, additional area may be required to provide appropriate circulation at the second entry. ~ Where adjacent or with direct access to an imaging room or treatment room where imaging devices are used, the change room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant. ~ Where paediatric services are provided, additional area within change cubicles will be required to support parents/carers assisting children to change. The provision of multiple benches with different seating heights (450mm-520mm for adults and 350mm for children) may also be considered to support paediatric patients. ~ Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. ~ A chair may be provided in lieu of a bench seat depending on patient cohort and service requirements. The depth of the seat for both chair and bench seat options is to be adequate to support movement while changing, and the weight rating of all seating, including provision for bariatric capacity, is to be considered. The colour of seating is to contrast with the flooring and walls to support visibility and reduce the risk of falls. ~ An operational model for responding to calls from staff/patients will be required to support the provision of the patient to staff call button, staff assist call button and emergency call button, and inclusion is to be determined based on service requirements. Additional staff assist and emergency call buttons my be located outside of the cubicle and shared between a number of change rooms depending on service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | Translation and QA Only | 12 | 2700 |  | 3 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 3 patients intermittently;; | The Change Room - Patient provides the area and amenities required for ambulant patients to change into appropriate clothes prior to physical therapy or hydrotherapy sessions, and to re-dress and perform personal ablutions afterwards. | ~ Change Rooms are typically divided into gender specific areas on a proportional basis. and will include Change Cubicle, Toilet, handbasin and lockers for secure storage of personal property. ~ Operational models for handling patient belongings are to be considered. The change room may include facilities for temporarily storing clothes, or close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. ~ Grab rails are to be securely fixed to the wall with the structural support required to meet weight ratings/SWL that must be confirmed at project level (generally accommodating patients up to 150kg for standard patient spaces). Provision of structural support and FF&E that is suitable for supporting bariatric patients (typically up to 250kgs) may be considered and confirmed at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | Translation and QA Only | 4.5 | 2700 | CHPT-D | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient intermittently;; 1 staff / carer assisting as required | The Change Cubicle - Patient, Accessible provides the area and amenities for patients using wheelchairs, walking aids and/or requiring assistance to change into a hospital gown or appropriate clothes prior to physical therapy, examination, diagnostic imaging, treatment, procedures or surgery, and to re-dress afterwards. The cubicle should provide facilities for temporarily hanging clothes and a bench seat or chair for the patient to sit on whilst changing. | ~ Provision of a door, cubicle partition system, or privacy curtain to enclose the change cubicle is to be determined to suit patient cohort and service requirements. Where possible, the cubicle should be located so the entry opening is discreet and not facing into high traffic areas. ~ Where door is provided it must swing outward. For door to swing inward, additional area for circulation and emergency release hardware is required. In both cases it is required that the door can be opened from the outside in an emergency. ~ The selection of door hardware, namely handles and locks/privacy latches, must ensure usability by people with limited dexterity and motor skills. ~ Lighting control may be provided external to the change cubicle to serve a number of change cubicles in an area, particularly where cubicle systems or privacy curtains are provided. Enclosed change cubicles may have individual light switches or motion controlled lighting. ~ Where two-way access is provided, e.g. from a corridor and directly from a treatment or imaging room, additional area may be required to provide appropriate circulation at the second entry. ~ Where adjacent or with direct access to an imaging room or treatment room where imaging devices are used, the change room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant. ~ Where paediatric services are provided, additional area within change cubicles will be required to support parents/carers assisting children to change. The provision of multiple benches with different seating heights (450mm-520mm for adults and 350mm for children) may also be considered to support paediatric patients. ~ Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. ~ The depth of the seat is to be adequate to support movement while changing, and the weight rating of all seating, including provision for bariatric capacity, is to be considered. The colour of seating is to contrast with the flooring and walls to support visibility and reduce the risk of falls. ~ An operational model for responding to calls from staff/patients will be required to support the provision of the patient to staff call button, staff assist call button and emergency call button, and inclusion is to be determined based on service requirements. Additional staff assist and emergency call buttons my be located outside of the cubicle and shared between a number of change rooms depending on service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CHST-10 | Change - Staff, 10m2 | Staff Amenities | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 3 staff intermittently | The Change - Staff, 10m2 provides the space and fit-out for staff to change into appropriate work clothing or gowns, to store their street clothing and to perform personal ablutions. The room may be comprised of a combination of showers, toilets, basins and lockers, with numbers to suit service and staff requirements. | ~ Change rooms are typically allocated as separate male and female areas and sized on a proportional basis. ~ Secure storage for personal property (e.g. lockers) may be provided within the change room or separately within the unit dependent on operational policies and service requirements. ~ Accessible change facilities for staff to be provided nearby. ~ A proportion (minimum 2%) of lockers may be required to be accessible with locking devices located between 900mm to 1100mm AFFL. ~ Secure, staff-only access to change rooms is required. ~ Visual privacy from the entry door to the changing areas and cubicles is to be considered during planning. ~ If provided for staff to change for sterile procedures, access to clean linen will be required | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CHST-35 | Change - Staff, 35m2 | Staff Amenities | Translation and QA Only | 35 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 16 staff intermittently | The Change - Staff, 35m2 provides the space and fit-out for staff to change into appropriate work clothing or gowns, to store their street clothing and to perform personal ablutions. The room may be comprised of a combination of showers, toilets, basins and lockers, with numbers to suit service and staff requirements. | ~ Change rooms are typically allocated as separate male and female areas and sized on a proportional basis. ~ Secure storage for personal property (e.g. lockers) may be provided within the change room or separately within the unit dependent on operational policies and service requirements. ~ Accessible change facilities for staff to be provided nearby. ~ A proportion (minimum 2%) of lockers may be required to be accessible with locking devices located between 900mm to 1100mm AFFL. ~ Secure, staff-only access to change rooms is required. ~ Visual privacy from the entry door to the changing areas and cubicles is to be considered during planning. ~ If provided for staff to change for sterile procedures, access to clean linen will be required | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | Translation and QA Only | 60 | 3000 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; up to 6 staff | A highly specialised procedure room where interventional Cardiac Catheter procedures are undertaken in an aseptic environment and may include administration of sedation or general anaesthesia. | ~ The Catheter Laboratory - Electrophysiology Studies may also be used for electrophysiology (EP) studies and treatment and is typically only provided in hospitals of tertiary level or higher, where required. ~ A Control room will be located adjacent and may serve more than one procedure room. ~ A clinical scrub area should be located immediately adjacent to the room staff entry. ~ Radiation shielding as advised by Radiation Consultant. ~ A strut channel system able to carry moving loads may be required. ~ Cable ducts from Control Room and Equipment room will be required. ~ 'X-Ray in Use' lights are required outside each entry door. ~ Power to imaging equipment should be on emergency supply. ~ The Catheter Laboratory for EP studies will require radiofrequency shielding. | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | Translation and QA Only | 55.5 | 3000 | CLAB | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; up to 6 staff | A procedure room where interventional Cardiac Catheter procedures are undertaken in a controlled, clean environment and may include administration of sedation or, much less commonly, general anaesthesia. | ~ A Control room will be located adjacent and may serve more than one procedure room. ~ A clinical scrub area should be located immediately adjacent to the room staff entry. ~ Radiation shielding as advised by Radiation Consultant. ~ A strut channel system able to carry moving loads may be required. ~ Cable ducts from Control Room and Equipment room will be required. ~ 'X-Ray in Use' lights are required outside each entry door. ~ Power to imaging equipment should be on emergency supply. | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | Translation and QA Only | 17 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 staff | Room adjacent to Catheter Lab EP Procedure Room/s with direct visibility to the patient for remote control of equipment, and review and reporting of images. | ~ The Control Room may serve two procedure rooms. ~ Radiation shielding as advised by Radiation Consultant. ~ Cable ducts from Catheter Lab Procedure Room and Computer/Equipment room will be required. | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | Translation and QA Only | 14 | 2700 | CLCRT | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 3 staff | Room adjacent to Catheter Lab Interventional Procedure Room/s with direct visibility to the patient for remote control of equipment, and review and reporting of images. | ~ The Control Room may serve two procedure rooms. ~ Radiation shielding as advised by Radiation Consultant. ~ Cable ducts from Catheter Lab Procedure Room and Equipment room will be required. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | Translation and QA Only | 10 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Clean Store, 10m2 provides space for the storage of clean consumables and equipment for patient care. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | Translation and QA Only | 20 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Clean Store / Medication Room, 20m2 provides a small space for the storage of clean consumables and the secure storage of medications, including intravenous fluids. | ~ This room may provide storage for drugs of dependence in accordance with relevant legislation. ~ Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. ~ Secured staff only access to the room is required. ~ The provision and placement of CCTV cameras is dependent on jurisdictional policies. ~ Refer to project specific requirements for the provision of automated medication management systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | Translation and QA Only | 8 | 2700 | CLUR-8 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Clean Store / Medication Room, Sub provides a small space for the storage of clean consumables and the secure storage of medications, including intravenous fluids. | ~ This room may provide storage for drugs of dependence in accordance with relevant legislation. ~ Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. ~ Secured staff only access to the room is required. ~ The provision and placement of CCTV cameras is dependent on jurisdictional policies. ~ Refer to project specific requirements for the provision of automated medication management systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLNUP | Clean-Up Room | Operating | Full AHIA Review | 12 | 2700 | CLUP-10 | 2 | 06.05.2025 |  | Up to 24 hours | 1-2 staff | The Clean-Up Room provides space and amenity for gross decontamination of instruments used in Operating Rooms or Procedure Rooms, storage for cleaning supplies and equipment, as well as storage of waste prior to collection. A Clean-up Room can serve multiple Operating Rooms or Procedure Rooms and should be located nearby to support post procedure processes. | ~ Clearance around the surgical waste management system and docking station, as informed by equipment specifications, is to be maintained at all times. ~ The requirement to provide a door to this room will vary across jurisdictions and is to be confirmed to suit local infection prevention and control policies. ~ Number, size and type of bins, including sharps, to be confirmed to suit waste management policies and service requirements. ~ Provision of cleaner's sink to be confirmed to suit operational policies and service requirements. ~ Type of spout provided to handwashing basin (i.e. gooseneck, straight, etc.) to be confirmed to meet local infection prevention and control policies. ~ Backflow prevention device requirements to be confirmed for all hydraulic fixtures to suit service requirements. ~ Air-conditioning and exhaust requirements to be confirmed to suit service requirements (i.e. extent of gross decontamination of instruments occurring within this room), operational processes (e.g. frequency of waste removal), and equipment selection. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
CLRM | Cleaner's Room | Logistics / Support Services | Translation and QA Only | 5 | 2700 | CLRM-5 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Cleaner's Room is a secure room for the storage and decanting of cleaning materials, washing and storage of cleaning equipment and cleaner's trolley, and for liquid waste disposal. | ~ This room may be shared between multiple units depending on service requirements. ~ Size requirements for a Cleaner's Room will be dependent on the department to be serviced and operational models for staffing and cleaning regimens that may dictate the type of equipment and number of trolleys to be accommodated. Where more than one trolley will be stored an additional 1.5m2 is required per trolley. ~ The requirements to accommodate vacuum cleaners, floor scrubbers or other floor cleaning equipment within the Cleaners Room is to be determined at a project/department level in conjunction with assessment of finishes and cleaning requirements. Where operational models do not provide a centralised area for the storage of large cleaning equipment (e.g. floor scrubbers), additional area may be required in units or in shared areas between units depending on the additional equipment to be stored. ~ Considerations regarding detergent/chemical management system to be confirmed at a project level, including water connection and associated services requirements (including back flow prevention). ~ Extent and type of storage for chemicals and consumables is to suit service requirements. Consideration of the weight of chemical bottles is required when determining appropriate storage solutions (i.e. if storing chemicals in bottles over 1 litre then low-height shelving is required to avoid lifting of heavy items from high shelves). ~ Hold open door hardware may be provided for hinged doors to allow for easy movement of trolleys in and out of the room. ~ Controlled, staff-only access may be required if this room is provided in a public or patient care area. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | Translation and QA Only | 7 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff | The Clean-Up Room is used for holding of used trolleys and articles from a procedure Room or catheter laboratory. Items may be sorted, rinsed or disposed of and dispatched to waste holding/ sterilising areas as appropriate. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
COMM | Communications Room | Logistics / Support Services | Translation and QA Only | 15 | 2700 |  | 6 | 07.04.2026 |  | 24 hours | 1-2 persons intermittently;;; | A secure room for engineering services to accommodate racks, backbone cabling and interface control panels for information and communication systems. Systems may include master antenna television (MATV), internet protocol television (IPTV), nurse call, security, telecommunications, building management system (BMS) and Fire/EWIS systems. | ~ The area shown is indicative; the size of the Communications Room will vary according to engineering consultant advice based on systems to be accommodated. ~ Head end units for security, nurse call, BMS, TMV, IPTV/MATV to be accommodated as required. ~ Equipment located in this room will require uninterruptible power fed from the essential supply (generator). ~ Dedicated air conditioning that is monitored by the Building Management System (BMS) is required ~ Provide adequate lighting to ensure visibility to both front and rear of racks. ~ The configuration of power and data (i.e., wall mounted or ceiling mounted services) to supply the racks is to be determine base on the room layout and equipment selected. ~ The Communication Room must be located such that it is not susceptible to possible water damage or excessive electromagnetic interference. Water or gas pipes must not pass through a Communication Room. ~ Where a Distributed Antenna System (DAS) for in-building mobile reception is provided, the telco carrier base station equipment is to be located in the Communications Room. Refer to telco for spatial requirements to determine sizing of the Communications Room. A DAS shall conform to the most recent edition of the Mobile Carriers Forum Design Specification for Distributed Antenna Systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CONS | Consult Room | Ambulatory Care | Translation and QA Only | 12 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient; 1-2 visitors; 1-2 staff | The Consult Room will provide for private consultation and physical examination of patients with or without support persons present. | ~ A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | Full AHIA Review | 16 | 2700 |  | 9 | 31.03.2026 |  | Up to 24 hours | 1 patient; 1 visitor; 1-2 staff | The Consult Room ENT/ Ophthalmology provides the space, equipment and services for consultation, assessment, examination and minor treatment and observation of patients for acute ENT and Ophthalmology related injury and illness with specialised equipment. | ~ This Standard Component is intended to support minor treatments. Where patients require sedation (including with nitrous oxide) access to a larger procedure room is required. ~ Where this room may also be used for general consultation, specialised equipment for ENT and Ophthalmology must be able to be stored within a lockable cupboard or store room. ~ Eye testing with a visual acuity chart and mirror requires a 6m distance from the chart to the patient when chart is reflected. ~ Vision panels within the door(s) are to have a cover to enable blackout of the room for eye testing as determined by clinical services requirements. ~ An eye wash station has been indicated within the room. Disposable eye wash bottles may be considered in conjunction with or instead of a fixed eye wash station depending clinical services requirements and local IPC policies. ~ Acoustic treatments may be required to minimise reverberation for ENT testing and are to be determined suit clinical services requirements. All acoustic finishes must meet IPC requirements (Refer to Part D: Infection Prevention and Control for more information). ~ A second door may be required for staff egress and provision will be dependent on local Work Health and Safety (WHS) policies. The location of the second door will be dependent on the overall department plan and availability of an appropriate area to egress. ~ The weight capacity of the examination chair selected must be considered to suit a wide range of patient requirements. ~ The clear area required on each side of the examination chair for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Ready access to medications, including refrigerated medications, is required. A small medication fridge with temperature monitoring, connected to building management system (BMS), may be provided within the room depending on local operational models for medication management. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical services requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins provided, including sharps bins, will be dependent on clinical services requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
CONS-UN | Consult Room - Universal Access | Ambulatory Care | Translation and QA Only | 17 | 2700 |  | 2 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient; 1-2 visitors; 1-2 staff | The Consult Room - Universal Access will provide for private consultation and physical examination of a range of patients with or without support persons present. | ~ The spatial allowance will accommodate patients who (a) are using a wheelchair, including a bariatric sized wheelchair; or (b) require a hoist to transfer. ~ The position of the basin, dispensers and other fittings also allows for use by staff in wheelchairs. ~ A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. ~ It is anticipated that one of these rooms may be provided within a 'pod' of consult rooms. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | Translation and QA Only | 0 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) |  | The Corridor - Patient Treatment Areas indicates requirements for circulation spaces between patient treatment spaces, patient accommodation and clinical support spaces within departments. | ~ Corridor widths will vary between departments and will depend on the requirement for frequent bed transportation; widths must allow for the safe movement and passing of trolleys, beds, wheelchairs and other mobile equipment as required. Provision should be made for situations where oversized additional equipment, e.g. bed extensions or bariatric beds, are in use. ~ Guidance for the calculation of areas (m2) for corridors is provided for in Health Planning Unit Schedules of Accommodation as circulation percentages. Refer to AusHFG Part C: Design for Access, Mobility, Safety and Security for further information. ~ Wall protection is recommended to protect wall linings and finishes from damage from impact. The height of the wall protection will be dependent on equipment frequently moved through the space; a height range of 900mm minimum up to 1500mm is recommended depending on service requirements. ~ Handrails are to be provided along not less than one side of all corridors in patient care areas to provide assistance and support for patients and visitors. Handrails are to be continuous along the corridors wherever practical. ~ Cleaner's electrical outlets to be provided at regular intervals as per mandatory requirements. ~ Corridor lighting, where patients are transported on beds/trolleys, should be positioned to prevent unnecessary glare to patient eyes. Light fittings shall be recessed, flush fitting and sealed to prevent dust ingress. ~ Manual controls to power-operated doors shall be located on the continuous accessible path of travel no closer than 500 mm from an internal corner and between 1000 mm to 2000 mm from the hinged door leaf in any position as per the requirements of AS1428.1. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
CTIR | CT Imaging Room | Medical Imaging | Full AHIA Review | 45 | 2700 |  | 2 | 15.05.2025 |  | Up to 24 hours | 1 patient;; up to 4 staff | The CT Imaging Room is designed for undertaking Computed Tomography (CT) scanning with direct overview and access from the adjoining CT Control Room. The CT Imaging Room may have a CT Equipment Room immediately adjacent for accommodating supporting power and control equipment. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between imaging unit, the equipment room (if provided) and the control room will be required and must be coordinated with the MME vendor. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room will require sufficient clearance to allow access for a patient on a bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Physiological monitoring on a display screen in the CT Control Room may be provided and would need to be supported with a connection provided within the CT Imaging Room. Provision will depend on service requirements and ICT policies. ~ Acoustic treatment to be considered to manage noise from the imaging device and the adjacent equipment room. All finishes must be meet infection prevention and control requirements. ~ Dimmable light may be considered to support patient comfort. Similarly, feature artwork or back lit panels on the ceiling may be considered above the CT table. ~ Depending on service requirements, general anaesthesia may be administered in this room. This must be confirmed by project teams to ensure appropriate workflows are provided to support this model of care, to confirm the correct building services are provided to ensure patient safety, and to determine medical gas system requirements. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Time tracking requirements (i.e. provision of electric or synchronised clock) is to be confirmed to suit service requirements. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and imaging equipment selection. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | Full AHIA Review | 16 | 2700 | CTCR | 5 | 15.05.2025 |  | Up to 24 hours | up to 4 staff | The CT Control Room provides the space and equipment for remote control of CT imaging equipment, and amenities for review of images and reporting. Direct visibility of the patient through an observation window and direct access to the imaging room is required. | ~ Cable ducts for services between the imaging unit, the equipment room (if provided) and the control room will be required and must be coordinated with the MME vendor. Additional building services connections and outlets are to be coordinated to suit equipment requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The size, quantity and configuration of computer display screens is to be finalised based on the specific image display and processing task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. Providing flexibility of monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Depending on service requirements and staffing profile, workflow control and advanced processing workstations may be combined into the CT control room to support staffing and efficient patient flow. ~ Additional RIS/PACs/EMR workstations may be required in larger services depending on service requirements and staffing models. ~ Physiological monitoring on a display screen in the CT Control Room may be provided and would need to be supported with a connection provided within the CT Imaging Room. Provision will depend on service requirements and ICT policies. ~ Acoustic treatment to be considered to manage noise from the CT machine and the adjacent equipment room. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
CTPR | CT Planning Room | Radiation Oncology | Translation and QA Only | 45 | 3000 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 patient;; up to 4 staff assisting | The CT Planning Room provides space and facilities for Computed Tomography (CT) scanning procedures as part of the planning of radiation therapy treatment for patients. A collocated Control Room with observation window is required for the remote operation of equipment. | ~ An Equipment Room may be required and will need to be in close proximity due to acceptable cable lengths. ~ Cable ducts between the Scanning Room, Control Room and Equipment Room will be required. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ The CT Planning Room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant to suit the equipment procured. 'X-ray in Use' lights are required outside each entry door to be illuminated when scanning begins. ~ Interlock system to doors recommended to prevent machine from running if door open and to stop the machine upon entry if in use. ~ Additional medical gases may be provided (including additional oxygen, additional suction, nitrous oxide and scavenge) depending on clinical requirements, such as the provision of anaesthetic services. ~ Dimmable lights are to be provided and lights are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort and distraction. ~ Where possible, it is preferred that ductwork in the ceiling is designed to the perimeter of room to allow for future flexibility to provide ceiling mounted equipment. ~ The need for and extent of emergency and UPS power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ Unistrut ceiling able to carry moving loads may be required. ~ A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be provided depending on clinical/service requirements and will be coordinated to support the technologies provided in the Linear Accelerator Treatment Room. The provision of these technologies is to be confirmed by the project and may have additional design requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DEN-MLB | Dental Laboratory, Minor | Oral Health | Translation and QA Only | 12 | 2700 |  | 4 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1-2 staff | The Minor Dental Laboratory provides facilities and equipment for dental clinicians/technicians to make adjustments to dentures or other dental prosthetics, and to store prosthetic supplies. | ~ Dust extraction is required at the source and may be integral to equipment in some instances. ~ If Bunsen burner to be used in this room, gas outlet or portable gas is required and overhead joinery may need to be reviewed to provide appropriate clearance. ~ A workstation with computer and barcode scanner may be provided for digital tracking and records. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DENSR-1 | Dental Surgery, Type 1 | Oral Health | Translation and QA Only | 14.5 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 patient; 1-2 carers / support persons; 1-2 staff | The Dental Surgery provides for dental consultation, examination and treatment for patients. This Standard Component provides a configuration for switching between a a right-handed and left-handed set-up and should not be mirrored. Dental surgery layouts will vary and will be dependent on existing/proposed workflows and the equipment procured. | ~ Services will be required for the dental chair unit; these will be dependent on the chair model and supplier and include dental air, dental suction, filtered water, power and drainage. ~ Facilities for viewing physical x-ray films brought in by patients may be provided in a central location as required. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Radiation shielding to be advised by Radiation Consultant. ~ An external outlook is desirable. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DENSR-2 | Dental Surgery, Type 2 | Oral Health | Translation and QA Only | 14.5 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 patient; 1-2 carers / support persons; 1-2 staff | The Dental Surgery provides for dental consultation, examination and treatment for patients. This Standard Component shows a right-handed configuration and should not be mirrored. The layout may be adjusted to provide an ambidextrous set up. Dental surgery layouts will vary and will be dependent on existing/proposed workflows and the equipment procured. | ~ Services will be required for the dental chair unit; these will be dependent on the chair model and supplier and include dental air, dental suction, filtered water, power and drainage. ~ Facilities for viewing physical x-ray films brought in by patients may be provided in a central location as required. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Radiation shielding to be advised by Radiation Consultant. ~ An external outlook is desirable. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DINR | Dining - Patient | Logistics / Support Services | Translation and QA Only | 40 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 16 patients seated;; 3-4 staff intermittently | The Dining Room is an area provided for patients to eat their meals away from the bedroom environment in an inpatient setting. The Dining Room may be used for other patient recreational activities when not in use for meals. In this instance, additional transfer of noise to adjacent patient care areas to be considered. | ~ Food services model, e.g. meal trolley (tray or re-thermalisation), servery, beverage bay, etc. will impact room design. A kitchen, servery or beverage bay may be collocated or combined with the Dining Room. ~ Size of space will depend on number of beds and models of care; designed area based on 3m2 per person. ~ Access will be required for patients with limited mobility including wheelchairs, walking frames and other walking aids. Design must also consider the needs of patients with dementia and frail/elderly. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. ~ Duress provision will be dependent on service requirements. ~ Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Lighting to be consistent across the space. ~ Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. ~ Where possible a achieving a domestic appearance with furniture, fittings and finishes is recommended. ~ The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. ~ Natural light and external outlook is essential. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Disposal Room provides for the temporary holding of waste, separated into various waste streams (general waste, clinical waste, cardboard recycling, co-mingled recycling, cytotoxic waste, confidential waste, sharps, soiled linen, etc.) prior to removal to a designated waste zone in the loading dock. | ~ Waste will be collected at regular times each day, or when requested, to prevent build-up of waste in the unit. ~ Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes. ~ Adequate space must be provided to allow for segregation of waste streams. ~ The use of 660 L bins should be carefully considered due to the WHS risks associated with manual handling, however it is acknowledged in some areas with significant waste output they may be required. Where the weight of full waste receptacles is a concern, the use of tugs/ACVs is often required. ~ Waste transfer may be manual, by motorised movers/tugs or via automated guided vehicle (AGV) systems. Where tugs and AGVs are being considered, it is important to confirm clearances, door widths and turning circles within the room, in the adjacent corridor and along path of travel to designated waste zone. ~ Hold open door hardware may be required to allow for easy movement of bins and trolleys in and out of the room. ~ Shelf may be provided for storage of small sharps bins prior to collection. ~ If a handwashing basin is not provided within the Disposal Room, one should be located in close proximity. The location of hand hygiene facilities may be dependent on local infection control policies. ~ Staff only access may be required if this room is provided in a public or patient care area. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | Translation and QA Only | 15 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Disposal Room provides for the temporary holding of waste, separated into various waste streams (general waste, clinical waste, cardboard recycling, co-mingled recycling, cytotoxic waste, confidential waste, sharps, soiled linen, etc.) prior to removal to a designated waste zone in the loading dock. | ~ Waste will be collected at regular times each day, or when requested, to prevent build-up of waste in the unit. ~ Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes. ~ Adequate space must be provided to allow for segregation of waste streams. ~ The use of 660 L bins should be carefully considered due to the WHS risks associated with manual handling, however it is acknowledged in some areas with significant waste output they may be required. Where the weight of full waste receptacles is a concern, the use of tugs/ACVs is often required. ~ Waste transfer may be manual, by motorised movers/tugs or via automated guided vehicle (AGV) systems. Where tugs and AGVs are being considered, it is important to confirm clearances, door widths and turning circles within the room, in the adjacent corridor and along path of travel to designated waste zone. ~ Dual access from within a unit and from an external services corridor may be provided depending on overall planning arrangement. ~ Hold open door hardware may be required to allow for easy movement of bins and trolleys in and out of the room. ~ Shelf may be provided for storage of small sharps bins prior to collection. ~ If a handwashing basin is not provided within the Disposal Room, one should be located in close proximity. The location of hand hygiene facilities may be dependent on local infection control policies. ~ Staff only access may be required if this room is provided in a public or patient care area. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Dirty Utility, 10m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 10m² fit out. | ~ Due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 10m² fit out. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | Translation and QA Only | 12 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Dirty Utility, 12m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. | ~ Due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 12m² fit out. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | Translation and QA Only | 14 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Dirty Utility, 14m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. The Dirty Utility, 14m2 may provide access doors from both sides of the room. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 14m² fit out. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | Translation and QA Only | 8 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Dirty Utility, Sub provides a small space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. | ~ Due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, Sub fit out. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | Translation and QA Only | 26 | 2700 | ECHO | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff | Room for diagnostic echocardiography procedures including transoesophageal echocardiography. Echocardiography procedures may be performed under local anaesthesia and sedation. | ~ The Echocardiography room should be located close to patient toilet and change rooms. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | Translation and QA Only | 10 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff | The Equipment Clean-Up Room is used for cleaning and maintaining of equipment used in the Unit. | ~ Storage may be required for holding cleaned equipment and spares. ~ Equipment may also be recharged in this room. ~ Natural light is desirable. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | Translation and QA Only | 12 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Equipment Clean Up Room is used for cleaning of equipment used in patient care or loaned to outpatients following return. | ~ Storage will be required for holding cleaning equipment. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | Translation and QA Only | 14 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff | The Equipment Clean-Up Room is used for cleaning and maintaining of equipment used in the Unit. | ~ Storage may be required for holding cleaned equipment and spares. ~ Equipment may also be recharged in this room. ~ Natural light is desirable. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | Translation and QA Only | 8 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff | The Equipment Clean-Up Room is used for cleaning and maintaining of equipment used in the Unit. | ~ Storage may be required for holding cleaned equipment and spares. ~ Equipment may also be recharged in this room. ~ Natural light is desirable. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ENPR | Procedure Room - Endoscopy | Operating | Full AHIA Review | 45 | 3000 |  | 2 | 06.05.2025 |  | 24 hours | 1 patient;; up to 8 staff | A Procedure Room - Endoscopy provides an aseptic environment in which to carry out endoscopic procedures on a patient under local, regional or general anaesthetic. The Procedure Room may be used for specialties including ENT, urology, endoscopy and other similar procedures. The Procedure Room may have direct access to a reprocessing area and, in some models, a sterile stock. | ~ The minimum critical dimension centred on the procedure zone is 6400mm clear to ensure adequate space for the procedure, circulation and equipment storage. ~ Isolated power supply is required individually to each medical services pendant, together with its associated line isolation and overload monitors. ~ Location and quantity of RCD outlets to suit overall electrical service provision and is to be confirmed by the project to suit local engineering services guidelines/policies. ~ If the room is used for Bronchoscopy procedures, negative pressure air conditioning and direct exhaust to roof is required. ~ If the room is used for bronchoscopy procedures, negative pressure air conditioning and direct exhaust to outside is required. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ If laser equipment is to be used, ‘laser in use’ warning lights are required outside all entry doors to the room. ~ If x-ray equipment is to be used, ‘x-ray in use’ warning lights are required outside all entry doors to the room. Radiation shielding will also be required and is to be assessed by a Radiation Consultant. ~ Automated doors with motion or elbow activation are provided to the Procedure Room - Endoscopy from the corridor and reprocessing areas. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Height of doors to be confirmed to suit the movement of mobile equipment such as mobile imaging devices. ~ If external windows are provided, they are to be double glazed with integral venetian blinds (with either manual or automated controls). ~ Room lights to be dimmable. Lighting control to room rights, warning signs, and operating lights to be coordinated within the room and an appropriate lighting control panel to be provided to functional requirements. ~ Configuration of services pendant (horizontal or vertical) to suit services requirements. Accessories (e.g. shelves, drawers, rails, etc.) are optional and can be selected to suit service and equipment requirements. Services allocations are indicative - type and number of services on the pendant to suit service requirements ~ Services pendant arms to have an adequate reach to be moved out of the way to allow for adequate room for movement of a patient trolley and mobile equipment. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | Full AHIA Review | 7 | 2700 |  | 5 | 15.12.2025 |  | 24 hours | 1 patient;; 1-2 staff assisting as required | The Ensuite - Accessible includes a shower, toilet and basin for use by a patient a disability, either independently or with assistance. The room layout and fittings shall comply with AS 1428.1 / NZS 4121. This Standard Component may be used in conjunction with an inboard, outboard or nested bedroom layout, and the ensuite and bedroom should be planned as a unit. | ~ The door is to be fitted with a lock that has an occupancy indicator and emergency release hardware. An outward swinging door is recommended to mitigate risk of accidental barricade in the event of a fall or loss of consciousness. If an inward swing is provided, an emergency release and pivot hinge to allow for the door to open outward is required. ~ The floor finish at the entry to the ensuite is to be flush with the adjacent floor finish in the bedroom. The floor finish in the shower area must also be flush and continuous with the adjacent floor in the ensuite and is not to have a raised hob. ~ A tiled floor finish may be provided instead of floor vinyl, and it is recommended that where floor tiles are used, wall tiles are also used to achieve an appropriate join between floor and wall finishes. ~ The slope of the floor to the drain in the shower must meet the relevant Australian/New Zealand building code compliance requirements. When meeting these requirements, the slope of the floor is then low enough to have minimal impact on patients using walking aids, patients with impaired mobility/balance, and staff assisting patients on commodes, wheelchairs, etc. ~ Provision of reticulated medical gas outlets (e.g. oxygen and suction) may be considered depending on patient cohort requirements. Where provided, the location of the outlets should allow for use within the shower and on the toilet with standard tubing lengths. Mitigating contamination risk of medical gas outlets from toilet plume is to be considered (e.g. cover to outlets and associated attachments). ~ Patient lifting tracks may be provided in adjacent bedrooms and this provision is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track, traverse track, etc.), installation (recessed or ceiling mounted), weight rating/safe working load (SWL), and extent, including whether that track extends to transfer the patient to the ensuite or is for bed to chair/wheelchair/commode transfer only, must also be confirmed by project teams to inform requirements for the ceiling structure, door width and clearances in the ensuite. Where the path of the lifter track includes full transfer to/within the ensuite, the door height must be increased and the frame must be designed to accommodate linking between tracks. Selected track and lifter equipment must meet local infection prevention and control (IPC) policies and cleaning requirements. ~ The connection point of the hand-held shower is to be located, with consideration of the length of the hose, to ensure that the shower head is not in reach of the toilet bowl. Risk mitigation strategies (e.g. reduced pressure zone devices) to be used where this cannot be achieved. ~ Grab rails are to be configured in alignment with AS 1428.1 / NZS 4121 and must be securely fixed to the wall with the structural support required to meet weight ratings/SWL that must be confirmed at project level (generally accommodating patients up to 150kg for standard patient rooms). ~ A wall mounted fold-down seat is indicated within the shower. Provision of a shower chair or commode in lieu of the wall mounted bench may be considered at project level in alignment with AS1428.1 / NZS 4121. ~ A shower curtain and track are noted as optional, and inclusion of the curtain and track, or track only (to support flexibility for future provision of curtains) is to be confirmed at project level to suit local work, health and safety (WHS), and IPC policies. Where curtains and tracks are provided, operational models for cleaning and maintenance must be considered. ~ The handwashing basin should include a detachable shroud to enclose pipe fittings. The shroud should be a separate element, rather than being integrally moulded with the basin. This separation ensures there is access to the plumbing (i.e. P-trap or S-bend) for maintenance, without requiring the removal of the entire basin. Refer to ‘Part D: infection Prevention and Control' for more information. ~ Where only one mirror is provided, it must be centred over the basin. A second mirror may be provided extending from 600mm AFFL to at least 1850mm AFFL in line with AS1428.1 / NZS 4121 requirements. ~ The use of commodes, mobile patient transfer equipment and sit-to-stand equipment is to be considered when finalising fitting selection. It is recommended that the set out of the toilet suite and grab rails (that are aligned with AS1428.1 / NZS 4121 requirements) is tested with assistive equipment that is being considered or has been selected to ensure appropriate clearances, including coordination with the height of the toilet seat and the toilet lid. Clearance from the equipment to the grab rails should ensure there is no risk of pinching or finger entrapment. ~ Operational models and IPC policies for use of a patient’s own mobility/transfer equipment, and any associated considerations for the design of the ensuite, are to be confirmed at project level. ~ The type and size of toilet paper dispensers can vary significantly. Where large toilet paper dispensers (e.g. jumbo roll, multi-roll, interleaved tissue, etc.) are selected to suit operational models for restocking, the location of the dispenser must be confirmed, with particular focus on the location of the operable element of the dispenser in relation to the patient seated on the toilet. Locating larger toilet paper dispensers above the grab rail may be considered (with formal assessment and exemption sought for an alternative solution from standard disability access requirements). When located above the grab rail, the placement and depth of the dispenser must not interfere with the use of the grabrail (e.g. by forcing a patient to reach around the dispenser to use the vertical section of the grab rail to pull themselves to a standing position) or with the clearances required for the use of assistive equipment (e.g. preventing a commode from fitting over the toilet). ~ Toilet lids and seats are to be robust and suitable for long term, high frequency use. The toilet lid/seat must be coloured to achieve a minimum 30% luminance contrast between the lid/seat, and the toilet pan, the floor, and the adjacent walls to support patients with visual impairments and comply with AS1428 / NZS 4121 requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A power outlet to support grooming, such as shaving and drying hair, is shown as optional. Local policies around provision and maintenance of electrical outlets in wet areas are to be confirmed to inform inclusion of a power outlet within the ensuite. Where provided, the outlet is to be located to comply with Australian and New Zealand Standards regarding the minimum distance from any water sources (i.e. basin spout and shower). ~ Layout of ensuites should consider the positioning of plumbing fixtures in relation to fire and smoke walls in an overall department configuration to minimise the impact of penetrations required for pipework. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | Full AHIA Review | 7 | 2700 | ENS-BA | 3 | 15.12.2025 |  | 24 hours | 1 patient;; 1-2 staff assisting as required | The Ensuite - Bariatric is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The Ensuite is associated with the 1 Bed Room - Bariatric. The area and layout must accommodate two assisting nurses and a shower commode with bariatric capacity. The ensuite and bedroom should be planned as a unit, with the use of a ceiling mounted hoist is coordinated across both rooms. | ~ Bariatric bedrooms and ensuites are to be designed to accommodate patients up to 250kgs. The provision of super bariatric bedrooms and ensuites, for the management of patients up to 450kg, is generally restricted in jurisdictions to selected healthcare facilities only. This is to ensure that safe and effective care can be provided. Refer to HPU 340 Adult Acute Inpatient Unit for more information. ~ The door is to be fitted with a lock that has an occupancy indicator and emergency release hardware. An outward swinging door is recommended to mitigate risk of accidental barricade in the event of a fall or loss of consciousness. If an inward swing is provided, an emergency release and pivot hinge to allow for the door to open outward is required. ~ The floor finish at the entry to the ensuite is to be flush with the adjacent floor finish in the bedroom. The floor finish in the shower area must also be flush and continuous with the adjacent floor in the ensuite and is not to have a raised hob. ~ A tiled floor finish may be provided instead of floor vinyl, and it is recommended that where floor tiles are used, wall tiles are also used to achieve an appropriate join between floor and wall finishes. ~ The slope of the floor to the drain in the shower must meet the relevant Australian/New Zealand building code compliance requirements. When meeting these requirements, the slope of the floor is then low enough to have minimal impact on patients using walking aids, patients with impaired mobility/balance, and staff assisting patients on commodes, wheelchairs, etc. ~ Provision of reticulated medical gas outlets (e.g. oxygen and suction) may be considered depending on patient cohort requirements. Where provided, the location of the outlets should allow for use within the shower and on the toilet with standard tubing lengths. Mitigating contamination risk of medical gas outlets from toilet plume is to be considered (e.g. cover to outlets and associated attachments). ~ A patient lifting track is typically provided in the associated bariatric bedroom and continues to the ensuite. Requirements for the bariatric patient lifting track in both the ensuite and the adjacent bedroom must be confirmed at a project level and are to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track, traverse track, etc.), installation (recessed or ceiling mounted), weight rating/safe working load (SWL), and extent must also be confirmed by project teams to inform requirements for the ceiling structure, door width and clearances in the ensuite. The door height and frame must be designed to accommodate linking between tracks. Selected track and lifter equipment must meet local infection prevention and control (IPC) policies and cleaning requirements. ~ Selected toilet pan must be able to support patients weighing up to 250kg. While most toilet pans are able to accommodate this weight, pans that are slightly wider and longer, such as those typically selected for accessible toilet configurations, can be fitted with bariatric toilet seats and provide support to bariatric patients and allow clearance for use of bariatric assistive equipment. Use of these toilet pans also allows the room to be used by other patients, including those with high assistance requirements, when it is not being used by a bariatric patient. Extra wide stainless steel toilets that are specifically designed for patients up to 450kg are often too large for other patients to use, reducing flexible utilisation of the bedroom and ensuite. It is therefore recommended that these toilets be used in super bariatric ensuites only. ~ Specific bariatric toilet seats are to be selected that are designed to accommodate patients up to 250kg and to flex in a way to reduce the risk of pinching between the seat and the pan. It is recommended that the toilet seat is coloured to achieve a minimum 30% luminance contrast between the seat and the toilet pan, the floor, and the adjacent walls to support patients with visual impairments. ~ The connection point of the hand-held shower is to be located, with consideration of the length of the hose, to ensure that the shower head is not in reach of the toilet bowl. Risk mitigation strategies (e.g. reduced pressure zone devices) to be used where this cannot be achieved. ~ Grab rails are to be securely fixed to the wall with the structural support required to meet weight ratings/SWL that must be confirmed at project level (generally accommodating patients up to 250kg for bariatric patient rooms). Space for staff assistance to both sides of the toilet is provided in this Standard Component and therefore drop-down grabs rails for use by patients with or without staff assistance have been indicated. Additional structural support requirements are to be confirmed at project level to accommodate the downward force on the drop-down grab rails. It is recommended that drop-down grab rail products with fold down support legs are selected for increased support and strength. ~ A shower curtain and track are not shown in this Standard Component due to provision of the ceiling mounted lifter track. Hinged curtain tracks that fold against the wall may be considered, and inclusion is to be confirmed at project level to suit local work, health and safety (WHS), and IPC policies. Where provided, operational models for cleaning and maintenance must be considered. ~ In-wall structural supports are to be provided for the basin and other relevant fittings to meet weight rating/SWL and downward force requirements. ~ The handwashing basin should include a detachable shroud to enclose pipe fittings. The shroud should be a separate element, rather than being integrally moulded with the basin. This separation ensures there is access to the plumbing (i.e. P-trap or S-bend) for maintenance, without requiring the removal of the entire basin. Refer to ‘Part D: infection Prevention and Control' for more information. ~ The use of commodes, mobile patient transfer equipment and sit-to-stand equipment is to be considered when finalising fitting selection. It is recommended that the set out of the toilet suite and grab rails is tested with assistive equipment that is being considered or has been selected to ensure appropriate clearances, including coordination with the height of the toilet seat and the toilet lid. Clearance from the equipment to the grab rails should ensure there is no risk of pinching or finger entrapment. ~ Operational models and IPC policies for use of a patient’s own mobility/transfer equipment, and any associated considerations for the design of the ensuite, are to be confirmed at project level. ~ With provision of drop-down grab rails to both sides of the toilet, inclusion of an integral toilet paper roll holder and nurse call button are recommended due to reach to wall mounted fittings being impractical. This may mean toilet paper stock differs in this ensuite compared to others where dispensers may be selected for jumbo roll, or interleaved tissue stock. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A power outlet to support grooming, such as shaving and drying hair, is shown as optional. Local policies around provision and maintenance of electrical outlets in wet areas are to be confirmed to inform inclusion of a power outlet within the ensuite. Where provided, the outlet is to be located to comply with Australian and New Zealand Standards regarding the minimum distance from any water sources (i.e. basin spout and shower). ~ Layout of ensuites should consider the positioning of plumbing fixtures in relation to fire and smoke walls in an overall department configuration to minimise the impact of penetrations required for pipework. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
ENS-BR | Ensuite - Birthing | Maternity | Translation and QA Only | 7 | 2400 |  | 2 | 07.04.2026 |  | 24 hours | 1 mother;; 1-2 staff / support persons assisting | An Ensuite - Birthing Room is for a mother to wash, shower and use the toilet, either independently or with assistance. During labour, the shower may be used for extended periods to manage pain and two shower heads are provided to support this. | ~ The area and layout must accommodate an assisting midwife and a support person. ~ The Ensuite - Birthing will have direct access from the Birthing Room. ~ The shower floor must not have a raised hob and the entrance to the ensuite is to be flush with the adjoining flooring. ~ A ladder or other wall mounted supportive fixtures may be included to provide support at various heights and facilitate different postures during active birthing. A birthing woman's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. Item to be suitable for wet area. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | Full AHIA Review | 6 | 2700 |  | 1 | 15.12.2025 |  | 24 hours | 1 patient;; 1-2 staff assisting as required | The Ensuite - High Assistance includes a shower, toilet and basin for use by a patient, typically with assistance. This Standard Component is typically used in a nested bedroom layout, however, with careful planning it may be used in conjunction with either an inboard or outboard bedroom layout. The ensuite and bedroom should be planned as a unit. | ~ The door is to be fitted with a lock that has an occupancy indicator and emergency release hardware. An outward swinging door is recommended to mitigate risk of accidental barricade in the event of a fall or loss of consciousness. If an inward swing is provided, an emergency release and pivot hinge to allow for the door to open outward is required. ~ The floor finish at the entry to the ensuite is to be flush with the adjacent floor finish in the bedroom. The floor finish in the shower area must also be flush and continuous with the adjacent floor in the ensuite and is not to have a raised hob. ~ A tiled floor finish may be provided instead of floor vinyl, and it is recommended that where floor tiles are used, wall tiles are also used to achieve an appropriate join between floor and wall finishes. ~ The slope of the floor to the drain in the shower must meet the relevant Australian/New Zealand building code compliance requirements. When meeting these requirements, the slope of the floor is then low enough to have minimal impact on patients using walking aids, patients with impaired mobility/balance, and staff assisting patients on commodes, wheelchairs, etc. ~ Provision of reticulated medical gas outlets (e.g. oxygen and suction) may be considered depending on patient cohort requirements. Where provided, the location of the outlets should allow for use within the shower and on the toilet with standard tubing lengths. Mitigating contamination risk of medical gas outlets from toilet plume is to be considered (e.g. cover to outlets and associated attachments). ~ Patient lifting tracks may be provided in adjacent bedrooms and this provision is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track, traverse track, etc.), installation (recessed or ceiling mounted), weight rating/safe working load (SWL), and extent, including whether that track extends to transfer the patient to the ensuite or is for bed to chair/wheelchair/commode transfer only, must also be confirmed by project teams to inform requirements for the ceiling structure, door width and clearances in the ensuite. Where the path of the lifter track includes full transfer to/within the ensuite, the door height must be increased and the frame must be designed to accommodate linking between tracks. Selected track and lifter equipment must meet local infection prevention and control (IPC) policies and cleaning requirements. ~ The connection point of the hand-held shower is to be located, with consideration of the length of the hose, to ensure that the shower head is not in reach of the toilet bowl. Risk mitigation strategies (e.g. reduced pressure zone devices) to be used where this cannot be achieved. ~ Grab rails are to be securely fixed to the wall with the structural support required to meet weight ratings/SWL that must be confirmed at project level (generally accommodating patients up to 150kg for standard patient rooms). Space for staff assistance to both sides of the toilet is provided in this Standard Component and therefore drop-down grabs rails for use by patients with or without staff assistance have been indicated. Additional structural support requirements are to be confirmed at project level to accommodate the downward force on the cantilevered drop-down grab rails. ~ A shower curtain and track are noted as optional, and inclusion of the curtain and track, or track only (to support flexibility for future provision of curtains) is to be confirmed at project level to suit local work, health and safety (WHS), and IPC policies. Where curtains and tracks are provided, operational models for cleaning and maintenance must be considered. ~ The handwashing basin should include a detachable shroud to enclose pipe fittings. The shroud should be a separate element, rather than being integrally moulded with the basin. This separation ensures there is access to the plumbing (i.e. P-trap or S-bend) for maintenance, without requiring the removal of the entire basin. Refer to ‘Part D: infection Prevention and Control' for more information. ~ The use of commodes, mobile patient transfer equipment and sit-to-stand equipment is to be considered when finalising fitting selection. It is recommended that the set out of the toilet suite and grab rails is tested with assistive equipment that is being considered or has been selected to ensure appropriate clearances, including coordination with the height of the toilet seat and the toilet lid. Clearance from the equipment to the grab rails should ensure there is no risk of pinching or finger entrapment. ~ Operational models and IPC policies for use of a patient’s own mobility/transfer equipment, and any associated considerations for the design of the ensuite, are to be confirmed at project level. ~ With provision of drop-down grab rails to both sides of the toilet, inclusion of an integral toilet paper roll holder and nurse call button are recommended due to reach to wall mounted fittings being impractical. This may mean toilet paper stock differs in this ensuite compared to others where dispensers may be selected for jumbo roll, or interleaved tissue stock. ~ Toilet lids and seats are to be robust and suitable for long term, high frequency use. It is recommended that the toilet lid/seat is coloured to achieve a minimum 30% luminance contrast between the lid/seat, and the toilet pan, the floor, and the adjacent walls to support patients with visual impairments. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A power outlet to support grooming, such as shaving and drying hair, is shown as optional. Local policies around provision and maintenance of electrical outlets in wet areas are to be confirmed to inform inclusion of a power outlet within the ensuite. Where provided, the outlet is to be located to comply with Australian and New Zealand Standards regarding the minimum distance from any water sources (i.e. basin spout and shower). ~ Layout of ensuites should consider the positioning of plumbing fixtures in relation to fire and smoke walls in an overall department configuration to minimise the impact of penetrations required for pipework. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | Full AHIA Review | 5 | 2700 |  | 1 | 15.12.2025 |  | 24 hours | 1 patient;; 1-2 staff assisting as required | The Ensuite - Inboard / Outboard includes a shower, toilet and basin for use by a patient, either independently or with assistance. This Standard Component may be used in conjunction with either an inboard or outboard bedroom layout, and the ensuite and bedroom should be planned as a unit. | ~ The door is to be fitted with a lock that has an occupancy indicator and emergency release hardware. An outward swinging door is recommended to mitigate risk of accidental barricade in the event of a fall or loss of consciousness. If an inward swing is provided, an emergency release and pivot hinge to allow for the door to open outward is required. ~ The floor finish at the entry to the ensuite is to be flush with the adjacent floor finish in the bedroom. The floor finish in the shower area must also be flush and continuous with the adjacent floor in the ensuite and is not to have a raised hob. ~ A tiled floor finish may be provided instead of floor vinyl, and it is recommended that where floor tiles are used, wall tiles are also used to achieve an appropriate join between floor and wall finishes. ~ The slope of the floor to the drain in the shower must meet the relevant Australian/New Zealand building code compliance requirements. When meeting these requirements, the slope of the floor is then low enough to have minimal impact on patients using walking aids, patients with impaired mobility/balance, and staff assisting patients on commodes, wheelchairs, etc. ~ Provision of reticulated medical gas outlets (e.g. oxygen and suction) may be considered depending on patient cohort requirements. Where provided, the location of the outlets should allow for use within the shower and on the toilet with standard tubing lengths. Mitigating contamination risk of medical gas outlets from toilet plume is to be considered (e.g. cover to outlets and associated attachments). ~ Patient lifting tracks may be provided in adjacent bedrooms and this provision is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track, traverse track, etc.), installation (recessed or ceiling mounted), weight rating/safe working load (SWL), and extent, including whether that track extends to transfer the patient to the ensuite or is for bed to chair/wheelchair/commode transfer only, must also be confirmed by project teams to inform requirements for the ceiling structure, door width and clearances in the ensuite. Where the path of the lifter track includes full transfer to/within the ensuite, the door height must be increased and the frame must be designed to accommodate linking between tracks. Selected track and lifter equipment must meet local infection prevention and control (IPC) policies and cleaning requirements. ~ The connection point of the hand-held shower is to be located, with consideration of the length of the hose, to ensure that the shower head is not in reach of the toilet bowl. Risk mitigation strategies (e.g. reduced pressure zone devices) to be used where this cannot be achieved. ~ Grab rails are to be securely fixed to the wall with the structural support required to meet weight ratings/SWL that are to be confirmed at project level (generally accommodating patients up to 150kg for standard patient rooms). A drop-down grab rail may be provided to one side of the toilet and provision is dependent on the anticipated patient cohort requirements, additional support requirements are to be confirmed to accommodate the downward force on the cantilevered drop-down grab rail. ~ A shower curtain and track are noted as optional, and inclusion of the curtain and track, or track only (to support flexibility for future provision of curtains) is to be confirmed at project level to suit local work, health and safety (WHS), and IPC policies. Where curtains and tracks are provided, operational models for cleaning and maintenance must be considered. ~ The handwashing basin should include a detachable shroud to enclose pipe fittings. The shroud should be a separate element, rather than being integrally moulded with the basin. This separation ensures there is access to the plumbing (i.e. P-trap or S-bend) for maintenance, without requiring the removal of the entire basin. Refer to ‘Part D: infection Prevention and Control' for more information. ~ The use of commodes, mobile patient transfer equipment and sit-to-stand equipment is to be considered when finalising fitting selection. It is recommended that the set out of the toilet suite and grab rails is tested with assistive equipment that is being considered or has been selected to ensure appropriate clearances, including coordination with the height of the toilet seat and the toilet lid. Clearance from the equipment to the grab rails should ensure there is no risk of pinching or finger entrapment. ~ Operational models and IPC policies for use of a patient’s own mobility/transfer equipment, and any associated considerations for the design of the ensuite, are to be confirmed at project level. ~ The type and size of toilet paper dispensers can vary significantly. Where large toilet paper dispensers (e.g. jumbo roll, multi-roll, interleaved tissue, etc.) are selected to suit operational models for restocking, the location of the dispenser must be confirmed, with particular focus on the location of the operable element of the dispenser in relation to the patient seated on the toilet. Locating larger toilet paper dispensers above the grab rail may be considered, but the placement and depth of the dispenser must not interfere with the use of the grabrail (e.g. by forcing a patient to reach around the dispenser to use the vertical section of the grab rail to pull themselves to a standing position) or with the clearances required for the use of assistive equipment (e.g. preventing a commode from fitting over the toilet). ~ Toilet lids and seats are to be robust and suitable for long term, high frequency use. It is recommended that the toilet lid/seat is coloured to achieve a minimum 30% luminance contrast between the lid/seat, and the toilet pan, the floor, and the adjacent walls to support patients with visual impairments. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A power outlet to support grooming, such as shaving and drying hair, is shown as optional. Local policies around provision and maintenance of electrical outlets in wet areas are to be confirmed to inform inclusion of a power outlet within the ensuite. Where provided, the outlet is to be located to comply with Australian and New Zealand Standards regarding the minimum distance from any water sources (i.e. basin spout and shower). ~ Layout of ensuites should consider the positioning of plumbing fixtures in relation to fire and smoke walls in an overall department configuration to minimise the impact of penetrations required for pipework. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | Full AHIA Review | 5 | 2700 | ENS-MH-A | 6 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/ensuite-mental-health-inboard/?fullscreen=true&utm_source=project-link&rev=6 | 24 hours | 1 patient;; 1 staff assisting as required | The Ensuite - Mental Health, Inboard provides a shower, toilet and basin for use by consumers in a mental health inpatient unit. The inboard ensuite layout is used in conjunction with the 1 Bed Room - Mental Health, Inboard Ensuite (1BR-MH-IN). | ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~If provided, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ The ensuite door configuration is to be confirmed at project level to suit service requirements and jurisdictional policies. The door in this Standard Component is indicated as a solid door with an angled cut down at top and optional undercut at bottom. Alternatively, magnetic load release leaf/saloon style doors may be provided. Anti-ligature sliding doors may also be considered based on a risk assessment and review of available products. Configuring the bedroom and ensuite arrangement to provide privacy without a door may be considered, however patient privacy and dignity and overall bedroom observation in this type of layout should be carefully assessed with users. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be assessed at project level to suit service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring, skirting and wall finish selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. tiles). ~ Where caulking is required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ Coat hooks are shown as optional. Some jurisdictions do not support the provision of coat hooks of any type (e.g. Victoria), refer to jurisdictional policies for guidance. In areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered. ~ Provision of motion sensor lighting or switched lighting is to be considered and confirmed at project level. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | Full AHIA Review | 5 | 2700 | ENS-MH-B | 5 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/ensuite-mental-health-nested/?fullscreen=true&utm_source=project-link&rev=5 | 24 hours | 1 patient;; 1 staff assisting as required | The Ensuite - Mental Health, Nested provides a shower, toilet and basin for use by consumers in a mental health inpatient unit. The nested ensuite layout is used in conjunction with the 1 Bed Room - Mental Health, Nested Ensuite (1BR-MH-NE). | ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~If provided, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ The ensuite door configuration is to be confirmed at project level to suit service requirements and jurisdictional policies. The door in this Standard Component is indicated as a solid door with an angled cut down at top and optional undercut at bottom. Alternatively, magnetic load release leaf/saloon style doors may be provided. Anti-ligature sliding doors may also be considered based on a risk assessment and review of available products. Configuring the bedroom and ensuite arrangement to provide privacy without a door may be considered, however patient privacy and dignity and overall bedroom observation in this type of layout should be carefully assessed with users. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be assessed at project level to suit service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring, skirting and wall finish selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. tiles). ~ Where caulking is required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ Coat hooks are shown as optional. Some jurisdictions do not support the provision of coat hooks of any type (e.g. Victoria), refer to jurisdictional policies for guidance. In areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered. ~ Provision of motion sensor lighting or switched lighting is to be considered and confirmed at project level. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
ENS-NE | Ensuite - Nested | Inpatient Accommodation | Full AHIA Review | 5 | 2700 | ENS-ST-C | 2 | 15.12.2025 |  | 24 hours | 1 patient;; 1-2 staff assisting as required | The Ensuite - Nested includes a shower, toilet and basin for use by a patient, either independently or with assistance. This Standard Component may be used in conjunction with the nested bedroom layout, and the ensuite and bedroom should be planned as a unit. | ~ The door is to be fitted with a lock that has an occupancy indicator and emergency release hardware. An outward swinging door is recommended to mitigate risk of accidental barricade in the event of a fall or loss of consciousness. If an inward swing is provided, an emergency release and pivot hinge to allow for the door to open outward is required. ~ The floor finish at the entry to the ensuite is to be flush with the adjacent floor finish in the bedroom. The floor finish in the shower area must also be flush and continuous with the adjacent floor in the ensuite and is not to have a raised hob. ~ A tiled floor finish may be provided instead of floor vinyl, and it is recommended that where floor tiles are used, wall tiles are also used to achieve an appropriate join between floor and wall finishes. ~ The slope of the floor to the drain in the shower must meet the relevant Australian/New Zealand building code compliance requirements. When meeting these requirements, the slope of the floor is then low enough to have minimal impact on patients using walking aids, patients with impaired mobility/balance, and staff assisting patients on commodes, wheelchairs, etc. ~ Provision of reticulated medical gas outlets (e.g. oxygen and suction) may be considered depending on patient cohort requirements. Where provided, the location of the outlets should allow for use within the shower and on the toilet with standard tubing lengths. Mitigating contamination risk of medical gas outlets from toilet plume is to be considered (e.g. cover to outlets and associated attachments). ~ Patient lifting tracks may be provided in adjacent bedrooms and this provision is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track, traverse track, etc.), installation (recessed or ceiling mounted), weight rating/safe working load (SWL), and extent, including whether that track extends to transfer the patient to the ensuite or is for bed to chair/wheelchair/commode transfer only, must also be confirmed by project teams to inform requirements for the ceiling structure, door width and clearances in the ensuite. Where the path of the lifter track includes full transfer to/within the ensuite, the door height must be increased and the frame must be designed to accommodate linking between tracks. Selected track and lifter equipment must meet local infection prevention and control (IPC) policies and cleaning requirements. ~ The connection point of the hand-held shower is to be located, with consideration of the length of the hose, to ensure that the shower head is not in reach of the toilet bowl. Risk mitigation strategies (e.g. reduced pressure zone devices) to be used where this cannot be achieved. ~ Grab rails are to be securely fixed to the wall with the structural support required to meet weight ratings/SWL that are to be confirmed at project level (generally accommodating patients up to 150kg for standard patient rooms). A drop-down grab rail may be provided to one side of the toilet and provision is dependent on the anticipated patient cohort requirements, additional support requirements are to be confirmed to accommodate the downward force on the cantilevered drop-down grab rail. ~ A shower curtain and track are noted as optional, and inclusion of the curtain and track, or track only (to support flexibility for future provision of curtains) is to be confirmed at project level to suit local work, health and safety (WHS), and IPC policies. Where curtains and tracks are provided, operational models for cleaning and maintenance must be considered. ~ The handwashing basin should include a detachable shroud to enclose pipe fittings. The shroud should be a separate element, rather than being integrally moulded with the basin. This separation ensures there is access to the plumbing (i.e. P-trap or S-bend) for maintenance, without requiring the removal of the entire basin. Refer to ‘Part D: infection Prevention and Control' for more information. ~ The use of commodes, mobile patient transfer equipment and sit-to-stand equipment is to be considered when finalising fitting selection. It is recommended that the set out of the toilet suite and grab rails is tested with assistive equipment that is being considered or has been selected to ensure appropriate clearances, including coordination with the height of the toilet seat and the toilet lid. Clearance from the equipment to the grab rails should ensure there is no risk of pinching or finger entrapment. ~ Operational models and IPC policies for use of a patient’s own mobility/transfer equipment, and any associated considerations for the design of the ensuite, are to be confirmed at project level. ~ The type and size of toilet paper dispensers can vary significantly. Where large toilet paper dispensers (e.g. jumbo roll, multi-roll, interleaved tissue, etc.) are selected to suit operational models for restocking, the location of the dispenser must be confirmed, with particular focus on the location of the operable element of the dispenser in relation to the patient seated on the toilet. Locating larger toilet paper dispensers above the grab rail may be considered, but the placement and depth of the dispenser must not interfere with the use of the grabrail (e.g. by forcing a patient to reach around the dispenser to use the vertical section of the grab rail to pull themselves to a standing position) or with the clearances required for the use of assistive equipment (e.g. preventing a commode from fitting over the toilet). ~ Toilet lids and seats are to be robust and suitable for long term, high frequency use. It is recommended that the toilet lid/seat is coloured to achieve a minimum 30% luminance contrast between the lid/seat, and the toilet pan, the floor, and the adjacent walls to support patients with visual impairments. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A power outlet to support grooming, such as shaving and drying hair, is shown as optional. Local policies around provision and maintenance of electrical outlets in wet areas are to be confirmed to inform inclusion of a power outlet within the ensuite. Where provided, the outlet is to be located to comply with Australian and New Zealand Standards regarding the minimum distance from any water sources (i.e. basin spout and shower). ~ Layout of ensuites should consider the positioning of plumbing fixtures in relation to fire and smoke walls in an overall department configuration to minimise the impact of penetrations required for pipework. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
EXIT | Exit Bay | Operating | Full AHIA Review | 11 | 2700 |  | 1 | 06.05.2025 |  | Up to 24 hours | accessed by staff intermittently | The Exit Bay provides area for patients and equipment to be moved from the Operating Room at the conclusion of a procedure. The Exit Bay provides space for the temporary storage of a patient bed while a procedure is in progress. Direct access to the Operating Room is required. | ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Exit Bay. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ A cupboard for digital operating room (DOR) ICT/AV equipment is indicated on the layout but is not included in the overall area measurement and the contents of the ICT/AV cupboard are not captured in this Standard Component. The size of the ICT/AV cupboard will vary depending on equipment to be accommodated. Rather than being located individually to each Operating Room, ICT/AV equipment may be consolidated in a room that is shared between a number of Operating Rooms as appropriate to suit equipment installation, testing and maintenance requirements. ~ Medical gas valve boxes for each Operating Room are typically located in the associated Exit Bay. Size and location of the medical gas valve box zone, to be kept clear of all other services, is to be confirmed by a medical gas engineering consultant. ~ Height and type of wall finish to suit local infection prevention and control policies and rigorous cleaning regimes. Provision and height of corner guards as required to provide protection from anticipated mobile equipment movement. ~ Depending on the use of x-ray equipment within the adjacent Operating Room, radiation shielding may be required to this room and is to be assessed by a Radiation Consultant. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
FLUO | Fluoroscopy Room | Medical Imaging | Full AHIA Review | 40 | 2700 |  | 2 | 15.05.2025 |  | Up to 24 hours | 1 patient;; 1-2 staff | The Fluoroscopy Room provides the space and equipment for radiographic imaging and minor interventional procedures involving contrast media. Direct access from an adjacent Fluoroscopy Control Room is required. | ~ Optional general x-ray equipment has been indicated in this Standard Component; this equipment may be provided in this room in addition to fluoroscopy equipment to optimise utilisation of this room in small services and/or provide for redundancy when another machine requires maintenance. Unistrut type ceiling may be required, depending on the equipment to be installed. ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between imaging unit, the equipment room (if provided) and the control room will be required and must be coordinated with the MME vendor. ~ A separate Fluoroscopy Equipment Room for power supply and control elements for the imaging device may be required depending on equipment selected. Where equipment generates a significant amount of heat and noise, separation from the patient area is to be considered. If provided the equipment room should be accessible directly from the imaging room or control room. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ Depending on service requirements, general anaesthesia may be administered in this room. This must be confirmed by project teams to ensure appropriate workflows are provided to support this model of care, to confirm the correct building services are provided to ensure patient safety, and to determine medical gas system requirements. ~ Where the Fluoroscopy service is to include interventional procedures an increase in area is required to accommodate additional staff, trolleys, an anaesthetic machine and other equipment. For interventional procedures, general anaesthesia may be given in this room and the appropriate services and support areas for recovery of patients will be required. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ The room will require sufficient clearance to allow access for a patient on a bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Patient transfer aids such as patient slides and hover mats are to be considered for assisted patient transfers to and from the fluoroscopy table. Final selection of transfer aids will be dependent on service requirements, the needs of the anticipated patient cohort (e.g. for ambulatory services, acute services, etc.), as well as WHS risk assessments/policies. ~ Close access to a patient toilet/shower/change room is required, with direct access from the room preferred to support patients that have changed into gowns. ~ An appropriate patient chair for barium swallows is to be stored outside of room and brought in as required. ~ Acoustic treatment to be considered to manage noise from the imaging device and the adjacent equipment room. All finishes must be meet infection prevention and control requirements. ~ Dimmable light may be considered to support patient comfort. ~ Time tracking requirements (i.e. provision of electric or synchronised clock) is to be confirmed to suit service requirements. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and imaging equipment selection. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | Full AHIA Review | 13 | 2700 | FLUOC | 2 | 15.05.2025 |  | Up to 24 hours | 1-2 staff | The Fluoroscopy Control Room provides the space and equipment for remote control of fluoroscopy equipment and amenities for the review of images and reporting. Direct visibility of the patient through an observation window and direct access to the imaging room is required. | ~ Cable ducts for services between the imaging device and the control area will be required and must be coordinated with the MME vendor. Additional building services connections and outlets are to be coordinated to suit equipment requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The size, quantity and configuration of computer display screens is to be finalised based on the specific image display and processing task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. Providing flexibility of monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
GYAH-GP | Gymnasium, Group Therapy | Allied Health | Translation and QA Only | 105 | 2700 |  | 1 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | up to 15 patients;; 2-3 staff | The Gymnasium - Group Therapy provides space and facilities for patient evaluation, rehabilitation exercise activities, therapy and ambulation training in a group setting. An open area is typically provided for aerobic/movement exercises and may also provide space for group debriefing, discussion and education after sessions. | ~ An external outlook and ready access to outdoor areas is desirable. ~ The range of specialised exercise equipment, open exercise areas and number of clients / patients to be accommodated within a gymnasium will vary from unit to unit and will require confirmation to inform overall space requirements. ~ RCD protection is required to body protected areas in accordance with AS/NZS3003. Quantity and location dependent on selected equipment and circuiting arrangements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | Translation and QA Only | 76 | 2700 |  | 1 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | up to 8 patients;; 3-4 staff | The Gymnasium - Individual Treatment provides space and facilities for one on one patient evaluation, therapy and ambulation training. A number of curtained bays with plinths are typically provided along with an open area accommodating a range of equipment such as stairs, parallel bars and exercise bikes. | ~ An external outlook and ready access to outdoor areas is desirable. ~ The range of specialised exercise equipment, open exercise areas and number of clients / patients to be accommodated within a gymnasium will vary from unit to unit and will require confirmation to inform overall space requirements. ~ RCD protection is required to body protected areas in accordance with AS/NZS3003. Quantity and location dependent on selected equipment and circuiting arrangements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
HYDP | Hydrotherapy Pool | Allied Health | Translation and QA Only | 260 | 5479 |  | 5 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | up to 12 patients;; 2-3 staff | The Hydrotherapy Pool is for patient therapy, rehabilitation and exercise under supervision. | ~ The pool size indicated is 15m x 6m (90m2 - not including pool surrounds). Pool and surrounds to comply with AS 3979 - Hydrotherapy Pools. ~ Ready access is required to adequate change facilities for clients/patients and staff, including accessible showers and toilets. ~ Emergency call points may be wall mounted and/or ceiling-suspended depending on the staffing model and local operational policies. ~ Appropriate storage for aids and equipment will be required separately to the storage of pool maintenance equipment and chemicals. ~ Depth 0.9m to 1.5 m with gradual slope. Depth at deep end may be reduced if paediatric use is likely to be frequent. ~ Ramp access and stair access to be provided with handrails. Pool handrails are required and are not to be recessed. All stainless steel railing to be chlorine resistant. ~ Temperature of water to be 33-34 degrees. Temperature of air to be no more than 6 degrees below water temperature. ~ Wet deck - single channel. ~ Water to be earthed. ~ Internal pool surface and pool surrounds shown as tiled. Tiles or other suitable surface to be non-slip; ensure a high level of slip resistance to tiles on the ramp (vertical surfaces of tiling do not need to be slip resistant). ~ Pool blanket is optional for insulation for energy conservation. ~ Hydraulic hoist may be required; weight rating to be confirmed at project level to suit service requirements. ~ Underwater pressure jets for therapeutic purposes are optional. ~ Departmental planning to provide external windows is recommended. ~ Disinfection system to be advised by expert consultant. ~ Pool may be made available to the community after-hours and on the weekends. Careful consideration will need to be given to location, controlled access and security. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
INTV | Interview Room | Ambulatory Care | Translation and QA Only | 12 | 2700 | INTF | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 8 persons;;; | The Interview Room provides space for confidential discussion and/or counselling between staff, patients and/or family members where required. The Interview Room may also be used as a multipurpose room for small staff groups or discussions. | ~ An external outlook is desirable. Assumes staff will bring their own devices as required. ~ A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
INTV-MH | Interview Room - Mental Health | Mental Health | Full AHIA Review | 14 | 2700 | INTF-MH | 3 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/interview-room-mental-health/?fullscreen=true&utm_source=project-link&rev=3 | Up to 24 hours (dependent on unit operating hours) | up to 6 persons;;; | The Interview Room - Mental Health (may be referred to on projects as a Dialogue Room) provides the space and amenities for interviews, counselling, collaborative care planning and small support network discussions within a Mental Health Unit. | ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Window size and minimum sill height are to be confirmed at project level. Access to natural daylight and an external outlook are desirable. Consider placement of windows and room orientation to suit privacy requirements. The type of window covering (e.g. roller blind, integral venetians, etc.) and associated controls are also to be confirmed at project level. ~ Doors should be selected to support safety, dignity and wellbeing. Selections should be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Inclusion and size of a vision panel to be confirmed to suit service requirements. Privacy film may be applied to the vision panel as required. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ A second door is required for safety and security. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Provision of a workstation is dependent on service requirements (e.g. for computer-based assessments to be undertaken). Impact on furniture arrangement when a workstation is included must be considered to support a positive dynamic between staff and consumers and encourage participation of consumers as equal partners in care. ~ Nearby access to a beverage bay or water fountain is recommended. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
LAUN-MH | Laundry - Mental Health | Mental Health | Full AHIA Review | 6 | 2700 |  | 6 | 31.03.2026 |  | 8am to 6pm, daily (units may limit times for use to minimise noise during certain hours) | 1 patient intermittently;; 1 staff assisting as required | The Laundry - Mental Health provides the space and facilities for consumers in a mental health inpatient unit to wash and dry clothing. Consumer access to this room and level of staff supervision is to be confirmed at project level to suit service requirements. | ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ A second door may be required for safety and security; provision will be dependent on service requirements and local Work Health and Safety (WHS) policies. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ This Standard Component shows a bench, laundry sink, and a domestic washing machine and dryer. Ironing facilities are not included, and provision is based on operational models and will require confirmation of storage requirements. The use and storage of clothes airers/drying racks may be considered, and inclusion would be based on risk assessments and operational models. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. ~ Where caulking required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ The number of washing machines and dryers required will vary depending on the size of the unit and the operational models for handling patient laundry. Additional space will be required to accommodate any increase in the number of machines. ~ While domestic washing machines and dryers are typically selected, the increased frequency of use compared to residential applications must be considered to ensure robustness and longevity of the selected items. ~ Air conditioning and exhaust requirements are to be confirmed to suit the machines selected, the number of machines and anticipated frequency of use. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ A residual current device (RCD) has been shown within this room. Requirements for restricted access to Leakage protection devices (LPDs) such as RCDs, as per AS/NZS 3003, is to be confirmed at project level. Where access needs to be restricted, RCDs may be consolidated in a central area within the unit (e.g. at a staff station). Location is to be confirmed at project level. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | Full AHIA Review | 6.5 | 2700 |  | 6 | 03.12.2025 |  | Up to 24 hours (units may limit times for use to minimise noise during certain hours) | 1-2 patients / visitors;; 1 staff assisting as required | The Laundry - Patient / Visitor provides space and amenities for patient and/or visitor use, including a washing machine, a dryer, a laundry sink, bench space and storage for a small amount of detergents and equipment such as an iron, distilled water, ironing board and folding drying rack. | ~ Domestic appliances have been indicated in this room. The use of commercial machines may be considered at project level to suit anticipated frequency of use and operational models. ~ A tall storage unit has been indicated for storage of equipment such as an iron (and distilled water), an ironing board and a folding drying rack. Provision of this equipment is to be confirmed at project level to suit operational models. ~ The type and storage requirements for any chemicals (e.g. laundry detergents, stain removers, etc.) are to be confirmed at project level to suit local jurisdictional policies and operational service requirements. ~ Exhaust requirements are to be confirmed to suit the selected appliances. ~ Body Protection has been indicated above as required. Depending on the context of this room (e.g. where it is only to be provided as an amenity for visitor in a dedicated overnight area), Body Protection requirements may not apply. Project teams must confirm if the room is to be classified as a Body Protected patient area based on the potential for use of this room by patients in accordance with the requirements of AS/NZS 2500. ~ Mobile duress coverage has been indicated as required with anticipated use by patients and occasional assistance being required from staff. Requirements for fixed duress and/or mobile duress coverage are to be confirmed by project teams to suit room context, service requirements, and local security and WHS policies. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | Translation and QA Only | 165 | 3000 |  | 1 | 07.04.2026 |  | 8am to 6pm, Mon - Fri (dependent on unit operating hours) | 1 patient;; up to 4 staff | The Linear Accelerator Treatment Room provides space and facilities for the treatment of patients requiring external beam radiation therapy (EBRT). A collocated Control Room is required for the remote operation of equipment. | ~ Cable pathways for services between the Control Room, Modulator Room and Treatment Room must be established and coordinated prior to construction and developed based on vendor and physics requirements. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ The Treatment Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints, including the provision of a maze entry or shielded door. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ The modulator may need to be accommodated within the Treatment Room. If so, this will be concealed by a wall, with a door for access. Depending on the quality of the power supply at a site, a power conditioner may be required and is typically located with the modulator. Additional noise from this equipment should also be accounted for with acoustic treatment. ~ Visibility of the Treatment Room from exit and via observation cameras is required to ensure all persons are clear of the room before treatment commences. A last person out button is to be provided, as well as a sensor gate and/or physical gate at the entry of the maze. A Beam-On/Off light system is required at the entry to be illuminated when treatment begins/ends. ~ Additional medical gases may be provided (including additional oxygen, additional suction, nitrous oxide and scavenge) depending on clinical requirements such as the provision of anaesthetic services. ~ Acoustic requirements will vary depending on the equipment procured and its proximity to the patient treatment area. For patient and staff comfort, acoustics should be considered to reduce the impact of noise from the equipment. ~ Dimmable lights are to be provided and are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort and speakers and connections should be provided to allow music to be played and controlled individually for each bunker. ~ Air conditioning is to be provided to control the room temperature and humidity to meet the equipment suppliers requirements; high equipment loads shall be accounted for. Air conditioning equipment shall be located outside of this room with ductwork to be installed to follow the entry maze with any penetrations considered to ensure radiation protection. Where possible, it is preferred that ductwork in the ceiling is designed to the perimeter of room for future flexibility to provide ceiling mounted equipment. ~ Cooling shall be provided to the linear accelerator equipment in the form of chilled water to meet the suppliers requirements, independent chiller equipment is preferred. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. Small UPS units are normally required as a minimum to support control and operating equipment. In some cases, these are supplied with the medical equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be provided depending on clinical/service requirements. The provision of these technologies is to be confirmed by the project and may have additional requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. ~ Allow sufficient distance between the isocentre of the machine and primary shielding wall for the flexibility to provide specialised treatments, e.g. Total Body Irradiation (TBI), depending on service requirements. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | Translation and QA Only | 21 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, Mon - Fri (dependent on unit operating hours) | up to 5 staff | The Linear Accelerator Control room is located adjacent to the Treatment Room for remote control of equipment with audio and visual contact with the patient via cameras, speakers and microphones. Each Treatment Room requires a Control Room. | ~ Cable pathways for services between the Control room to the Treatment Room must be established and coordinated prior to construction. Radiation shielding is to be as advised by a Radiation Consultant. ~ Air conditioning to provide comfort conditions; high equipment loads shall be accounted for. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. Small UPS units are normally required as a minimum to support control and operating equipment. In some cases, these are supplied with the medical equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ Cable management and the potential for computers to be consolidated into a rack (either within the room or in a dedicated, collocated air conditioned room/cupboard) to be determined at project level. ~ Provision of a height adjustable workstation may be considered depending on local policies and staff accessibility requirements. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | Translation and QA Only | 10 | 2700 | LNPT-10 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 6 patients / visitors;; 1-2 staff intermittently | The Patient Lounge provides an environment away from clinical areas and/or patient bedrooms for patients and visitors to meet and socialise. It is an area where family groups can visit together with patients. | ~ A range of occupants will need to be accommodated including adults, children, able-bodied people as well as people with disabilities. ~ The size of lounge areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ Access for a patient lifter or patient bed may be required depending on patient cohort and service requirements. ~ The Patient Lounge is often located in close proximity to or combined with a Bay - Beverage. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. ~ Duress provision will be dependent on service requirements. ~ Provision of a hearing augmentation system may be required depending on television and amplification system provided. ~ Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Room may be designed to be open to a corridor. Additional transfer of noise to adjacent patient care areas to be considered if room is not enclosed. ~ The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. ~ Natural light and external outlook is essential. | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | Translation and QA Only | 20 | 2700 | LNPF-20 | 3 | 07.04.2026 |  | Up to 24 hours | up to 10 patients / visitors;; 1-2 staff intermittently | The Patient Lounge provides an environment away from clinical areas and/or patient bedrooms for patients and visitors to meet and socialise. It is an area where family groups can visit together with patients. | ~ A range of occupants will need to be accommodated including adults, children, able-bodied people as well as people with disabilities. ~ The size of lounge areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ Access for a patient lifter or patient bed may be required depending on patient cohort and service requirements. ~ The Patient Lounge is often located in close proximity to or combined with a Bay - Beverage. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. ~ Duress provision will be dependent on service requirements. ~ Provision of a hearing augmentation system may be required depending on television and amplification system provided. ~ Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Room may be designed to be open to a corridor. Additional transfer of noise to adjacent patient care areas to be considered if room is not enclosed. ~ The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. ~ Natural light and external outlook is essential. | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MAMMO | Mammography Room | Medical Imaging | Full AHIA Review | 18 | 2700 |  | 5 | 15.05.2025 |  | Up to 24 hours | 1 patient;; 1-2 staff | The Mammography Room provides the space and equipment for undertaking diagnostic and screening mammography, as well as performing minor procedures such as biopsies. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between the imaging device and the control area will be required and must be coordinated with the MME vendor. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room will require sufficient clearance to allow access for a patient on a bed. ~ Close access to a patient toilet and change room is required, with direct access from the room being preferred to support patients that have changed into gowns. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | Translation and QA Only | 14 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Medication Room, 14m2 is used for the secure storage of medications, including intravenous fluids, and a small amount of medication-related clean consumables. | ~ The medication room may provide storage for drugs of dependence in accordance with relevant legislation. ~ Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. ~ Secured staff only access to the room is required. ~ The provision and placement of CCTV cameras is dependent on jurisdictional policies. ~ Refer to project specific requirements for the provision of automated medication management systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MEET-15 | Meeting Room, 15m2 | Administration | Translation and QA Only | 15 | 2700 | MEET-L-15 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 8 staff seated | The Meeting Room, 15m² provides the space and amenities to accommodate up to 8 staff (seated) for meetings, education and training activities. | ~ Inclusion of videoconferencing systems and audio visual (AV) equipment will not be required in all 15m² meeting rooms, particularly where the room is predominantly used for ad hoc meetings with BYO devices. Provision of ICT/AV equipment and services will need to be confirmed based on service requirements. ~ Where provided, the configuration of videoconferencing systems and AV equipment will vary to suit service requirements and local ICT policies. The display system, sound system, microphone, camera, control panels and supporting AV equipment must be carefully considered within the context of the department/facility in order to provide a cohesive, intuitive solution for users. ~ Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. Decor should also be light/neutral and free from busy patterns within the camera view for optimal image quality. ~ Furniture and layout will vary to suit service requirements. Selection of furniture that supports reconfiguration of the layout for flexible use of the space is recommended, e.g. provision of stackable chairs and folding tables. ~ Due to the flexibility of furniture arrangements possible within meeting rooms, the occupancy of the room will vary. The total number of people that may be accommodated in the space will be dependent on the furniture layout. ~ Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) will be dependent on the specifications/features of the selected ICT/AV equipment and software. Provision of a hearing augmentation system is to be confirmed at project level in consultation with accessibility and ICT experts. ~ Inclusion of a fixed duress button may be considered depending on the location of the room within a department. Fixed duress may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Where a meeting room is intended to be used with patients and/or support persons, carers, family, etc., additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be required to suit service requirements and local WHS and security policies. An operational model for responding to calls will be needed to support the inclusion of duress call system. ~ When a meeting room is to be used with patients and/or support persons, carers, family, etc. in mental health settings, an alternative egress door should be provided. Where appropriate, equipment may be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Room booking panels may be provided to suit the department/facility approach to room scheduling. ~ Acoustics are to be carefully considered to ensure appropriate sound levels and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption, particularly where videoconferencing equipment is provided. Background noise (e.g. from air conditioning) should be minimised. Some hard surfaces may be covered with appropriate acoustic finishes to reduce reverberation as required. ~ Ready access to a telephone in an adjacent space may be required for staff to answer pagers. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MEET-20 | Meeting Room, 20m2 | Administration | Translation and QA Only | 20 | 2700 | MEET-L-20 | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 12 staff seated | The Meeting Room, 20m² provides the space and amenities to accommodate up to 12 staff (seated) for meetings, education and training activities. | ~ The configuration of videoconferencing systems and AV equipment will vary to suit service requirements and local ICT policies. The display system, sound system, microphone, camera, control panels and supporting AV equipment must be carefully considered within the context of the department/facility in order to provide a cohesive, intuitive solution for users. ~ Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. Decor should also be light/neutral and free from busy patterns within the camera view for optimal image quality. ~ Furniture and layout will vary to suit service requirements. Selection of furniture that supports reconfiguration of the layout for flexible use of the space is recommended, e.g. provision of stackable chairs and folding tables. ~ Due to the flexibility of furniture arrangements possible within meeting rooms, the occupancy of the room will vary. The total number of people that may be accommodated in the space will be dependent on the furniture layout. ~ Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) will be dependent on the specifications/features of the selected ICT/AV equipment and software. Provision of a hearing augmentation system is to be confirmed at project level in consultation with accessibility and ICT experts. ~ Inclusion of a fixed duress button may be considered depending on the location of the room within a department. Fixed duress may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Where a meeting room is intended to be used with patients and/or support persons, carers, family, etc., additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be required to suit service requirements and local WHS and security policies. An operational model for responding to calls will be needed to support the inclusion of duress call system. ~ When a meeting room is to be used with patients and/or support persons, carers, family, etc. in mental health settings, an alternative egress door should be provided. Where appropriate, equipment may be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Room booking panels may be provided to suit the department/facility approach to room scheduling. ~ Acoustics are to be carefully considered to ensure appropriate sound levels and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption, particularly where videoconferencing equipment is provided. Background noise (e.g. from air conditioning) should be minimised. Some hard surfaces may be covered with appropriate acoustic finishes to reduce reverberation as required. ~ Ready access to a telephone in an adjacent space may be required for staff to answer pagers. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MEET-30 | Meeting Room, 30m2 | Administration | Translation and QA Only | 30 | 2700 | MEET-L-30 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 18 staff seated | The Meeting Room, 30m² provides the space and amenities to accommodate up to 18 staff (seated) for meetings, education and training activities. | ~ The configuration of videoconferencing systems and AV equipment will vary to suit service requirements and local ICT policies. The display system, sound system, microphone, camera, control panels and supporting AV equipment must be carefully considered within the context of the department/facility in order to provide a cohesive, intuitive solution for users. ~ Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. Decor should also be light/neutral and free from busy patterns within the camera view for optimal image quality. ~ Furniture and layout will vary to suit service requirements. Selection of furniture that supports reconfiguration of the layout for flexible use of the space is recommended, e.g. provision of stackable chairs and folding tables. ~ Due to the flexibility of furniture arrangements possible within meeting rooms, the occupancy of the room will vary. The total number of people that may be accommodated in the space will be dependent on the furniture layout. ~ Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) will be dependent on the specifications/features of the selected ICT/AV equipment and software. Provision of a hearing augmentation system is to be confirmed at project level in consultation with accessibility and ICT experts. ~ Inclusion of a fixed duress button may be considered depending on the location of the room within a department. Fixed duress may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Where a meeting room is intended to be used with patients and/or support persons, carers, family, etc., additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be required to suit service requirements and local WHS and security policies. An operational model for responding to calls will be needed to support the inclusion of duress call system. ~ When a meeting room is to be used with patients and/or support persons, carers, family, etc. in mental health settings, an alternative egress door should be provided. Where appropriate, equipment may be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Room booking panels may be provided to suit the department/facility approach to room scheduling. ~ Acoustics are to be carefully considered to ensure appropriate sound levels and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption, particularly where videoconferencing equipment is provided. Background noise (e.g. from air conditioning) should be minimised. Some hard surfaces may be covered with appropriate acoustic finishes to reduce reverberation as required. ~ Ready access to a telephone in an adjacent space may be required for staff to answer pagers. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MEET-55 | Meeting Room, 55m2 | Administration | Translation and QA Only | 55 | 2700 | MEET-L-55 | 3 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 45 staff seated | A large multipurpose room for staff meetings, education and training activities. Requirement for Hearing Augmentation to be confirmed. | ~ An operable wall may be provided to open this room to an adjoining meeting room, increasing capacity for lectures, training activities or events. Connections and coordination between AV and video conferencing equipment in adjoining rooms will need to be considered to support both separate and combined activities. ~ Video conferencing systems and AV equipment will be dependent on service requirements and local ICT policies. The lectern design, display system, sound system, microphone, room and video conferencing control and supporting AV equipment must be carefully considered to provide a cohesive solution for users. ~ To support video conferencing, decor should be light/neutral and free from busy patterns within the camera view for optimal image quality. ~ Room booking panels may be provided to suit service/facility approach to room scheduling. ~ Occupancy will vary, with the total number of people that may be accommodated in the space dependent on furniture layout. ~ Furniture and layout will vary to suit service requirements. Furniture considerations include provision of chairs with integral note tables, stackable chairs and folding tables to support reconfiguration of the layout for flexible use of the space. ~ A storage zone or enclosed storeroom may be provided to hold additional furniture to support alternate layouts. If multiple rooms are provided, furniture storage areas may be shared. ~ Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. ~ Acoustics to be carefully considered to ensure appropriate sound levels, particularly with video conferencing equipment provided, and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption. Background noise (e.g. from air conditioning) should be minimised. Hard surfaces may be covered to reduce reverberation as required. ~ Where a meeting room is intended to be used with patients and/or family, additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be considered to suit service requirements. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ When used with patients and/or family in mental health settings, an alternative egress door should be provided. Where possible, equipment should be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. ~ Ready access to a telephone in an adjacent space may be required to answer pagers. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MEET-9 | Meeting Room, 9m2 | Administration | Translation and QA Only | 9 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 staff seated | The Meeting Room, 9m² provides the space and amenities to accommodate up to 4 staff (seated) for interviews, meetings, and education and training activities. This room may also function as a 'breakout' room in an open plan office environment. For small meeting spaces suitable for use with patients/visitors refer to the Interview Room (INTV) Standard Component. | ~ Inclusion of videoconferencing systems and audio visual (AV) equipment will not be required in all 9m² meeting rooms, particularly where the room is predominantly used for ad hoc meetings with BYO devices. Provision of ICT/AV equipment and services will need to be confirmed based on service requirements. ~ Where provided, the configuration of videoconferencing systems and AV equipment will vary to suit service requirements and local ICT policies. The display system, sound system, microphone, camera, control panels and supporting AV equipment must be carefully considered within the context of the department/facility in order to provide a cohesive, intuitive solution for users. ~ Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. Decor should also be light/neutral and free from busy patterns within the camera view for optimal image quality. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) will be dependent on the specifications/features of the selected ICT/AV equipment and software. Provision of a hearing augmentation system is to be confirmed at project level in consultation with accessibility and ICT experts. ~ Inclusion of a fixed duress button may be considered depending on the location of the room within a department. Fixed duress may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Room booking panels may be provided to suit the department/facility approach to room scheduling. ~ Acoustics are to be carefully considered to ensure appropriate sound levels and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption, particularly where videoconferencing equipment is provided. Background noise (e.g. from air conditioning) should be minimised. Some hard surfaces may be covered with appropriate acoustic finishes to reduce reverberation as required. ~ Ready access to a telephone in an adjacent space may be required for staff to answer pagers. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | Translation and QA Only | 30 | 3000 |  | 4 | 07.04.2026 |  | 8am to 5pm, daily (may vary depending on services requirements) | up to 4 staff | The Mortuary - Autopsy Room is for undertaking post mortem examinations. An observation area is to be provided to at least one Autopsy Room within a department. | ~ Layout of tables and orientation of observation bay may be adjusted to suit the type of autopsy being performed (e.g. coronial or non-coronial). The Mortuary - Autopsy Room should be located with ready access to Mortuary - Body Holding. ~ doors to be sealed for odours, post mortem table to have water flushing system. Appropriate Smoke/Heat detection to be considered. | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | Translation and QA Only | 22 | 2700 | MOR-CS | 4 | 07.04.2026 |  | 24 hours | 1-2 staff intermittently | The Mortuary - Body Holding provides refrigerated storage for the temporary holding of bodies with an adjacent area to transfer a body from a trolley into storage. | ~ The room can be configured with refrigerated cabinets or as a cool room depending on service requirements. ~ The Mortuary - Body Holding should be located with ready access to the Mortuary - Viewing Room. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | Translation and QA Only | 7 | 2700 | MOR-EX | 4 | 07.04.2026 |  | Up to 24 hours | 1-2 staff intermittently | The Mortuary - Body Reception is an area for receiving bodies from the hospital and checking-in to the holding room/cool room as well as the checking-out of bodies for release to funeral directors, relatives or for transfer to the coroner. | ~ This room should be located on a corridor that is in close proximity to both the staff-only mortuary entry and the exit to the funeral director's covered parking area. Entry to this area by authorised personnel only. Handwashing facilities should be located in close proximity. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | Translation and QA Only | 8 | 2700 |  | 5 | 07.04.2026 |  | 8am to 5pm, daily (may vary depending on services requirements) | up to 5 visitors; 1-2 staff | The Mortuary - Viewing Room is provided for relatives and others to view a body with the support of a social worker. The Mortuary - Viewing Room will be located adjacent to the Mortuary - Waiting. | ~ A body may be viewed through a window from within the Mortuary - Waiting, with access provided between the two rooms provided to allow for viewing a body directly. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | Translation and QA Only | 9 | 2700 |  | 5 | 07.04.2026 |  | 8am to 5pm, daily (may vary depending on services requirements) | 4-5 visitors; 1-2 staff | The Mortuary - Waiting provides an area for relatives and others to await the viewing of a body and to have private discussions with social workers. The area should be comfortable and non-clinical in appearance with furnishings and artwork that are culturally appropriate. Natural light is desirable. The Mortuary - Waiting will be located adjacent to the Mortuary - Viewing Room. A body may be viewed through the window from within the Mortuary - Waiting, with access provided between the two rooms to view a body directly. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
MRI | MRI Room | Medical Imaging | Full AHIA Review | 46 | 2700 | MRIR | 2 | 15.05.2025 |  | Up to 24 hours | 1 patient;; up to 3 staff | The MRI Imaging Room is designed for undertaking Magnetic Resonance Imaging (MRI) scanning with direct overview from the adjoining MRI Control Room. The MRI Imaging Room must have the MRI Equipment Room immediately adjacent for accommodating supporting power and control equipment. | ~ The MRI Imaging Room is located within Zone IV as set out in the RANZCR MRI Safety Guidelines. ~ Magnetic and Radiofrequency shielding is to be as advised by specialist consultant. ~ The entrance of the MRI Imaging Room must be visible from the MRI Control Room. ~ Appropriate warning signs are required indicating the presence and permanency of a strong magnetic field and identifying items for which entry is prohibited. ~ There shall be a designated site outside the MRI Imaging Room, outside the 0.5m T line and away from the room entry door, for patients to be brought to if requiring emergency treatment. ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between imaging unit, the equipment room and the control room will be required and must be coordinated with the MME vendor. ~ Structural assessment is required to ensure the floor of the MRI Imaging Room and the access route for installation/replacement of equipment will accommodate the weight of the MRI unit. ~ A removable panel to the wall of the MRI Imaging Room is required to allow MRI Unit replacement. ~ Depending on service requirements, general anaesthesia may be administered in this room. This must be confirmed by project teams to ensure appropriate workflows are provided to support this model of care, to confirm the correct building services are provided to ensure patient safety, and to determine medical gas system requirements. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Waveguide ports, also known as penetration panels, are specialised openings in the walls designed to allow the passage of various items like tubing and cables without compromising the magnetic and radiofrequency shielding. Waveguide ports are required from the MRI Control Room to the MRI Imaging Room. Where a service includes administration of anaesthetic, waveguide ports are required from the Anaesthetic Preparation Area to the MRI Imaging Room, along with an observation window with clear view of the patient. ~ All equipment and fittings in the room to be MRI compatible and constructed of non-ferrous material ~ Consideration for the use of multi-parameter MRI compatible monitors and infusion pumps to be confirmed at project level to suit local jurisdictional policies and operational service requirements. Where not provided, a cable port may need to be installed to run clinical leads from outside the imaging room to the patient for continuous monitoring and provision of care. ~ Florescent light fixtures are not permitted in the MRI Imaging Room ~ Temperature and humidity control are required. ~ In planning, room location to be considered in relation to location and movement of metal object outside the MRI Room, such as beds, trolleys, lifts, motor vehicles, trains, trams, AGV’s, transformers and AC cables. Room location must also take into consideration static elements such as steel beams and reinforcement, especially beneath the MRI Unit. ~ Room location to consider building vibration limits that can impact image quality. This may include new building works and potential refurbishments nearby. ~ Smoke detection within the MRI room shall be multi-aspirated detection with the sampling unit located outside of the risk area. Fire sprinklers and pipework shall be of non-ferrous material and suitable for an MRI room. A performance solution shall be completed to address the minimum fire protection requirements of the MRI room. ~ The room will require sufficient clearance to allow access for a patient on an MRI compatible trolley. Trolley movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Patient transfer aids such as patient slides and hover mats are to be considered for assisted patient transfers to and from the MRI table. Final selection of transfer aids will be dependent on service requirements, the needs of the anticipated patient cohort (e.g. for ambulatory services, acute services, etc.), as well as WHS risk assessments/policies. All equipment to be used within the room must be non-ferrous/MRI compatible. ~ Acoustic treatment to be considered to manage noise from the imaging device and the adjacent equipment room. All finishes must be meet infection prevention and control requirements. ~ Dimmable light may be considered to support patient comfort. Similarly, feature artwork on the ceiling may be considered above the MRI table. ~ Time tracking requirements (i.e. provision of electric or synchronised clock) is to be confirmed to suit service requirements. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE
MRI-CTRL | MRI Control Room | Medical Imaging | Full AHIA Review | 14 | 2700 | MRICR | 2 | 15.05.2025 |  | Up to 24 hours | up to 3 staff | The MRI Control Room provides the space and equipment for remote control of MRI equipment, and the amenities for review of images and reporting. Direct visibility of the patient through an observation window and direct access to the imaging room is required. | ~ The MRI Control Room is located within Zone III (the outer controlled area) as set out in the RANZCR MRI Safety Guidelines. ~ The entrance of the MRI Imaging Room must be visible from the MRI Control Room. ~ Magnetic and Radiofrequency shielding is to be as advised by specialist consultant. ~ Cable ducts for services between the imaging unit, the equipment room and the control room will be required and must be coordinated with the MME vendor. Additional building services connections and outlets are to be coordinated to suit equipment requirements. ~ Waveguide ports, also known as penetration panels, are specialised openings in the walls designed to allow the passage of various items like tubing and cables without compromising the magnetic and radiofrequency shielding. Waveguide ports are required from the MRI Control Room to the MRI Imaging Room. ~ The size, quantity and configuration of computer display screens is to be finalised based on the specific image display and processing task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. Providing flexibility of monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | Translation and QA Only | 12 | 2700 | OFF-S12 | 6 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 staff (with up to 3 additional staff / visitors intermittently) | The Office - 1 Person, 12m² provides the space and amenities to accommodate 1 staff member carrying out computer based and administrative tasks in privacy. The room size allows for a small table for small meetings, ad hoc discussions or interviews with up to 3 additional persons as required. | ~ Consider the placement of power and data within the room to support flexible arrangement of the furniture to suit user requirements. ~ Inclusion of a fixed duress button is dependent on the location of the room and may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Requirements for the size and ergonomic features of the workstation are to be confirmed at project level to suit local Work Health and Safety (WHS) and office accommodation policies. ~ Provision and extent of emergency/standby power is to be confirmed at project level to suit site and service requirements. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | Translation and QA Only | 9 | 2700 | OFF-S9 | 6 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 staff (with up to 2 additional staff / visitors intermittently) | The Office - 1 Person, 9m² provides the space and amenities to accommodate 1 staff member carrying out computer based and administrative tasks in privacy. Small meetings, ad hoc discussions or interviews with 1-2 additional persons may be conducted intermittently in this space. | ~ Consider the placement of power and data within the room to support flexible arrangement of the furniture to suit user requirements. ~ Inclusion of a fixed duress button is dependent on the location of the room and may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Requirements for the size and ergonomic features of the workstation are to be confirmed at project level to suit local Work Health and Safety (WHS) and office accommodation policies. ~ Provision and extent of emergency/standby power is to be confirmed at project level to suit site and service requirements. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
OFF-2P | Office - 2 Person | Administration | Translation and QA Only | 12 | 2700 |  | 6 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 2 staff (with up to 2 additional staff / visitors intermittently) | The Office - 2 Person provides the space and amenities to accommodate 2 staff members carrying out computer based and administrative tasks in privacy. Small meetings, ad hoc discussions or interviews with 1-2 additional persons may be conducted intermittently in this space. | ~ Consider the placement of power and data within the room to support flexible arrangement of the furniture to suit user requirements. ~ Inclusion of a fixed duress button is dependent on the location of the room and may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Requirements for the size and ergonomic features of the workstation are to be confirmed at project level to suit local Work Health and Safety (WHS) and office accommodation policies. ~ Provision and extent of emergency/standby power is to be confirmed at project level to suit site and service requirements. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | Translation and QA Only | 15 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 4 workstations;;; | An Office - Clinical Workroom, typically adjoining or in close proximity to a Staff Station, is for staff to write up notes, review patient records and digital images, hold confidential discussions, store records and conduct handovers. | ~ One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Staff Station. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication. ~ Location of power and data outlets (above or below the bench) is to meet local operational/WHS requirements. Cable management solutions to be considered to meet infection control and cleaning requirements. ~ A desktop printer may be provided. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. ~ Provision of height adjustable workstations may be considered depending on local policies and staff accessibility requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | Translation and QA Only | 5 | 2700 |  | 2 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 2 staff | The Write-up Bay provides a write-up bench for use by members of the patient care team. In this space the User may review and write-up patient records, enter patient data on computer and make telephone calls. | ~ If located within the Operating Unit it may also include an optional area for porters to wait until paged or called by staff. ~ The Write-up space must not impede the corridor. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
OFF-WS | Office - Workstation | Administration | Translation and QA Only | 4.5 | 2700 | OFF-SWS | 3 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 staff / visitor | The Office - Workstation indicates the space and amenities required within an open plan arrangement to accommodate 1 staff member carrying out computer based and administrative tasks. | ~ Depending on overall layout of the open plan office space, services for workstations may be wall mounted or soft-wired cable trays may be connected via an umbilical to the floor or ceiling. ~ Inclusion of fixed duress buttons within the overall open plan office space may be considered depending on the location of the room within a department. Fixed duress may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Requirements for the size and ergonomic features of the workstation are to be confirmed at project level to suit local Work Health and Safety (WHS) and office accommodation policies. ~ A modesty panel or extended acoustic panel may be required for workstations depending on layout of the overall open plan office space. ~ Shared storage facilities may be allocated to the overall open plan office space separately to the workstation. ~ Small meeting tables for informal discussions may be provided between a number of workstations in larger open plan areas. ~ Where devices (e.g. laptops) are expected to be brought to the workstation by the user, a dock may be provided in lieu of a CPU. ~ Adequate coverage in the overall open plan office space by ceiling mounted wireless access points (WAPs) is to be provided. ~ Provision and extent of emergency/standby power is to be confirmed at project level to suit site and service requirements. ~ Access to natural light is desirable and, where overall department planning allows, external windows should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
OPG | OPG Room | Medical Imaging | Full AHIA Review | 19 | 2700 |  | 2 | 15.05.2025 |  | Up to 24 hours | 1 patient;; 1 staff | The OPG Room provides the space and equipment for diagnostic orthopantomogram x-ray imaging which produces panoramic x-rays of the jaw. This Standard Component may be located within a Dental/Oral Health Unit or Medical Imaging Unit. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between the imaging device and the control area will be required and must be coordinated with the MME vendor. ~ The OPG Room is designed to accommodate OPG, Lateral Cephalogram and Cone Beam CT imaging devices with minor adjustments to suit equipment and meet shielding requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
OR-GEN | Operating Room - General | Operating | Full AHIA Review | 60 | 3000 | ORGN | 7 | 06.05.2025 |  | Up to 24 hours | 1 patient;; up to 12 staff | An Operating Room provides an aseptic environment in which to carry out surgical procedures on a patient under local, regional or general anaesthetic. The Operating Room - General is flexibly used for various surgical procedures that require complex and large equipment. This Standard Component may be adapted for Operating Rooms dedicated to different specialties, for example neurosurgery, orthopaedics, cardiac surgery, obstetrics and trauma. | ~ The minimum critical dimension centred on the sterile zone is 7400mm clear to ensure adequate space within the sterile zone (min 3400mm wide), circulation zone (min 1000mm wide) and equipment zone (min 1000mm wide). ~ Where the Operating Room is intended to be used for cardiothoracic procedures and for some forms of hybrid operating theatres, cardiac electrical protection is required. ~ Isolated power supply is required individually to each medical services pendant, together with its associated line isolation and overload monitors. ~ Location and quantity of RCD outlets to suit overall electrical service provision and is to be confirmed by the project to suit local engineering services guidelines/policies. ~ A wall mounted medical services panel has been indicated as optional and may be provided for theatres where, for example, obstetric procedures are intended to be undertaken and the additional panel provides access to services for an infant away from the operating table if required. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ If laser equipment is to be used, ‘laser in use’ warning lights are required outside all entry doors to the room. ~ If x-ray equipment is to be used, ‘x-ray in use’ warning lights are required outside all entry doors to the room. Radiation shielding will also be required and is to be assessed by a Radiation Consultant. ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Anaesthetic Preparation Room and Exit Bay. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Height of doors to be confirmed to suit the movement of mobile equipment such as mobile imaging devices. ~ If external windows are provided, they are to be double glazed with integral venetian blinds (with either manual or automated controls). ~ Room lights to be dimmable. Lighting control to room rights, warning signs, and operating lights to be coordinated within the room and an appropriate lighting control panel to be provided to functional requirements. ~ Configuration of services pendant (horizontal or vertical) to suit services requirements. Accessories (e.g. shelves, drawers, rails, etc.) are optional and can be selected to suit service and equipment requirements. Services allocations are indicative - type and number of services on the pendant to suit service requirements ~ Services pendant arms to have an adequate reach to be moved out of the way to allow for adequate room for movement of a patient trolley and mobile equipment. ~ If not dedicated for use in a particular Operating Room, microscope(s) should be located in a nearby equipment bay in close proximity for flexible use between Operating Rooms. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
OVBR | Overnight Stay - Bedroom | Staff Amenities | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Available 24 hours | 1 staff / visitor | A 1 bed room with an adjoining ensuite for staff, parents or carers needing to remain on close call overnight. | ~ The room shall be lockable. ~ An external outlook is required. ~ Overnight stay bedroom and ensuite layouts may be adjusted to provide accessible facilities i.e. as required if a standalone suite is provided or in a portion of rooms if multiple overnight stay suites are provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
OVES | Overnight Stay - Ensuite | Staff Amenities | Translation and QA Only | 5 | 2700 |  | 6 | 07.04.2026 |  | Available 24 hours | 1 staff / visitor | An ensuite with shower, toilet and basin adjoining the overnight stay bedroom for staff, carers or parents needing to remain on close call overnight. | ~ Overnight stay bedroom and ensuite layouts may be adjusted to provide accessible facilities e.g. as required if a standalone suite is provided or in a portion of rooms if multiple overnight stay suites are provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PAR | Parenting Room | Sanitary Facilities | Translation and QA Only | 9 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 persons intermittently;;; | The Parenting Room provides an enclosed, lockable room with the amenities required for parents to feed and change babies including a changing table, waste bin, sink, and arm chair. Access and clearance for prams is required. | ~ The Parenting Room should be located to have ready access to other public amenities sanitary facilities and is often collocated with waiting areas. ~ Inclusion of a small fridge within the room may be considered if the room is located to serve a staff area; provision will be dependent on operational policies. ~ This Standard Component shows a wall mounted drop-down change table. Custom joinery for baby changing facilities may be considered and provision is to be determined at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PBSC | Patient Bay - Specimen Collection | Pathology | Translation and QA Only | 9 | 2700 | SPECC | 4 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1 patient; 1 visitor; 1 staff | A Patient Bay used for the collection of specimens to be transferred to a laboratory for testing. | ~ Ready access to a handwashing basin is required. ~ Ready access may be required to a pneumatic tube bay that is in a staff supervised area. ~ Recliner must be able to lay flat to support the patient in the event of an adverse reaction (e.g. fainting). ~ A desk may be provided in lieu of Workstation on Wheels depending on operational model. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ A risk assessment should be undertaken to inform staff safety requirements with adjoining cubicles which may require adjustments to the design and/or operational strategies, such as the use of mobile duress systems. ~ Refer to the Pathology HPU for paediatric requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | Translation and QA Only | 9 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Medical Day Treatment may be used for assessment and treatment of non-admitted patients receiving scheduled treatment in either a bed or recliner (e.g. for infusions such as antibiotics and chemotherapy). | ~ A staff handwashing basin will be provided for each 4 bays ~ The Patient Bay will have, wherever possible, clear line of sight to a staff station and close access to a patient toilet. ~ Access to natural light and views is required. ~ Medical Gases may be provided individually to each bay or shared between two bays depending on service requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | Translation and QA Only | 9 | 2700 | TRMT-RD-A | 5 | 07.04.2026 |  | 7am to 9pm, daily (may vary depending on service requirements) | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Renal Dialysis is for patients receiving haemodialysis therapy. Treatments for each patient may take from 3 to 6 hours, occurring up to 3 days per week. | ~ A staff handwashing basin will be provided for each 4 bays and the Patient Bay will have, wherever possible, clear line of sight to a staff station. ~ Access to natural light and views is required. ~ Furniture and furnishings should provide a high level of patient comfort and amenity. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | Translation and QA Only | 9 | 2700 | TRMT-RD-B | 4 | 07.04.2026 |  | 7am to 9pm, daily (may vary depending on service requirements) | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Renal Dialysis is for patients receiving haemodialysis therapy. Treatments for each patient may take from 3 to 6 hours, occurring up to 3 days per week. | ~ A staff handwashing basin will be provided for each 4 bays and the Patient Bay will have, wherever possible, clear line of sight to a staff station. ~ Access to natural light and views is required. ~ Furniture and furnishings should provide a high level of patient comfort and amenity. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | Translation and QA Only | 50 | 3000 |  | 2 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | 1 patient;; up to 3 staff assisting | The PET-CT Imaging Room provides the area and facilities for Positron Emission Tomography-Computed Tomography (PET/CT) scanning procedures with a Control Room and Equipment Room (as required) located nearby. | ~ It is not essential that the control is directly adjacent to the Imaging Room where patients are monitored via observation cameras, however ready access is required to attend to patient needs. If the Control Room is adjacent an observation window may be provided and shielding requirements will need to be confirmed. ~ Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. ~ Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access and support structure as required. ~ The PET-CT Imaging Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ Configuration of medical gases is to be confirmed to meet clinical requirements such as the provision of anaesthetic services. ~ Dimmable lights are recommended and are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort. ~ 'X-ray in Use' lights are required outside each entry door. ~ Laser marker system for procedure planning may be required subject to model of care and equipment selected. ~ Structural assessment is required to ensure the floor will be rigid with no vibration and will accommodate the weight of the PET-CT unit. ~ Room temperature and humidity control is required. Temperature requirements for equipment are to be confirmed by the vendor, including requirement for circulated cooling water. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the PET-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ An optional laser system for patient positioning and procedure planning has been indicated and may be provided subject to service requirements. A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be considered depending on clinical/service requirements (e.g. for radiation therapy planning). The provision of these technologies is to be confirmed by the project and may have additional requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. ~ Consideration needs to be given to the clearances of equipment and replacement part delivery routes. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PHA-CO | Pharmacy - Counter | Pharmacy | Translation and QA Only | 9 | 2700 |  | 4 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1-2 staff | The Pharmacy Counter provides a reception point for the Pharmacy Unit for patients and staff to drop off prescriptions to be filled and collect dispensed prescriptions. | ~ The Counter is to have good visibility of the waiting area and visitors as they approach. ~ Information on prescribed medications will be provided to patients at the counter and a degree of privacy is required for these discussions. Interview rooms may be located nearby to provide more private information or counselling. ~ Cash handling and EFTPOS facilities may be required in this space depending on operational models and the proximity of the Unit to the central hospital cashier. ~ Security glazing will be required. The design must support clear communication between pharmacy staff and patients with communication slots. A hearing augmentation system may be considered. Small items will also need to be passed through and forms may need to be signed the design of the glazing needs to support this function. ~ The ability to lock down the Unit, e.g. in evenings when the pharmacy is closed, is required. This may be achieved by lockable doors from public corridors to the waiting area, however lockable shutters to the counter may be considered. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | Translation and QA Only | 6 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1 staff | The Distribution Workstation provides workspace to sort and process dispensed medications to be distributed from the Pharmacy to clinical units (e.g. imprest medications) and may be used to prepare specialised packs (e.g. resuscitation trolley supplies). | ~ Ready access to bulk store and refrigerated storage is required from this area. ~ Direct access to a dispatch/collection area is required for holding items prior to delivery. ~ Printer and telephone facilities to be shared between multiple workstations. A Multifunction device is to be in close proximity to the distribution area. ~ Ensure adequate lighting over workspace. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | Translation and QA Only | 4 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1 staff | The Dispensing Workstation provides workspace to prepare, assemble and label patient medications for dispensing to inpatients and outpatients. The workstations can be configured to provide dispensing/assembly stations and a checking station as required. | ~ Dispensing workstations should be arranged to support effective workflows, reduce travel time and avoid error. These stations should be arranged such that extended reaches are avoided. Where dispensing workstations are arranged adjacent to each other, corridors in between them should be wide enough to provide unobstructed movement for staff and trolleys. ~ Ready access to the bulk store and refrigerated storage is required. ~ Printer and telephone facilities to be shared between multiple workstations. A Multifunction device is to be in close proximity to the dispensing area. ~ Ensure adequate lighting over workspace - task lighting may be required. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | Translation and QA Only | 12 | 2700 | PREP | 4 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1-2 staff | The Preparation Room provides a dedicated area for the extemporaneous preparation and compounding of non-aseptically prepared products and cleaning of equipment as required. The Preparation Room should be located in close proximity to the dispensing area. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | Translation and QA Only | 6 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1 staff | The Returns Workstation provides workspace to sort and process medication returns from within the hospital that are to be returned to stock or sent for disposal. | ~ Storage is required to accommodate the returns before they are processed. ~ Ready access to refrigerated storage and disposal room is required from this area. ~ Printer and telephone facilities to be shared between multiple workstations. A Multifunction device is to be in close proximity to the returns area. ~ Ensure adequate lighting over workspace. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PLAY | Play Area - Paediatric | Public Areas | Translation and QA Only | 10 | 2700 | PLAP-10 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 children intermittently;; | The Play Area - Paediatric is typically associated with a waiting area and provides the space and amenities for children to play while waiting with their parents / carers prior to attending an appointment and/or receiving clinical care in a department. | ~ The Play Area should allow access for prams and be located in close proximity to public amenities, including baby change facilities. ~ Provision of age appropriate furnishing, artwork and play equipment (if provided) to be based on service and population. Furniture that is easily wiped clean is recommended. ~ Furniture suitable for adults is typically provided within the space to support supervision of children but may be provided in the adjacent waiting area if layout allows for adequate visibility. ~ The Play Area should be designed to minimise noise transfer to other areas. ~ Provision of interactive board/projector technologies and associated services may be considered depending on operational policies and ICT support. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PLNT-WT | Plant - Water Treatment | Renal Dialysis | Translation and QA Only | 18 | 2700 | WTPL | 4 | 07.04.2026 |  | 24 hours | 1-2 staff | The Plant - Water Treatment is a lockable room for water treatment systems, including particle filters, water softeners, carbon filters and reverse osmosis (RO) water plant/systems, for the provision of safe water for patients receiving haemodialysis therapy. | ~ The Water Treatment Plant Room should be located in close proximity to the Renal Dialysis Unit to permit short tubing runs to each Treatment Bay, and permit staff to monitor and service the water treatment systems. ~ Refer to manufacturer's specifications for details of RO water treatment plant equipment. In particular, this equipment will incorporate a heat disinfection function, and water saving features. The final components of the system will be determined by the quality of feed water and the ability of the overall system to produce and maintain appropriate water quality. Water treatment requirements to be confirmed by a dialysis water treatment specialist. ~ High level sound isolation is required to ensure noise generated from this room does not invade treatment spaces. ~ Structural engineer's assessment must be sought for floor load bearing capacity with respect to water treatment and pre-treatment plant equipment. ~ Ventilation, exhaust and/or air-conditioning must be designed to accommodate the heat loads of the specified equipment. ~ Light is to be minimised; there are to be no windows provided. ~ Service access will be required around the perimeter of plant equipment, clearances will be determined by manufacturer's specifications. ~ A second door may be provided for separate deliveries and maintenance access if located in the patient treatment area. ~ Pipework and components installed after the water inlet in this room shall not contain brass or copper. ~ Options for cooling of high temperature (circa 90°C) waste water discharged from RO plant is to be considered. ~ Where chilled water is not available, a chiller may be required outside the plant room. The maximum temperature of the feed water to be assessed to allow determination of any requirement for a heat exchanger or chiller design as determined by expert. The intent of this is ensure the temperature at the dialysis point for patient care is between 30-37°C. ~ Redundancy within the pre-treatment and treatment devices/filters should be considered based on the hospitals service criticality level, the feed water quality or risk around quality, and the hospital location where supply of replacement equipment is difficult. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PLST | Plaster Room | Ambulatory Care | Translation and QA Only | 18 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient; 1 visitor; up to 4 staff | The Plaster Room allows for the application of plaster or other splints and for the closed reduction of displaced fractures or dislocations under sedative or regional anaesthesia. | ~ Typically provided as a dedicated room for high volume services, otherwise, a generic Treatment Room may be used with the inclusion of a plaster trap and other specific plastering equipment. ~ The cast saw shall incorporate an integrated dust extraction system or the room shall have an independent dust extraction system suitably located to capture the dust at source. A room exhaust shall also be included to prevent dust from entering adjacent spaces. ~ The plaster trap shall be easily accessible for cleaning and maintenance. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PROC | Procedure Room | Ambulatory Care | Translation and QA Only | 20 | 3000 | PROC-20 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; up to 4 staff | The Procedure Room provides a controlled environment and facilities for carrying out procedures that do not require the full facilities of the Operating Suite. This may include suturing of wounds, complex dressings, lumbar puncture, catheterisations. administration of local anaesthesia and use of medical gases in connection with the procedures being performed. General anaesthesia will not be administered in this room. | ~ Lead shielding may be required depending on use of mobile imaging equipment. Treatment of bariatric patients including mobile, bariatric lifter access. ~ The ceiling height has been nominally shown at 3000mm, however 2700mm is also acceptable and the height is to be determined based on ceiling mounted equipment and operational requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | Full AHIA Review | 12 | 2700 | PBTR-A | 8 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-acute-treatment/?fullscreen=true&utm_source=project-link&rev=8 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Acute Treatment provides the space, equipment and services for assessment, treatment and observation of patients with acute conditions and injuries within the Emergency Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station/write-up area is required for patient observation. ~ The patient bay may be configured with side walls. Inclusion, height and extent of side walls is to be determined at project level to suit the overall department layout and requirements for patient observation. For the requirements of an enclosed bay please refer to Patient Bay – Emergency, Acute Treatment, Enclosed (PTB-E-ACU-E). ~ A handwash basin is to be provided for every 4-6 patient bays. Quantity and location of handwashing basins in relation to the patient bay will be subject to the overall department layout and informed by ensuring reasonable travel distances and ease of access from each patient bay. Close access to dedicated PPE bays shared between patient bays is also required separate to bays for handwashing basins. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency Unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Input of electronic medical records (EMR) may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between multiple bays, with the quantity of WOWs to be rationalised across the unit to suit clinical services requirements and staffing models. Ensure circulation space is sufficient for bedside and bed-end data entry. Parking areas for WOWs and facilities for battery/equipment charging are required to support this model. Alternative configurations, such as provision of wall mounted computers (either within individual bays or as shared write up spaces between bays) may be provided depending on clinical services requirements and local ICT policies. ~ The patient monitor may be mounted on the patient’s left or the patient’s right. The location of the patient monitor is to be determined at project level to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the bracket for the patient monitor. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, underbed storage baskets, etc. for clothes and small bags) is to be considered at project level to ensure an appropriate solution is provided for patient and visitor comfort and convenience. ~ It is recommended that a dedicated power outlet, clearly separate from the medical services panel (MSP), is provided to support patient and visitor use for charging portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ In some spaces, such as patient bays, a level of speech privacy of “confidential” would be recommended to protect sensitive patient information. However, due to clinical services requirements for patient care and observation, these spaces cannot be fully enclosed and therefore cannot achieve this level of speech privacy. The speech privacy rating of “not private” has been noted in relation to the elements of the physical environment that can contribute to speech privacy, however, operational approaches to maintaining confidentiality during discussions with patients and support persons must be considered. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | Full AHIA Review | 15 | 2700 | PRTR-AS | 3 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-acute-treatment-enclosed/?fullscreen=true&utm_source=project-link&rev=3 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Acute Treatment, Enclosed provides an enclosed space, equipment and services for assessment, treatment and observation of patients with acute conditions and injuries within the Emergency Unit. | ~ This Standard Component shows the requirements for a general enclosed patient bay for acute emergency treatment. For the requirements of an open patient bay refer to Patient Bay - Emergency, Acute Treatment (PTB-E-ACU). ~ Where this Standard Component is used to inform design of a standard isolation space for acute emergency treatment an ensuite that is not shared with other patients may be required. ~ Where this Standard Component is used to inform design of a negative pressure isolation space for acute emergency treatment, an ensuite that is not shared with other patients may be required and an anteroom will be required. A negative pressure room will also have specific air handling and grille location requirements and these are to be confirmed at project level to align with local engineering services guidance. To support maintenance of negative pressure it is also recommended that the entry door swings outwards, and adequate circulation space will be required in the corridor to support this. ~ The extent of glazing provided to the room is to be determined at project level to suit the overall department layout and requirements for patient observation. Provision of integral blinds or extension of the privacy curtain track over the internal observation window is to be determined to suit requirements for observation and patient privacy. ~ Close access to dedicated PPE bays shared between patient bays is required. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Input of electronic medical records (EMR) may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between multiple bays, with the quantity of WOWs to be rationalised across the unit to suit clinical services requirements and staffing models. Ensure circulation space is sufficient for bedside and bed-end data entry. Parking areas for WOWs and facilities for battery/equipment charging are required to support this model. Alternative configurations, such as provision of wall mounted computers (either within individual bays or as shared write up spaces between bays) may be provided depending on clinical services requirements and local ICT policies. ~ The patient monitor may be mounted on the patient’s left or the patient’s right. The location of the patient monitor is to be determined at project level to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the bracket for the patient monitor. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, underbed storage baskets, etc. for clothes and small bags) is to be considered at project level to ensure an appropriate solution is provided for patient and visitor comfort and convenience. ~ It is recommended that a dedicated power outlet, clearly separate from the medical services panel (MSP), is provided to support patient and visitor use for charging portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Inclusion of a patient entertainment system may be considered depending on anticipated length of stay within the patient bay and patient cohort (e.g. paediatrics). Solutions may include individual systems provided to each enclosed patient bay (with integration to patient handset for speaker, and audio/content controls) or portable solutions, such as tablets, brought to patients as needed. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | Full AHIA Review | 6.5 | 2700 | PBAT | 3 | 31.03.2026 |  | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Ambulance Triage provides the space equipment and services for initial assessment and physical examination of patients that have arrived at the Emergency Unit via ambulance. | ~ Clear line of sight to the patient in the patient bay from the ambulance write-up is required for patient observation. Direct access from ambulance write-up, triage and the reception/administration area of the Emergency Unit is required. ~ A handwash basin is to be provided for every 4-6 patient bays. Quantity and location of handwashing basins in relation to the patient bay will be subject to the overall department layout and informed by ensuring reasonable travel distances and ease of access from each patient bay. Close access to dedicated PPE bays shared between patient bays is also required separate to bays for handwashing basins. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | Full AHIA Review | 6.5 | 2700 | PBTR-FT | 3 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-ambulatory-treatment/?fullscreen=true&utm_source=project-link&rev=3 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Ambulatory Treatment (also referred to as “Fast Track”) provides the space equipment and services for assessment, treatment and observation of ambulant patients with non-complex (e.g. single system) acute conditions and injuries requiring a short episode of care within the Emergency Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station/write-up area is required for patient observation. ~ A handwash basin is to be provided for every 4-6 patient bays. Quantity and location of handwashing basins in relation to the patient bay will be subject to the overall department layout and informed by ensuring reasonable travel distances and ease of access from each patient bay. Close access to dedicated PPE bays shared between patient bays is also required separate to bays for handwashing basins. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ The weight capacity of recliners selected must be considered to suit a wide range of patient requirements. The recliner must also have the ability to lay completely flat. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ It is recommended that a dedicated power outlet, clearly separate from the medical services panel (MSP), is provided to support patient and visitor use for charging portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ In some spaces, such as patient bays, a level of speech privacy of “confidential” would be recommended to protect sensitive patient information. However, due to clinical services requirements for patient care and observation, these spaces cannot be fully enclosed and therefore cannot achieve this level of speech privacy. The speech privacy rating of “not private” has been noted in relation to the elements of the physical environment that can contribute to speech privacy, however, operational approaches to maintaining confidentiality during discussions with patients and support persons must be considered. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | Full AHIA Review | 10 | 2700 | PBTR-NA | 7 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-non-acute-treatment/?fullscreen=true&utm_source=project-link&rev=7 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Non-Acute Treatment provides the space equipment and services for assessment, treatment and observation of patients with non-acute conditions and injuries that require a short episode of care (e.g. less than 24 hours) within the Emergency Unit / Emergency Short Stay Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station/write-up area is required for patient observation. ~ The patient bay may be configured with side walls. Inclusion, height and extent of side walls is to be determined at project level to suit the overall department layout and requirements for patient observation. ~ A handwash basin is to be provided for every 4-6 patient bays. Quantity and location of handwashing basins in relation to the patient bay will be subject to the overall department layout and informed by ensuring reasonable travel distances and ease of access from each patient bay. Close access to dedicated PPE bays shared between patient bays is also required separate to bays for handwashing basins. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Inclusion of a patient monitor is optional, and provision is dependent on clinical services requirements. If provided, the patient monitor may be mounted on the patient’s left or the patient’s right. The location of the patient monitor is to be determined at project level to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the bracket for the patient monitor. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project suit operational models and local ICT strategies and policies. Services (power, data and/or AV connection) are to be confirmed to suit selected system. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, underbed storage baskets, etc. for clothes and small bags) is to be considered at project level to ensure an appropriate solution is provided for patient and visitor comfort and convenience. ~ It is recommended that a dedicated power outlet, clearly separate from the medical services panel (MSP), is provided to support patient and visitor use for charging portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ In some spaces, such as patient bays, a level of speech privacy of “confidential” would be recommended to protect sensitive patient information. However, due to clinical services requirements for patient care and observation, these spaces cannot be fully enclosed and therefore cannot achieve this level of speech privacy. The speech privacy rating of “not private” has been noted in relation to the elements of the physical environment that can contribute to speech privacy, however, operational approaches to maintaining confidentiality during discussions with patients and support persons must be considered. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | Full AHIA Review | 25 | 3000 | PBTR-R | 8 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-resuscitation/?fullscreen=true&utm_source=project-link&rev=8 | 24 hours | 1 patient;; up to 8 staff | The Patient Bay - Emergency, Resuscitation provides the space, equipment and services for assessment, resuscitation, treatment and observation of patients with critical conditions and injuries within the Emergency Unit. | ~ The requirement for body protection or cardiac protection within the Patient Bay - Emergency, Resuscitation, in accordance with AS/NZS 3003, is to be confirmed at project level based on the medical procedures to be undertaken in the space and the level of protection against electric shock afforded in the medical electrical equipment available for these procedures. ~ Clear area is required to both sides of the patient bed to accommodate an ambulance trolley and the staff and equipment required to assist/complete patient transfers. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used should be confirmed at project level. Ceiling mounted patient lifting tracks may be considered based on local WHS policies. ~ Use of mobile imaging equipment within the resuscitation bay is to be confirmed at project level. Radiation shielding and signage requirements will need to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ Clinical requirements and models of care for paediatric and neonatal patients are to be confirmed at project level. One resuscitation bay may be assigned for use with paediatric and neonatal patients and hold the required equipment (e.g. appropriate resuscitation trolleys and warming equipment) and consumables. Alternatively, equipment and consumables for paediatric and neonatal patients may be stored in a central shared zone to be brought any resuscitation bay as required. ~ Clinical requirements and models of care for trauma services, and their resulting spatial requirements are to be confirmed at project level. ~ The content and configuration of the medical services pendant, including medical gases, power and data, will be dependent on clinical services requirements and medical equipment selection, and is to be confirmed at project level. A medical services panel may be provided in lieu of a medical services pendant, depending on models of care and subject to consultation and confirmation with Emergency Unit clinicians. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to the atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given nitrous oxide is used as a recreational drug. ~ Enclosing the Patient Bay - Emergency, Resuscitation may be considered at project level. Where a bay is enclosed, provision of sliding glazed doors that support observation is advised. ~ Where the Patient Bay - Emergency, Resuscitation is enclosed for use as a negative pressure isolation room, an anteroom and an ensuite will be required. A negative pressure room will also have specific air handling and grille location requirements, and these are to be confirmed at project level to suit local engineering services guidance. Provision of negative pressure isolation resuscitation rooms will be dependent on jurisdictional requirements, clinical services planning, service level and patient profile, and must be confirmed at project level. ~ Direct access from ambulance arrivals or a diagnostic imaging room to a Patient Bay - Emergency, Resuscitation may be provided depending on clinical services requirements and operational models. Provision of an additional point of entry to the resuscitation bay will require coordination with ceiling and wall mounted equipment. ~ Personal protective equipment (PPE) is to be in readily accessible locations between resuscitation bays. Refer to Part D: Infection Prevention and Control for more information. ~ Patient monitoring and display screen requirements (e.g. for viewing patient information, review of medical imaging from portable imaging equipment, use of a emergency decision support tool, etc.) are to be confirmed at project level to suit clinical services requirements and local ICT strategies and policies. ~ Provision of cameras for capturing treatment for use in education, streaming to education spaces and/or to enable remote assistance in small services will be dependent on clinical services requirements (including for virtual models of care) and local ICT strategies and policies. ~ Close access is required to linen bays and blanket warming cabinets. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical services requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | Full AHIA Review | 24.5 | 3000 | PBIC | 2 | 12.11.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff (with up to 6 additional staff as required) | The Patient Bay - Intensive Care provides an acuity adaptable, curtained bay for a patient requiring intensive medical treatment, nursing care and monitoring for potentially life threatening conditions. | ~ Visual access to the room from a Staff Station is required. ~ In planning of the overall department, room layouts should not be mirrored. Layout are to be "handed", with any specific items being "mirrored" to be confirmed at project level to suit clinical service requirements. ~ The dialysis machine, RO water machine, and the dialysis wall box and its associated large cooling water trap with sealed lid are optional. These items may not be provided in all services or to all bedrooms/bays within a service. Provision is dependent on the clinical service requirements in relation to the delivery of dialysis. The various dialysis therapies will have specific implications for plumbing and pipework in relation to flushing, maintenance and wastewater/effluent handling. See HPU 360 Intensive Care for more information. ~ Overall content and configuration of the medical services pendants is to be confirmed at project level, including type and quantity of medical gases, power and data. The final arrangement will be dependent on clinical service requirements and will vary depending on clinical needs and the selection of mobile vs pendant mounted equipment. Pendants may be provided as one pendant with two arms on a single mounting point, or as single arms on multiple mounting points to increase the reach around the bed space (e.g. when the bed is located as shown or rotated 90 degrees) to support clinical care. Tertiary facilities that act as ECMO retrieval centres or otherwise perform a significant number of ECMO procedures may consider including a pendant located at the foot of the bed to enhance delivery of this treatment by supporting femoral access and connection to the required medical equipment. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ Access to natural light and outlook is essential (with non-reflected light and views preferred). To balance this requirement with clinical requirements, the room should provide the ability to provide care with the bed in various orientations. This Standard Component shows the bed oriented vertically on the page with the head of the bed toward the window, supporting quick access by staff to either side from the entry to the room. The bed may be re-oriented to provide views to the window as a patient’s clinical state improves. The reach of the arms of the pendant should support provision of clinical care when the bed is turned 90 degrees. ~ Design to suit local cultural requirements to be considered at project level and supported by community consultation. For more information refer to ‘AusHFG Culturally Sensitive Planning and Design’ and local policies and guidance on culturally responsive design. ~ Requirements for staff notetaking/write-up within the room, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. Configurations such as a ceiling mounted arm at the foot of the bed with a computer and keyboard mounting bracket, or provision of a computer based on a fixed bench as an alternative to a workstation on wheels (WoW), may be considered and assessed at project level. Provision may be dependent on alignment with local ICT strategies, policies and workflows as well as cost impact. ~ Connection of the patient monitor to a central monitoring system is required. ~ Additional ICT requirements, particularly in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. ~ The configuration of the patient lifter track (i.e. linear track, H-track, pendant mounted, etc.), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) are to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Coordination of the lifter track with room lighting, pendants, examination light, patient entertainment system and any ceiling mounted services is to be carefully considered. ~ Patient entertainment systems may be mounted on the wall or ceiling. Configuration of the patient entertainment (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall or ceiling is required for mounting the patient entertainment system. ~ The ability for slave monitoring (i.e. mirror content from the pendant mounted patient monitor) to be provided through the screen for the patient entertainment system for added visibility of information in emergency situations is to be considered to suit project requirements. Where slave monitoring is not possible through patient entertainment system display screen, and is required to suit models of care, an additional slave display screen and associated services may be required. ~ A wall clock should be visible in all patient bays. Clocks can support orientation of patients to the time of day, helping to reduce confusion and delirium. However, it has been noted they may also cause distress (e.g. from a sense of time passing too slowly or losing chunks of time). Clock products with the ability to turn off/dim the display may be considered to flexibly respond to patient preferences/needs. The placement of the clock within the room and type of clock provided, including connections to a master clock system, is to be confirmed at a project level. ~ The use of switchable glass in lieu of integral blinds to observation windows may be considered at project level and inclusion would be based on an assessment of maintenance, product lifecycle and downtime requirements. For longevity of the product, switchable glass must be turned off (i.e. be opaque) for a period of time each day; this must be considered in relation to where this product is intended to be used to ensure the downtime requirement does not compromise patient observation. ~ Operational models, work health and safety requirements and IPC policies regarding the changing/laundering of privacy curtains is to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient spaces is to suit local security and WHS policies and operational service requirements. ~ Furniture to accommodate a carer within the room is to be confirmed at project level, including consideration of anticipated length of stay, operational models for provision of linen, provision of carer property storage, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use. Fixed joinery items may be considered to provide this function; however, freestanding furniture is recommended where flexibility is required. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ Lighting is to be designed support clinical observation of patients (e.g. accurate colour rendering, appropriate colour temperature, etc.) as per AS/NZS 1680. Consideration of lighting systems that are automated to support circadian rhythms (e.g. through intensity tuning, color tuning, etc.) may be considered at project level. ~ Positioning of light fixtures is to be coordinated with ceiling mounted equipment (e.g. pendant, examination light, patient lifter track, display screen, etc.) to ensure appropriate, uniform illumination of the patient for observation when needed. It is recommended to avoid direct of light fittings over the patient’s head (noting that the bed is movable and may be arranged in different configurations to meet clinical needs and equipment set-up). ~ A dedicated power outlet, clearly separate from outlets for clinical use, is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | Full AHIA Review | 16.5 | 3000 | NBIC-HD; NBICU | 5 | 03.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff (with up to 6 additional staff as required) | The Patient Bay - Neonatal, Intensive Care / High Dependency provides the space, services and facilities for the medical care of newborns that are premature, medically unstable and/or critically ill. The patient bay also provides amenities for family integrated care, including space and furniture that supports skin-to-skin contact (kangaroo care), breastfeeding/expressing breast milk, and rest for parents and family. | ~ A width of 1m around the humidicrib/care station is to be maintained clear of any fixed items to support access for staff and equipment in an emergency. ~ Requirements for receiving critically ill transferred newborns with NETS (Newborn & Paediatric Emergency Transport Service) are to be confirmed at project level. ~ Lighting within the patient bay and from adjacent corridor areas should be carefully considered and should be dimmable and adjustable to suit requirements at different times of day. Continuous bright light is detrimental and causes stress for newborns. Lighting should be zoned to allow separate control for lighting in the family area. Direct overhead lighting should be avoided. The use of cyclic lighting controls may be considered and are to be confirmed at project level. ~ Visual access to the room from a Staff Station is required. ~ In planning of the overall department, room layouts should not be mirrored. Layouts are to be "handed", with any specific items being "mirrored" to be confirmed at project level to suit clinical service requirements. ~ The patient bay may be configured with either half height walls or full height walls to the sides of the bay. Height of walls and provision of any glazing is to be determined at a project level to suit the overall department layout and requirements for patient observation. Location of wall mounted items and configuration of privacy curtains and tracks are to be confirmed to suit wall heights. Where half height walls are provided, curtains of a shorter length may be provided above to ensure visual privacy can be achieved as required. Curtains and curtain tracks are optional; units may choose to use portable screens in lieu of ceiling mounted privacy curtains. ~ Support for care of multiples (twins, triplets, quads) with a small number of bays configured without a separating wall may be considered when determining the overall layout of unit. ~ Alcohol-based hand rub (ABHR) may be provided in wall mounted dispensers or in a holder that can be attached to a trolley. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies and support use by family and visitors as required. ~ A Type A handwashing basin is to be located nearby and may be shared between 4-6 bays (subject to the unit layout and ease of access from each bay). Refer to Part D Section 4.1.2-5 for more information. ~ Per clinical services planning, enclosed bays may be provided. Where a patient bay is enclosed, a handwashing basin (Type A) and a glazed sliding door (minimum 1400 clear opening) is to be provided. Additional area will be required to accommodate the basin, the door circulation and any dedicated dirty linen and waste receptacles (depending on operational models). ~ For enclosed bays, the extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation. Provision of integral blinds or extension of the privacy curtain track over internal glazing is to be determined to suit requirements for observation, family privacy and infection prevention and control requirements (IPC). ~ For requirements for enclosing and adapting the patient bay for provision of an isolation room, e.g. provision of an anteroom, access to PPE, air handling and pressure, etc. refer to ‘AusHFG Part D: Infection Prevention and Control’ and ‘AusHFG Isolation Room- Engineering and Design Requirements’. ~ Medical services panel(s) may be provided instead of a pendant and requirements must be confirmed at project level to suit clinical services requirements and equipment selection. Where medical services panel is provided instead of pendant, ceiling height is to be 2700mm. Ceiling height of 3000mm is only required for pendant installation and arm clearances. ~ Life of components, and access for maintenance and replacement of pendants is to be considered during design. ~ Overall content and configuration of the medical services panels/pendants is to be confirmed at project level, including type and quantity of medical gases, power and data. The final arrangement will be dependent on clinical service requirements and will vary depending on clinical needs and the selection of mobile or pendant/rail/wall mounted equipment. ~ The frequency of use and storage of nitric oxide cylinders is to be confirmed at project level to clinical service requirements and operational models for medical gas cylinder storage. A medical gas outlet for scavenge or mobile scavenging equipment may be required where nitric oxide is to be used. ~ Provision of external windows for natural light and external outlook is desirable and may be provided to individual patient bays or shared by a group/pod of bays. Overall department layout will determine location of external windows. Ability to achieve blocking/blackout of light as needed to be assessed to support patient and family rest. Integral blinds to be provided to windows in neonatal special care patient areas to meet cleaning and infection prevention and control (IPC) requirements; refer to Part D Section 6.4 for more information. ~ Furniture to accommodate family within the room is to be confirmed at project level to ensure the selected items provide comfortable seating, support breastfeeding and expressing breast milk, enable skin-to-skin contact (kangaroo care) and can be used for sleeping. Operational models for provision of linen, the extent and configuration of property storage to be provided, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use must also be considered. Fixed joinery items may be considered; however, freestanding furniture is recommended to support flexible arrangements. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ Refer to HPU 390 Neonatal Care Unit for information on overnight stay rooms for family and rooming-in models that are separate from the patient bay. ~ Provision and storage of chairs for visitors that can be shared between bays and brought to a patient bay as needed to accommodate larger groups for short periods is to be considered. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support family and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Access to patient bays for mothers who are inpatients and may be brought in on a patient bed (when they are not able to be brought in a wheelchair) is to be considered. Visits and transportation from the inpatient unit are typically managed by the inpatient staff. The mother’s bed must be able to be located so that corridors to other patient bays are not blocked for staff and equipment. The location must also ensure access to the head of the mother’s bed can be achieved easily if their condition deteriorates. ~ Storage of breast milk/formula (fridge within neonatal cubicle or in central room) to be confirmed at project level to suit local jurisdictional and operational service requirements. Provision of fridges for storing breast milk/formula requires BMS monitoring. ~ Requirements for staff notetaking/write-up within the bay, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities within the unit, or provision of fixed wall mounted computers in each bay, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bay. Provision of wall mounted computers will require side walls to be raised to provide adequate structural support within the wall. ~ Additional ICT requirements (cameras, display screens, building services, etc.) for virtual care such as patient monitoring/assessment, staff support, family consultation etc. (e.g. in rural and remote facilities) are to be confirmed at project level to suit clinical service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ The configuration of the Nurse Call system, including provision of “quiet call” systems that aim to reduce noise by alerting staff on handheld devices, is to be assessed at project level to suit clinical services requirements and local ICT policies. ~ High noise levels are detrimental to newborn health. Ceiling and wall finishes are to be suitable for the cleaning required in clinical environments, with acoustic treatments that meet infection prevention and control requirements to be considered and assessed to reduce the impact of noise within the patient bay. ~ Projects are to confirm the types of medical procedures requiring equipment to be powered from an isolated supply within the patient bay to confirm the requirement for provision of a line isolation monitor within the bay. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | Full AHIA Review | 12.5 | 2700 | NBLD, NBSC | 5 | 03.12.2025 |  | 24 hours | 1 patient; 1-2 visitors; 1-2 staff (with up to 4 additional staff as required) | The Patient Bay - Neonatal, Special Care provides the space, services and facilities for the medical care of newborns that are premature and/or not sufficiently stable to be discharged. The patient bay also provides amenities for family integrated care, including space and furniture that supports skin-to-skin contact (kangaroo care), breastfeeding and expressing breast milk, and rest for parents and family. | ~ A width of 1m around the humidicrib/care station is to be maintained clear of any fixed items to support access for staff and equipment in an emergency. ~ The layout shown in this Standard Component assumes that NETS (Newborn and Paediatric Emergency Transport Service) retrievals of critically ill newborns would be undertaken in a separate dedicated space, not within the Special Care patient bay. ~ Lighting within the patient bay and from adjacent corridor areas should be carefully considered and should be dimmable and adjustable to suit requirements at different times of day. Continuous bright light is detrimental and causes stress for newborns. Lighting should be zoned to allow separate control for lighting in the family area. Direct overhead lighting should be avoided. The use of cyclic lighting controls may be considered and are to be confirmed at project level. ~ Visual access to the room from a Staff Station is required. ~ In planning of the overall department, room layouts should not be mirrored. Layouts are to be "handed", with any specific items being "mirrored" to be confirmed at project level to suit clinical service requirements. ~ The patient bay may be configured with either half height walls or full height walls to the sides of the bay. Height of walls and provision of any glazing is to be determined at a project level to suit the overall department layout and requirements for patient observation. Location of wall mounted items and configuration of privacy curtains and tracks are to be confirmed to suit wall heights. Where half height walls are provided, curtains of a shorter length may be provided above to ensure visual privacy can be achieved as required. Curtains and curtain tracks are optional; units may choose to use portable screens in lieu of ceiling mounted privacy curtains. ~ Support for care of multiples (twins, triplets, quads) with a small number of bays configured without a separating wall may be considered when determining the overall layout of unit. ~ Alcohol-based hand rub (ABHR) may be provided in wall mounted dispensers or in a holder that can be attached to a trolley. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies and support use by family and visitors as required. ~ A Type A handwashing basin is to be located nearby and may be shared between 4-6 bays (subject to the unit layout and ease of access from each bay). Refer to Part D Section 4.1.2-5 for more information. ~ Per clinical services planning, enclosed bays may be provided. Where a patient bay is enclosed, a handwashing basin (Type A) and a glazed sliding door (minimum 1400 clear opening) is to be provided. Additional area will be required to accommodate the basin, the door circulation and any dedicated dirty linen and waste receptacles (depending on operational models). ~ For enclosed bays, the extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation. Provision of integral blinds or extension of the privacy curtain track over internal glazing is to be determined to suit requirements for observation, family privacy and infection prevention and control requirements (IPC). ~ For requirements for enclosing and adapting the patient bay for provision of an isolation room, e.g. provision of an anteroom, access to PPE, air handling and pressure, etc. refer to ‘AusHFG Part D: Infection Prevention and Control’ and ‘AusHFG Isolation Room- Engineering and Design Requirements’. ~ Overall content and configuration of the medical services penal is to be confirmed at project level, including type and quantity of medical gases, power and data. The final arrangement will be dependent on clinical service requirements and will vary depending on clinical needs and the selection of mobile or rail/wall mounted equipment. ~ The frequency of use and storage of nitric oxide cylinders is to be confirmed at project level to clinical service requirements and operational models for medical gas cylinder storage. A medical gas outlet for scavenge or mobile scavenging equipment may be required where nitric oxide is to be used. ~ Provision of external windows for natural light and external outlook is desirable and may be provided to individual patient bays or shared by a group/pod of bays. Overall department layout will determine location of external windows. Ability to achieve blocking/blackout of light as needed to be assessed to support patient and family rest. Integral blinds to be provided to windows in neonatal special care patient areas to meet cleaning and infection prevention and control (IPC) requirements; refer to Part D Section 6.4 for more information. ~ Furniture to accommodate family within the room is to be confirmed at project level to ensure the selected items provide comfortable seating, support breastfeeding and expressing breast milk, enable skin-to-skin contact (kangaroo care) and can be used for sleeping. Operational models for provision of linen, the extent and configuration of property storage to be provided, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use must also be considered. Fixed joinery items may be considered; however, freestanding furniture is recommended to support flexible arrangements. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ Refer to HPU 390 Neonatal Care Unit for information on overnight stay rooms for family and rooming-in models that are separate from the patient bay. ~ Provision and storage of chairs for visitors that can be shared between bays and brought to a patient bay as needed to accommodate larger groups for short periods is to be considered. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support family and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Access to patient bays for mothers who are inpatients and may be brought in on a patient bed (when they are not able to be brought in a wheelchair) is to be considered. Visits and transportation from the inpatient unit are typically managed by the inpatient staff. The mother’s bed must be able to be located so that corridors to other patient bays are not blocked for staff and equipment. The location must also ensure access to the head of the mother’s bed can be achieved easily if their condition deteriorates. ~ Storage of breast milk/formula (fridge within neonatal cubicle or in central room) to be confirmed at project level to suit local jurisdictional and operational service requirements. Provision of fridges for storing breast milk/formula requires BMS monitoring. ~ Requirements for staff notetaking/write-up within the bay, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities within the unit, or provision of fixed wall mounted computers in each bay, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bay. Provision of wall mounted computers will require side walls to be raised to provide adequate structural support within the wall. ~ Additional ICT requirements (cameras, display screens, building services, etc.) for virtual care such as patient monitoring/assessment, staff support, family consultation etc. (e.g. in rural and remote facilities) are to be confirmed at project level to suit clinical service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ The configuration of the Nurse Call system, including provision of “quiet call” systems that aim to reduce noise by alerting staff on handheld devices, is to be assessed at project level to suit clinical services requirements and local ICT policies. ~ High noise levels are detrimental to newborn health. Ceiling and wall finishes are to be suitable for the cleaning required in clinical environments, with acoustic treatments that meet infection prevention and control requirements to be considered and assessed to reduce the impact of noise within the patient bay. ~ Projects are to confirm the types of medical procedures requiring equipment to be powered from an isolated supply within the patient bay to confirm the requirement for provision of a line isolation monitor within the bay. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | Translation and QA Only | 6.5 | 2700 | PBTR-H-6 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient; 1 visitor; 1-2 staff intermittently | A Patient Bay - Holding provides facilities for patient holding and preparation prior to examination, diagnostic imaging, treatment, procedures or surgery. | ~ A handwashing basin will be provided close by to be shared between multiple bays. ~ Staff observation is required and, where possible, a clear line of sight from a staff station is to be provided. Close access to a patient toilet is required. ~ The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring equipment. ~ The requirement for fixed wall mounted patient monitoring will be dependent on service requirements. A patient monitor may be located on the left or right side of bedhead depending on monitor functionality and staff workflows. Appropriate wall supports are required for mounting the bracket where a monitor is provided. ~ Where patient monitoring is provided, criticality of monitoring is to be assessed. Provision of emergency/standby power or UPS is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Facilities to accommodate bariatric patients within a select number of bays, including accommodating bariatric recliners, is to be considered to ensure sufficient amenity is provided. Provision will be dependent on service and patient cohort requirements. ~ Depending on service requirements, enclosed holding bays may be provided. Where a Patient Bay is to be enclosed, additional area is required to accommodate a dedicated handwashing basin and circulation at the door. Observation windows may be required and the extent of glazing to be provided is to suit requirements for staff supervision. ~ PPE may be consolidated between multiple bays. Provision of PPE and placement throughout the overall department will be dependent on local infection control policies. ~ A mobile sharps bin will be shared between multiple bays as required. Where use of sharps is frequent, a wall mounted bin sharps bin may be considered. ~ Electronic Medical Record (EMR) management may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays. Ensure circulation space is sufficient for bedside and bed end data entry. Parking for WOWs and facilities for battery charging are required to support this model of care. Alternative configurations, such as wall mounted monitors in bays, may be considered depending on local ICT policies. ~ Patient entertainment systems may be considered depending on anticipated length of stay within the holding bay and patient cohort requirements (e.g. paediatrics). Solutions may include individual systems provided to each bay (with integration to patient handset for audio and content control), a central display screen visible from multiple bays, or portable solutions, such as tablets, brought to patients as needed. ~ Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. ~ Depending on anticipated length of stay and pre-procedure requirements, local control of lighting within the bay may be provided to allow patients to dim/adjust lighting levels to increase comfort. ~ Access to natural light is required and an external outlook is recommended. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | Translation and QA Only | 9 | 2700 | PBTR-H-9 | 7 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient; 1 visitor; 1-2 staff intermittently | A Patient Bay - Holding provides facilities for patient holding and preparation prior to examination, diagnostic imaging, treatment, procedures or surgery. | ~ A handwashing basin will be provided close by to be shared between multiple bays. ~ Staff observation is required and, where possible, a clear line of sight from a staff station is to be provided. Close access to a patient toilet is required. ~ The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring equipment. ~ The requirement for fixed wall mounted patient monitoring will be dependent on service requirements. A patient monitor may be located on the left or right side of bedhead depending on monitor functionality and staff workflows. Appropriate wall supports are required for mounting the bracket where a monitor is provided. ~ Where patient monitoring is provided, criticality of monitoring is to be assessed. Provision of emergency/standby power or UPS is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Facilities to accommodate bariatric patients within a select number of bays, including accommodating bariatric beds, is to be considered to ensure sufficient amenity is provided. Provision will be dependent on service and patient cohort requirements. ~ Patient transfer aids such as mobile hoists, patient slides and hover mats are to be considered for assisted patient transfers to and from beds in holding bays. A ceiling mounted hoist may also be considered for patient transfers. Selection of transfer aids will be dependent on service and patient cohort requirements as well as WHS risk assessment. Appropriate ceiling support is required for the provision of a ceiling mounted hoist. ~ Depending on service requirements, enclosed holding bays may be provided. Where a Patient Bay is to be enclosed, additional area is required to accommodate a dedicated handwashing basin and circulation at the door. Observation windows may be required and the extent of glazing to be provided is to suit requirements for staff supervision. ~ PPE may be consolidated between multiple bays. Provision of PPE and placement throughout the overall department will be dependent on local infection control policies. ~ A mobile sharps bin will be shared between multiple bays as required. Where use of sharps is frequent, a wall mounted bin sharps bin may be considered. ~ Electronic Medical Record (EMR) management may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays. Ensure circulation space is sufficient for bedside and bed end data entry. Parking for WOWs and facilities for battery charging are required to support this model of care. Alternative configurations, such as wall mounted monitors in bays, may be considered depending on local ICT policies. ~ Patient entertainment systems may be considered depending on anticipated length of stay within the holding bay and patient cohort requirements (e.g. paediatrics). Solutions may include individual systems provided to each bay (with integration to patient handset for audio and content control), a central display screen visible from multiple bays, or portable solutions, such as tablets, brought to patients as needed. ~ Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. ~ Depending on anticipated length of stay and pre-procedure requirements, local control of lighting within the bay may be provided to allow patients to dim/adjust lighting level to increase comfort. ~ Access to natural light is required and an external outlook is recommended. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | Translation and QA Only | 9 | 2700 | PBTR-RS1 | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff intermittently (with up to 2 additional staff as required) | A Patient Bay - Recovery, Stage 1 provides facilities for the recovery of patients from anaesthetic post procedure, and is located within the Operating Unit or Day Procedures Unit. | ~ A handwashing basin will be provided close by to be shared between up to 4 Patient Bays. Staff observation is required and a clear line of sight from a staff station should be provided. ~ The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring and diagnostic equipment. ~ A patient monitor may be located on the left or right side of bedhead depending on monitor functionality and staff workflows. Appropriate wall supports are required for mounting the bracket where a monitor is provided. ~ Provision of emergency/standby power or UPS for patient monitoring is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Facilities to accommodate bariatric patients within a select number of bays, including accommodating bariatric beds, is to be considered to ensure sufficient amenity is provided. Provision will be dependent on service and patient cohort requirements. ~ Patient transfer aids such as mobile hoists, patient slides and hover mats are to be considered for assisted patient transfers to and from beds in holding bays. A ceiling mounted hoist may also be considered for patient transfers. Selection of transfer aids will be dependent on service and patient cohort requirements as well as WHS risk assessment. Appropriate ceiling support is required for the provision of a ceiling mounted hoist. ~ Depending on service requirements, enclosed recovery bays may be provided. Where a Patient Bay is to be enclosed, additional area is required to accommodate a dedicated handwashing basin and circulation at the door. Observation windows may be required and the extent of glazing to be provided is to suit requirements for staff supervision. ~ Additional area may be required in a percentage of Recovery Stage 1 bays to suit various services requirements, e.g. to support maternity patients or paediatric patients, for accommodating bariatric patients, for care of complex patients, or for extended recovery models. The percentage of bays that may be provided with increased area will be dependent on the anticipated case mix. ~ Electronic Medical Record (EMR) management may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays. Ensure circulation space is sufficient for bedside and bed end data entry. Parking for WOWs and facilities for battery charging required to support this model of data entry. Alternative configurations, such as wall mounted monitors in bays, may be considered depending on local ICT policies. ~ Access to natural light is required. Where windows are provided, integral blinds are required for infection prevention and control. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
PTRY | Pantry | Logistics / Support Services | Translation and QA Only | 9 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Pantry is for staff preparing and/or heating refreshments and snacks for patients, washing utensils and crockery or temporarily storing dirty items for collection, storing food and drink and disposing of food waste. This room may be shared between multiple units depending on service requirements. | ~ If food re-thermalisation trolleys are to be located in this room during meal times an additional 2m2 per trolley will be required as well as appropriate power outlets. Refer to Bay - Meal Trolley (BMT) for requirements. ~ Local food preparation regulations and infection control policies may require a Type B hand wash basin, separate to the sink, to be included in the room or may allow for it to be located nearby. ~ Fridge dimensions will vary depending on selection and service requirements; clear area provided for the fridge is to allow for adequate ventilation and full opening of door. Where double door fridges are provided, additional area will be required. ~ If an instantaneous boiling water tap/unit is provided, access should be restricted to the water unit e.g. within a cupboard. If system is located within a joinery unit, ensure appropriate ventilation is provided. ~ Provision and type of ice machine will be dependent on service requirements and local infection prevention and control policies. Where ice machine is provided, ensure adequate support to bench for weight of appliance. ~ Where tea service is provided the height of the hot water dispenser is to be considered to ensure large kettles can be filled easily. ~ Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling streams indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal and anticipated traffic, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. ~ Storage of nutritional supplements may require a lockable cupboard and will be dependent on service requirements. ~ Temperature of fridge may need to be monitored. A data outlet, or alternative connection to suit project/equipment requirements, may be required for connection the Building Management System (BMS) depending on service requirements. ~ Controlled, staff-only access may be required if this room is provided in a public or patient care area. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
RECP-10 | Reception, 10m2 | Public Areas | Translation and QA Only | 10 | 2700 | RECL-10 | 6 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 staff seated | The Reception, 10m2 provides the area and amenities for three staff members to receive and check-in patients / visitors to a unit and direct them to their destination or to an adjacent waiting area. The Reception may also act as an administrative base of the unit, including organising bookings for appointments and directing phone calls to other staff, as well as controlling access. Depending on the function of unit, the Reception may also take payments. | ~ Dependent on location, security glazing or shutters may be required. ~ A recessed area for front access by wheelchair users is typically required. Depending on check in requirements at Reception, a set down area for visual access only may be sufficient. ~ Provision of a hearing augmentation system may be required, particularly where security glazing if provided, and requirements are to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Adjustable height workstations may be provided in line with WHS policies and access for disabled staff working within the Reception area is to be considered. ~ CCTV monitor, intercom and door release buttons linked to entry points may be required for access control depending on location. ~ A desktop printer and labels printer may be provided as required. Printing, scanning and photocopying facilities may be consolidated with ready access from Reception to suit service requirements. ~ Swipe card access to reception may be provided to suit security requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
RECP-15 | Reception, 15m2 | Public Areas | Translation and QA Only | 15 | 2700 | RECL-15 | 6 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 2 staff seated | The Reception, 15m2 provides the area and amenities for three staff members to receive and check-in patients / visitors to a unit and direct them to their destination or to an adjacent waiting area. The Reception may also act as an administrative base of the unit, including organising bookings for appointments and directing phone calls to other staff, as well as controlling access. Depending on the function of unit, the Reception may also take payments. | ~ Dependent on location, security glazing or shutters may be required. ~ A recessed area for front access by wheelchair users is typically required. Depending on check in requirements at Reception, a set down area for visual access only may be sufficient. ~ Provision of a hearing augmentation system may be required, particularly where security glazing if provided, and requirements are to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Adjustable height workstations may be provided in line with WHS policies and access for disabled staff working within the Reception area is to be considered. ~ CCTV monitor, intercom and door release buttons linked to entry points may be required for access control depending on location. ~ A desktop printer and labels printer may be provided as required. Printing, scanning and photocopying facilities may be consolidated with ready access from Reception to suit service requirements. ~ Swipe card access to reception may be provided to suit security requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
RECP-20 | Reception, 20m2 | Public Areas | Translation and QA Only | 20 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 3 staff seated | The Reception, 20m2 provides the area and amenities for three staff members to receive and check-in patients / visitors to a unit and direct them to their destination or to an adjacent waiting area. The Reception may also act as an administrative base of the unit, including organising bookings for appointments and directing phone calls to other staff, as well as controlling access. Depending on the function of unit, the Reception may also take payments. | ~ Dependent on location, security glazing or shutters may be required. ~ A recessed area for front access by wheelchair users is typically required. Depending on check in requirements at Reception, a set down area for visual access only may be sufficient. ~ Provision of a hearing augmentation system may be required, particularly where security glazing if provided, and requirements are to be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Adjustable height workstations may be provided in line with WHS policies and access for disabled staff working within the Reception area is to be considered. ~ CCTV monitor, intercom and door release buttons linked to entry points may be required for access control depending on location. ~ A desktop printer and labels printer may be provided as required. Printing, scanning and photocopying facilities may be consolidated with ready access from Reception to suit service requirements. ~ Swipe card access to reception may be provided to suit security requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
RECP-E | Reception - Emergency | Emergency | Full AHIA Review | 20 | 2700 | REC-E | 8 | 31.03.2026 |  | 24 hours | 4 staff seated (with up to 2 additional staff intermittently) | The Reception - Emergency provides the space, equipment and services for receiving patients and visitors and directing them to their destination or to the waiting area of the Emergency Unit. The Reception - Emergency also acts as an administrative base for the unit. | ~ Triage - Emergency, Assessment Counters (TRIAGE-CO) and/or Triage - Emergency, Assessment Rooms (TRIAGE-RM) are to be in close proximity to the Reception - Emergency. ~ Multiple Triage - Emergency, Assessment Counters may be combined with the Reception - Emergency. When these Standard Components are combined, the final overall room configuration should include an egress that takes staff behind the secure line of the Emergency Unit. ~ Clear line of sight to the waiting room is recommended for observation. ~ Provision of a window for visual access from Reception - Emergency to a Triage Room/Counter (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. This window may be fixed or an operable sliding type (e.g. to allow passing of items/documents). ~ Provision of a window for visual access to the ambulance entry area (if collocated) may be considered to support efficient registration of patients arriving by ambulance. ~ While oversight of the patient/visitor entry, ambulance entry and waiting room is desirable, it is not always possible and security cameras and feeds are typically required. Display screens for security CCTV feeds should be located so they are not viewable by the public. Size and quantity of screens is to be determined to suit security requirements. ~ An intercom and door release buttons linked to the external entry doors and main department entry point(s) may be required for access control depending on service requirements. Lockdown alarms and buttons will also be required to suit security protocols and operational models for unit lock down. ~ This Standard Component shows 2 x counters where patients/visitors are standing and 1 x wheelchair accessible counter. Counters may be provided as standing height or seated height, or a mix of both, with at least one counter to provide wheelchair access as per AS1428.1 / NZS 4121. ~ Configuration of the security glazing (size of communication slot, size of pass-through aperture for paperwork, etc.) is to be determined at project level to suit operational models. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) and associated items (microphones, signage, etc.) is to be confirmed at project level, in consultation with accessibility experts, to suit the configuration of the counter and security glazing. ~ Acoustic treatment requirements are to be determined suit patient privacy requirements and reduce potential noise transfer to/from the adjacent waiting area. ~ Provision of height adjustable workstations in lieu of fixed joinery benches may be considered at project level and provision should be in line with local WHS policies. Where height adjustable workstations are provided the location of services and the interaction of the moving workstation surface with the static public facing counter must be carefully considered. ~ The final location of doors is to be determined to suit overall department layout and minimise risk of staff entrapment. At least one door must provide an egress that takes staff behind the secure line of the Emergency Department. The other door may provide direct access to the waiting room. Provision of access control devices (e.g. proximity card readers) is to be finalised to suit security requirements. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for stationery and consumables will be dependent on service requirements, operational models and ICT policies and strategies. This includes considering the facility’s use of electronic medical records (EMR) as well as the need to store any remaining paper forms. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
REPR | Reporting Room | Medical Imaging | Full AHIA Review | 12 | 2700 |  | 2 | 15.05.2025 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 staff | The Reporting Room provides two workspaces with high-performance computers for reviewing of and reporting on patient images from various medical imaging modalities. | ~ The size, quantity and configuration of computer display screens is to be finalised based on reviewing and reporting task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. ~ Display screens shown on desk mounted brackets may be wall mounted. Ensure appropriate in-wall support is provided where display screens are to be wall mounted. Where monitors are wall mounted, interaction with height adjustable desks and distances to services connections must be considered. Flexible monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Emerging technology, and its implications for the space, are to be considered. This may include investigating potential hardware, software and process changes that may, for example, result in the inclusion of additional display screens or CPUs, and the ergonomic, services and construction requirements for accommodating these changes in the future (e.g. supports in the wall for mounting, provision for installing additional services, etc.). ~ A large PACS display screen may be provided to be shared between the two workstations for collaborative image reviewing by teams. Screen sharing capabilities from each workstation would be required to support this. Where this is provided, the room occupancy could be up to 8 staff for limited periods. ~ Type and number of data connections for display screens to be confirmed to suit service and equipment requirements (cat-6 data, HDMI, etc.). ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ It is recommended by RANZCR that the light level of the room is able to be lowered to 20-40 lux. The combination of dimmable general room lighting, dimmable indirect lighting (wall and/or ceiling fixtures), and the use of FF&E items such as back lit monitors and keyboards, as well as any light from external sources (e.g. from corridor through glazing), is to be assessed to ensure the overall quality of light in the room is appropriate. Removal of any potential sources of glare on the computer screens is required to ensure it meets requirements for the performance of reviewing and reporting tasks. Each workstation is to have, to the extent possible, independent control for lighting effecting that workstation. ~ Acoustic wall panels and screens shown are indicative and the acoustic treatment of the room is to be designed to mitigate noise transfer between workstations and from adjacent areas. ~ The heat generated by computer equipment is to be considered when determining the air-conditioning requirements for this room. ~ Depending on the location of the Reporting Room, access control (e.g. via proximity card reader) may be provided to ensure staff only access and inclusion of a fixed duress button that is accessible from both workstations may be required to support staff safety. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for shielding to this room will be determined by the arrangement of the overall department floor plan and proximity of the Reporting Room to any imaging modalities. Radiation shielding requirements are to be assessed and advised by a qualified Radiation Consultant. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
REPW | Reporting Workstation | Medical Imaging | Full AHIA Review | 6 | 2700 |  | 2 | 15.05.2025 |  | Available 24 hours | 1-2 staff | The Reporting Workstation is a single workspace with a high-performance computer for reviewing of and reporting on patient images from various medical imaging modalities. | ~ This Standard Component is provided as a module that would be multiplied in an open plan arrangement. The number of workstations will be determined at a project level to suit service requirements and staffing profile. Shared elements that are not provided at each workstation, e.g. fixed duress in central location, nurse call annunciators, storage, etc. must be considered when modules are combined. ~ Depending on the overall layout when workstation modules are combined, services may be wall mounted for each individual workstation or soft-wired cable trays may be provided and connected to a central point where power and data are wall mounted or delivered via an umbilical/pole from the ceiling or floor. ~ The size, quantity and configuration of computer display screens is to be finalised based on reviewing and reporting task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. ~ Display screens shown on desk mounted brackets may be wall mounted. Ensure appropriate in-wall support is provided where display screens are to be wall mounted. Where monitors are wall mounted, interaction with height adjustable desks and distances to services connections must be considered. Flexible monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Emerging technology, and its implications for the space, are to be considered. This may include investigating potential hardware, software and process changes that may, for example, result in the inclusion of additional display screens or CPUs, and the ergonomic, services and construction requirements for accommodating these changes in the future (e.g. supports in the wall for mounting, provision for installing additional services, etc.). ~ A large PACS display screen may be provided to be shared between multiple workstations for collaborative image reviewing by teams. Screen sharing capabilities from each workstation would be required to support this. ~ Type and number of data connections for display screens to be confirmed to suit service and equipment requirements (cat-6 data, HDMI, etc.). ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ A modesty panel or an extended acoustic panel to the back of the workstation may be required depending on the layout developed for multiple workstations. ~ It is recommended by RANZCR that the light level of the room is able to be lowered to 20-40 lux. The combination of dimmable general room lighting, dimmable indirect lighting (wall and/or ceiling fixtures), and the use of FF&E items such as back lit monitors and keyboards, as well as any light from external sources (e.g. from corridor through glazing), is to be assessed to ensure the overall quality of light in the room is appropriate. Removal of any potential sources of glare on the computer screens is required to ensure it meets requirements for the performance of reviewing and reporting tasks. Each workstation is to have, to the extent possible, independent control for lighting effecting that workstation. ~ Acoustic wall panels and screens shown are indicative and acoustic treatment of the overall room with multiple workstations is to be considered as a whole when designing to mitigate noise transfer between workstations and from adjacent areas. ~ The heat generated by computer equipment is to be considered when determining the air-conditioning requirements for this room. ~ Storage spaces for staff property and stationery may be allocated separately to be shared between multiple workstations. ~ An annunciator for nurse calls may be located to be shared between multiple workstations depending on overall service requirements. ~ Depending on the location of the room containing Reporting Workstations, access control (e.g. via proximity card reader) may be provided to ensure staff only access and the inclusion of a fixed duress button that is accessible in a central location to all workstations may be required to support staff safety. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for shielding to this room will be determined by the arrangement of the overall department floor plan and proximity of the Reporting Room to imaging modalities. Radiation shielding requirements are to be assessed and advised by a qualified Radiation Consultant. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
SECL | Seclusion Room | Mental Health | Full AHIA Review | 14 | 3300 |  | 7 | 31.03.2026 |  | 24 hours | 1 patient as required;; 1-2 staff as required | A Seclusion Room provides a safe space for the sole confinement of a distressed or agitated person requiring separation for short periods at any hour of the day or night on an involuntary basis. | ~ The design of the Seclusion room should take into account future flexibility for conversion to another function (e.g. de-escalation room, sensory room, etc.) when services are able to phase out the practice of seclusion through changes in models of care. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment. Jurisdictional policies may require an increase in the thickness of the glass for a Seclusion Room. ~ Provision of a clear zone outside the seclusion room is required for safe access by the patient and staff, for continuous staff observation, and to support consumer privacy and dignity. An observation window is required with height to suit observation from a seated position. Placement and size of the window is to be confirmed to maximise visibility to all areas of the room. A secondary observation window on an adjacent wall may be provided for improved visibility dependent on layout. ~ An outward opening, single leaf (min 1200mm clear opening) solid door is to be provided. The door and door frame are to be robust and designed with no sharp edges and no element of the door hinges is to protrude into the Seclusion Room. The design must ensure that the consumer cannot open it or use any element of it for self-harm. The doors must be fitted with robust door hinges, door support structure and electric strike security. It is recommended that multi-point locking bolts are to be provided to both the hinge and latch sides of the door to secure the door leaf at the top, middle and bottom (or provision of an equivalent robust locking mechanism). Lock requirements are to be confirmed at project level to suit local jurisdictional policies and operational service requirements. ~ It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. ~ No potential ligature points or sharp edges are permitted to any corners, doors, door frames, and window frames (external and internal) within this room. All fittings should be flush/recessed. ~ Robustness of construction/finishes to be suitable for high impact. Floor, wall and ceiling construction must meet all relevant standards and jurisdictional policies. ~ A clock must be located within the area outside the seclusion room and be visible from within the seclusion room (i.e. through the observation window or door vision panel). ~ Direct/close access to a toilet/ensuite may be required to suit jurisdictional policies. Design of the door to the ensuite (e.g. hinged, sliding, etc.), access control and observation requirements are to be confirmed to inform inclusion of ensuite. Where direct access to a toilet/ensuite is provided from within the seclusion room, observation windows and an additional door for staff access may be required from the corridor. ~ Direct/close access to an outdoor space may be considered to support future flexibility for use of this room as a de-escalation space. ~ An external outlook is desirable. Access to natural light is required. Controls for integral blinds to external windows to be located in the staff observation area. ~ Provision of an observation camera within the seclusion room, with video feed displayed to the staff member in the observation area outside of the room, may be considered subject to jurisdictional policies. ~ Acoustic separation and treatment to be considered carefully to minimise disruption to other consumers, along with physical distance from communal (lounge and dining) and sleeping areas. ~ Room lighting must be dimmable and/or have controlled switching to allow for the provision of a low stimulus environment. Provision of lighting to provide sensory input as per therapeutic care plans may be considered based on service requirements and operational models. ~ Ceiling recessed speakers have been shown as optional depending on service requirements. Speaker connection requirements are to be confirmed if included. Music input is to be controlled from a device/control panel in the staff observation area. Inclusion of controls within the seclusion room to support self-regulation by consumers is subject to jurisdictional policies and models of care. ~ The ability for a patient and staff to communicate is required. Where this is not possible through the door, a two-way intercom within the seclusion room may be considered subject to jurisdictional policies. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ Air-conditioning vents/grilles are to be flush, and of the type manufactured and marketed as tamper proof and anti-ligature. Local temperature control to the staff observation area may to be considered. ~ Leakage protection devices (LPDs) such as residual current devices (RCDs) that cover the electrical services within this Standard Component are assumed to be provided in a central area within the unit (e.g. at a staff station). Location is to be confirmed at project level. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE
SECR | Security Observation Room | Logistics / Support Services | Translation and QA Only | 12 | 2700 | SECR-10 | 4 | 07.04.2026 |  | 24 hours | 1-2 staff | The Security Observation Room is a lockable room for security personnel to observe nearby areas and monitor surveillance equipment. Security staff in will be responsible maintaining order and de-escalating developing situations where aggression may become an issue. Staff identification and access control cards may be produced by security staff in this room. Security staff may also receive, receipt and record lost items of value, contraband and weapons, including reporting to police services in line with jurisdictional policies and procedures. | ~ This room may be provided as a satellite room separate to the main Security Department (e.g., in the Emergency Unit) or as a reception area for the Security Department. Security Observation Rooms are typically located close to the main entrance, after hours entrances and/or overseeing the emergency unit waiting area. ~ ICT requirements, including computer, camera and printer may be required for creating identification and access control cards for staff as well as passes for contractors and visitors, depending on facility requirements. Requirements for photography for identification card are to be confirmed based operational policies. Where provided, a camera will need to be located near a computer with unobstructed view through an observation window towards a blank wall in an area with adequate lighting. ~ Lockdown buttons to entry ways may be provided within the room dependent on service requirements and will be determined based on overall security strategy for the facility. ~ The provision and configuration of a weapons safe within the room will be depending on operational policies and jurisdictional requirements. ~ Clear signage indicating the function of the room is required. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SHAC | Shower - Accessible | Sanitary Facilities | Translation and QA Only | 4 | 2700 | SHD | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff assisting as required | The Shower - Accessible provides an enclosed, lockable room with an accessible shower, hand washing basin and changing area for use by patients, visitors or staff with disabilities (with or without assistance). | ~ The room layout and all fixtures, furniture and equipment (FF&E) are to comply with AS 1428.1 and NZ 4121. ~ Signage with tactile Braille nominating 'All Gender Accessible Shower' required to room. ~ If the Shower - Accessible is located in a patient care area for use by patients, the nurse call system should be included and emergency release door hardware should be installed to allow staff access in emergency situations. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system. ~ Facilities for hand hygiene and PPE to be available nearby if this room is for patient use. ~ If the Shower - Accessible is to be dedicated for use by staff, access control (e.g. a swipe card reader) may be required if this room is provided in a public area or patient care area. ~ The entrance to the room is to be flush with the adjoining floor for access in commode chairs/wheelchairs or with other assistive devices. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SHPT | Shower - Patient | Sanitary Facilities | Translation and QA Only | 4 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff assisting as required | The Shower - Patient provides an enclosed, lockable room with a shower, hand washing basin and changing area for use by patients (with or without assistance). | ~ Signage with tactile Braille nominating 'All Gender Patient Shower' required to room. ~ Emergency release door hardware should be installed to allow staff access in emergency situations. ~ The entrance to the room is to be flush with the adjoining floor for access in commode chairs/wheelchairs or with other assistive devices. ~ A shower curtain and track are noted as optional, and inclusion of the curtain and track, or track only (to support flexibility for future provision of curtains) is to be confirmed at project level to suit local work, health and safety (WHS), and IPC policies. Where curtains and tracks are provided, operational models for cleaning and maintenance must be considered. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ A power outlet to support grooming, such as shaving and drying hair, is shown as optional. Local policies around provision and maintenance of electrical outlets in wet areas are to be confirmed to inform inclusion of a power outlet within the ensuite. Where provided, the outlet is to be located to comply with Australian and New Zealand Standards regarding the minimum distance from any water sources (i.e. basin spout and shower). | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SHST | Shower - Staff | Sanitary Facilities | Translation and QA Only | 3 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 staff intermittently | The Shower - Staff provides an enclosed, lockable room with a shower and changing area for use by staff. | ~ Access control (e.g. a swipe card reader) may be required if this room is provided in a public area or patient care area. ~ The Shower - Staff may be allocated as gender specific or all gender. ~ A shower curtain and track are noted as optional, and inclusion of the curtain and track, or track only (to support flexibility for future provision of curtains) is to be confirmed at project level to suit local work, health and safety (WHS), and IPC policies. Where curtains and tracks are provided, operational models for cleaning and maintenance must be considered. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | Translation and QA Only | 50 | 3000 |  | 2 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | 1 patient;; up to 3 staff assisting | The SPECT-CT Imaging Room provides the area and facilities for Single Photon Emission Computed Tomography (SPECT) scanning procedures with an adjacent Control Room and Equipment Room. The SPECT-CT Imaging Room will be located with ready access to patient dosing areas. | ~ Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. ~ Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ The SPECT-CT Imaging Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints. Where shielding significantly increases the weight of the doors, automatic doors may be considered. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ Configuration of medical gases is to be confirmed to meet clinical requirements such as the provision of anaesthetic services. ~ Dimmable lights are recommended and are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort. ~ 'X-ray in Use' lights are required outside each entry door. ~ Room temperature and humidity control is required. Temperature requirements for equipment are to be confirmed by the vendor, including requirement for circulated cooling water. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the SPECT-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Some models of SPECT/CT require three phase power to be supplied. ~ Structural assessment is required to ensure the floor will be rigid with no vibration and will accommodate the weight of the SPECT-CT unit. ~ Consideration needs to be given to the clearances of equipment and replacement part delivery routes. ~ Where a service is may be performing minor interventional procedures, a Type A handwashing basin will be required instead of Type B. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | Translation and QA Only | 14 | 2700 |  | 2 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | up to 3 staff | The SPECT-CT Control room is located adjacent to the SPECT-CT Imaging Room, with direct visibility to the patient, for remote control of equipment with audio and visual contact with the patient via cameras, speakers and microphones. | ~ Each Imaging Room requires a Control Room. ~ Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. ~ Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the SPECT-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. Some models of SPECT/CT require three phase power to be supplied. ~ Cable management and the potential for computers to be consolidated into a rack (either within the room or in a dedicated, collocated air conditioned room/cupboard) to be determined at project level. ~ Provision of a height adjustable workstation may be considered depending on local policies and staff accessibility requirements. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SRM-15 | Staff Room, 15m2 | Staff Amenities | Translation and QA Only | 15 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 8 staff intermittently | The Staff Room is a shared facility for staff to use for respite, rest and relaxation during meal breaks, especially where it is difficult for staff to use common facilities particularly at night or due to distance. The room may also be used for small meetings or tutorials and for the storage of staff resources or library materials. Facilities for food and beverage preparation and storage should be provided. | ~ An external outlook is desirable. ~ Staff only access may be required if this room is provided in a public or patient care area. ~ A dishwasher may be provided depending on local operational polices. ~ A side approach to the sink for wheelchair access has been shown; front access may be required depending on local/jurisdictional policies and staff requirements. ~ The use of thermal heat detectors for fire detection is recommended. ~ A portable fire extinguisher and fire blanket must be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SRM-35 | Staff Room, 35m2 | Staff Amenities | Translation and QA Only | 35 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 24 staff intermittently | The Staff Room is a shared facility for staff to use for respite, rest and relaxation during meal breaks, especially where it is difficult for staff to use common facilities particularly at night or due to distance. The room may also be used for small meetings or tutorials and for the storage of staff resources or library materials. Facilities for food and beverage preparation and storage should be provided. | ~ An external outlook is desirable. ~ Staff only access may be required if this room is provided in a public or patient care area. ~ A dishwasher may be provided depending on local operational polices. ~ Front access to the sink for wheelchair access has been shown; a side approach may be acceptable depending on local/jurisdictional policies and staff requirements. ~ The use of thermal heat detectors for fire detection is recommended. ~ A portable fire extinguisher and fire blanket must be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 2 workstations;;; | The Staff Station is the operational and administrative base of a unit and enquiry point for patients and visitors. It provides for the co-ordination of patient care, patient observation, write-up of clinical notes, data entry and making/receiving telephone calls. The Staff Station may also accommodate a receptionist/ward clerk. | ~ The number of workspaces and area (m2) requirements will vary depending on the type of department, activity level, number of full and part-time staff, operational models and building layout. ~ One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Clinical Workroom. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations are provided). ~ A set down area may be provided for side access by visitors and patients in wheelchairs. If the Staff Station also serves a reception function, a recessed area for front access by wheelchair users may be required. ~ The room may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security as required in high risk areas. ~ Standing-height workstations may be provided. ~ A desktop printer and labels printer may be provided as required. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. ~ Additional monitors may be required for patient monitoring or security purposes depending on service requirements. ~ Placement and visibility of nurse annunciators in adjacent corridors needs to be considered and coordinated with other ceiling elements such as bulkheads. ~ Any rooms that are accessed from behind the staff station will require additional area for appropriate door circulation clearance. ~ Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | Translation and QA Only | 14 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 3 workstations;;; | The Staff Station is the operational and administrative base of a unit and enquiry point for patients and visitors. It provides for the co-ordination of patient care, patient observation, write-up of clinical notes, data entry and making/receiving telephone calls. The Staff Station may also accommodate a receptionist/ward clerk. | ~ The number of workspaces and area (m2) requirements will vary depending on the type of department, activity level, number of full and part-time staff, operational models and building layout. ~ One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Clinical Workroom. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations are provided). ~ A set down area may be provided for side access by visitors and patients in wheelchairs. If the Staff Station also serves a reception function, a recessed area for front access by wheelchair users may be required. ~ The room may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security as required in high risk areas. ~ Standing-height workstations may be provided. ~ A desktop printer and labels printer may be provided as required. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. ~ Additional monitors may be required for patient monitoring or security purposes depending on service requirements. ~ Placement and visibility of nurse annunciators in adjacent corridors needs to be considered and coordinated with other ceiling elements such as bulkheads. ~ Any rooms that are accessed from behind the staff station will require additional area for appropriate door circulation clearance. ~ Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | Translation and QA Only | 20 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 4 workstations;;; | The Staff Station is the operational and administrative base of a unit and enquiry point for patients and visitors. It provides for the co-ordination of patient care, patient observation, write-up of clinical notes, data entry and making/receiving telephone calls. The Staff Station may also accommodate a receptionist/ward clerk. | ~ The number of workspaces and area (m2) requirements will vary depending on the type of department, activity level, number of full and part-time staff, operational models and building layout. ~ One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Clinical Workroom. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication (e.g. if a Clinical Workroom and/or multiple Staff Stations are provided). ~ A set down area may be provided for side access by visitors and patients in wheelchairs. If the Staff Station also serves a reception function, a recessed area for front access by wheelchair users may be required. ~ The room may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security as required in high risk areas. ~ Standing-height workstations may be provided. ~ A desktop printer and labels printer may be provided as required. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. ~ Additional monitors may be required for patient monitoring or security purposes depending on service requirements. ~ Placement and visibility of nurse annunciators in adjacent corridors needs to be considered and coordinated with other ceiling elements such as bulkheads. ~ Any rooms that are accessed from behind the staff station will require additional area for appropriate door circulation clearance. ~ Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | Full AHIA Review | 14 | 2700 |  | 2 | 31.03.2026 |  | 24 hours | 3 staff (with up to 2 additional staff intermittently) | The Staff Station - Emergency, Control Hub provides the space, equipment and services for a central operational and administrative base of an Emergency Unit. It supports the coordination of patient care, patient flow, and ambulance arrivals as well as overseeing central monitoring, security feeds and the ambulance phone. Alternatively, depending on operational models, ICT strategies and policies, staffing profile, size and complexity of the service, etc., these functions may be distributed/duplicated across the Emergency Unit. | ~ This Standard Component indicates 3 x workstations (providing a base workstation for 1 x doctor-in-charge, 1 x nurse-in-charge and 1 x clerk), with an additional workstation area for central monitoring. The number of workstations required will vary depending on operational models, staffing models and the size and complexity of the service. ~ One computer workstation has been shown as a downtime workstation with provision of UPS power. Requirements for and location of downtime facilities will need to be confirmed to meet clinical services requirements, operational models for downtime, and local ICT policies. Provision of downtime computers will need to be rationalised across the unit to avoid unnecessary duplication. ~ The Staff Station - Emergency, Control Hub may be enclosed (e.g. with security glazing and lockable doors) or other physical design/planning solutions may be considered (e.g. increased counter depth, egress to secure area) for staff safety and security. Requirements are to be determined at project level based on a risk assessment. If provided, security glazing configuration (inclusion/size of communication slot, size of pass-through apertures for paperwork, etc.) is to be determined at project level to suit clinical services requirements and operational models. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) and associated items (microphones, signage, etc.) is to be confirmed at project level, in consultation with accessibility experts, to suit the configuration of the counter and security glazing. ~ The quantity and type of display screens required to oversee and control the flow of patients throughout the Emergency Department (including ambulance arrivals, patient flow and security feeds) are to be confirmed at project level to suit clinical services requirements and operational models. ~ If overall department planning results in rooms being accessed from behind the Staff Station, additional area for appropriate door circulation clearances will be required. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Acoustic treatments may be considered to assist with reducing noise transfer from adjacent spaces. All acoustic finishes must meet IPC requirements (Refer to Part D: Infection Prevention and Control for more information). ~ Provision of height adjustable workstations in lieu of fixed joinery benches may be considered at project level and provision should be in line with local WHS policies. Where height adjustable workstations are provided the location of services and the interaction of the moving workstation surface with the static public facing counter must be carefully considered. ~ Placement and visibility of nurse annunciators in adjacent corridors must be considered and coordinated with other ceiling elements such as bulkheads. ~ The type, extent and configuration of storage within the room for stationery and consumables will be dependent on service requirements, operational models and ICT policies and strategies. This includes considering the facility’s use of electronic medical records (EMR) as well as the need to store any remaining paper forms. ~ Size, type and quantity of waste bins will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the proximity of the counter to adjacent patient areas. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Wall mounted fire services items may be included in the Staff Station or provided nearby in a conspicuous and readily accessible position including a mimic panel, warden intercom phone, manual call point, break glass alarm, portable fire extinguisher and fire blanket. A ceiling mounted visual alarm device may also be provided in the Staff Station or in an adjacent corridor. Inclusion of these items in the Staff Station will be dependent on the overall department layout. Location, mounting heights and clearances to meet AS1670.1 and AS2444. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
STAD | Store - Accountable Drugs | Pharmacy | Translation and QA Only | 7.5 | 2700 |  | 4 | 07.04.2026 |  | 24 hours | 1-2 staff intermittently | The Store Accountable Drugs is a strongroom located within the Pharmacy Unit for the storage of accountable (Schedule 8) drugs and medications and provides a secure caged area for assembling orders. | ~ This room is to comply with jurisdictional legislation and public health facility policy, including any special provisions for refrigerated medicines. ~ The strong room should be designed in collaboration with an expert security consultant with assessment of the risks for the particular site. ~ The strong room should be independent of the rest of the building structure with no beams or columns passing through the ceiling, walls or floor. ~ The ceiling walls and floor should be built utilisiing suitable construction methods, e.g. reinforced concrete or steel plate modular forms (the wall thickness shown in this Standard Component is indicative only). ~ A gate door is to be provided for security when the main door is open. The security door should be torch and drill resistant, fitted with an appropriate locking mechanism incorporating duress features and an internal release mechanism in case persons are trapped within. ~ The strongroom will require adequate ventilation and a torch and drill resistant breather tube must be fitted to comply with fire regulations. ~ Security monitoring and detection equipment should be incorporated into the alarm system, to detect any attack on the structure. ~ A telephone should be installed for staff safety | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STBK | Store - Bulk | Logistics / Support Services | Translation and QA Only | 30 | 2700 | STBK-20 | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 2-3 staff intermittently | The Store - Bulk is the primary storage area for all delivered supplies and equipment prior to distribution to hospital services / departments. | ~ The Bulk Store should be located with ready access to the loading dock area. ~ Some departments, such as pharmacy, renal dialysis and pathology, will have bulk storage spaces that are managed independently. ~ Type and extent of storage solutions for this room will depend on the departments to be serviced and operational models for stock and equipment delivery. ~ Where a 'direct to imprest' model is used, consumable inventory is stored at a supply chain distribution centre and delivered to the hospital already packed into trolleys specific to the clinical area and immediately delivered to those areas. Long term storage is not required and less area is needed near the loading dock. ~ A 'central bulk store' model refers to goods being delivered to the hospital in large quantities and stored in a central bulk store. The process involves the delivery of goods on pallets, goods are then checked, unloaded, and placed in a bulk store by hospital supply staff. Consumables will then be picked and packed from the central store and delivered to clinical units and other areas as required. ~ Automated or motorised equipment may be considered to assist with the safe and efficient transfer of supply trolleys throughout the healthcare facility. Where tugs and AGVs are being considered, it is important to confirm clearances, door widths and turning circles within the room, in the adjacent corridor and along path of travel to all services / departments. ~ Refrigerated storage requirements to be confirmed at project level. ~ Wall protection is recommended to protect wall linings and finishes from damage from impact. The height of the wall protection will be dependent on equipment and trolleys frequently moved through the space; a height range of 900mm minimum up to 1500mm is recommended depending on trolley and equipment selection. ~ Hold open door hardware may be required to allow for easy movement of pallet jacks and trolleys in and out of the room. ~ Controlled, staff only access is required. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STCL | Store - Cleaner | Logistics / Support Services | Translation and QA Only | 12 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Store - Cleaner is a store provided for the central storage of consumables and bulk containers of cleaning chemicals. Large facilities may provide a separate room for the storage of chemicals depending on quantities, safety requirements and operational policies for centralised storage and decanting of chemicals to units. | ~ Hold open door hardware may be required to allow for easy movement of equipment and trolleys in and out of the room. ~ Type and extent of storage solutions for this room will depend on the departments to be serviced and operational models for cleaning and restocking consumables. ~ Type of storage provided for cleaning chemicals, particularly where the storage of significant quantities of chemicals containing flammable ingredients, to be assessed to meet safety and service requirements. ~ A clean linen trolley, or equivalent, may be provided for storage of clean mop heads that are laundered either onsite or offsite. The size of trolley will vary depending on service model and size of facility. ~ Controlled, staff only access is required. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | Translation and QA Only | 14 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | A secure room for the storage and recharging of mobile equipment when not in use. | ~ Clear space is required for parking mobile equipment including IV poles, wheelchairs, patient transfer equipment, trolleys and commode chairs. ~ Hooks may be provided for hanging equipment and rails may be provided to mount equipment whilst recharging. ~ Minimum and maximum shelving heights to suit local WHS and infection control policies, as well as fire safety requirements (e.g. the top of stored products is to be no nearer than 500mm to sprinkler deflectors). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | Translation and QA Only | 20 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | A secure room for the storage and recharging of mobile equipment when not in use. | ~ Clear space is required for parking mobile equipment including IV poles, wheelchairs, patient transfer equipment, trolleys and commode chairs. ~ Hooks may be provided for hanging equipment and rails may be provided to mount equipment whilst recharging. ~ Minimum and maximum shelving heights to suit local WHS and infection control policies, as well as fire safety requirements (e.g. the top of stored products is to be no nearer than 500mm to sprinkler deflectors). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STFS-10 | Store - Files, 10m2 | Administration | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | 8am to 6pm, Mon - Fri (dependent on unit operating hours) | 1-2 staff intermittently | The Store - Files, 10m² provides the space and amenities for the secure storage of files or patient clinical records. | ~ Type, size and quantity of shelving / storage solution to be selected to suit service requirements and work health and safety (WHS) policies. ~ Fire rating to room to be in accordance with Australian / New Zealand building codes, and comply with jurisdictional legislation regarding record-keeping (including any referenced Australian / New Zealand Standards). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STFS-20 | Store - Files, 20m2 | Administration | Translation and QA Only | 20 | 2700 |  | 6 | 07.04.2026 |  | 8am to 6pm, Mon - Fri (dependent on unit operating hours) | 1-2 staff intermittently | The Store - Files, 20m² provides the space and amenities for the secure storage of files or patient clinical records. | ~ Type, size and quantity of shelving / storage solution to be selected to suit service requirements and work health and safety (WHS) policies. ~ If compactus shelving is installed, the track may be surface mounted or recessed into the floor. Advice from a structural engineer is to be sought on floor load bearing capacity and potential deflection effect on walls, doors, etc. Handwheel operation may be required to reduce operator strain depending on block load, refer to local WHS policies. ~ Fire rating to room to be in accordance with Australian / New Zealand building codes, and comply with jurisdictional legislation regarding record-keeping (including any referenced Australian / New Zealand Standards). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STGN | Store - General | Clinical Support Set 1 | Translation and QA Only | 9 | 2700 | STGN-9 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | A secure room for the storage of general supplies used within the department. | ~ Facilities to support restocking workflows, including the use of barcode systems, to be considered to suit operational requirements. ~ Minimum and maximum shelving heights to suit local WHS and infection control policies, as well as fire safety requirements (e.g. the top of stored products is to be no nearer than 500mm to sprinkler deflectors). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STPP | Store - Patient Property | Mental Health | Full AHIA Review | 8 | 2700 |  | 7 | 31.03.2026 |  | Available 24 hours | 1-2 staff intermittently | The Store - Patient Property provides a secure room for the storage of patient property, including luggage, for the duration of their admission. | ~ The type, extent and configuration of storage solutions within the room, including provision of lockers, will be dependent on service requirements and operational policies for the method of property separation and volume of property to be stored per patient. ~ Maximum and minimum shelf heights are to be confirmed at project level to meet local work health and safety (WHS) policies. Requirements for the storage and restraint of items over certain heights and weights must also be confirmed to ensure safety conditions are able to be met (including for seismic considerations as applicable). ~ Operational models for access by patients, with or without staff supervision, or for staff only access are to be confirmed at project level. ~ This room may be provided in Mental Health Inpatient Units. Requirements for the selection of suitable finishes, hardware, fixtures and fittings of a type manufactured and marketed as anti-ligature (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. Anti-ligature fittings may require a performance solution to be provided for the room to meet accessibility requirements. This must be considered and addressed at project level to meet applicable legislation and standards (to be confirmed with the project accessibility and building code consultants). | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE
STRT | Stress Testing | Cardiac Investigations | Translation and QA Only | 20 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff | Room for undertaking patient diagnostic stress testing procedures. | ~ The Stress Testing room should be located close to patient toilet and change rooms. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
STSS | Store - Sterile Stock | Operating | Full AHIA Review | 40 | 2700 | STSS-20 | 6 | 06.05.2025 |  | 24 hours | 2-3 staff (with up to 4 additional staff intermittently) | A room with an aseptic environment for storage and holding of sterile stock for use in the Operating Suite or other acute treatment areas. | ~ This Standard Component assumes direct access to Operating Rooms and that it is multiplied as a module to serve Operating Rooms that are planned in a row – with the end of the room to be enclosed once modules are combined. Where sterile stock storage is centralised and transported through corridors to Operating Rooms. This room is to be enclosed (size, FF&E, and services increased according to number of Operating Rooms to be served), and door arrangements are to be adjusted to suit. ~ Sterile stock is to be stored in shelving compliant with AS 5369, this may be provided as either static units, single mobile units and/or as a compactus. If a compactus is to be used, depending on the product selected and the materials it is made from, structural engineering advice may need to be sought to ensure adequate load-bearing capacity and potential deﬂection eﬀect on walls, doors, etc. ~ Storage solutions must support consumable items to be stored separately (i.e. in different shelving units) to reusable medical devices (RMDs) as per AS 5369. ~ The size, quantity and type of storage solution will vary to suit service requirements. Additional shelving units require an approximate area of 1m2 per unit (assumes 900W x 400D x 2100H unit with space in front to access). ~ Storage height to be limited to 520mm min below ceiling to meet ﬁre sprinkler system requirements within AS 2118.1. ~ A clearance of 1100mm is recommended to be provided for circulation spaces within Store – Sterile Stock to facilitate movement of trolleys and staff. ~ Conﬁguration of computer workstations (bench mounted, wall mounted on articulated brackets, and/or workstations on wheels) is to be conﬁrmed to suit service requirements and local ICT policies. ~ Provision of automated doors to access this store from the corridor to be confirmed by project to suit service requirements and operational policies. ~ Light ﬁxtures to be sealed and flush-mounted to minimise opportunity for dust accumulation and ensure ease of cleaning. ~ Depending on proximity of this room to the Operating room and the use of x-ray equipment during procedures, radiation shielding may be required to some walls of this room and is to be assessed by a Radiation Consultant. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
TRBNL | Tribunal Hearing Room | Mental Health | Full AHIA Review | 30 | 2700 |  | 2 | 31.03.2026 |  | 9am to 5pm, Mon - Fri (may vary depending on service requirements for multipurpose use of room) | up to 12 persons seated;;; | The Tribunal Hearing Room provides the space and amenities to support the functions of the Mental Health Tribunal, including hearings, confidential discussions and/or counselling between the Tribunal members, the treating team, consumer, and their support persons and representatives. Hearings may be conducted in person or via video conference. The room may also be used for Staff handovers, clinical reviews, education, large family meetings and other activities during times when not in use as a Tribunal Hearing Room. | ~ Requirements for Tribunal Hearing Rooms, including audio visual/teleconferencing system requirements, will vary across jurisdictions. Refer to local policies for guidance. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Natural light and external outlook are desirable. Consider placement of windows and room orientation to suit privacy requirements and location of camera for videoconferencing to avoid glare. ~ Requirement for the provision of an adjacent observation area is to be confirmed based on service requirements and jurisdictional policies. Where provided, an observation window with integral venetians is to be provided. ~ Doors should be selected to support safety, dignity and wellbeing. Selections should be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Inclusion and size of a vision panel to be confirmed to suit service requirements. Privacy film may be applied to the vision panel as required. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ The Tribunal Hearing Room will require safe and effective access and egress. A second door is required. The location and swing of the secondary egress door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Mobile duress alarms are assumed to be provided. Fixed duress buttons are to also be included at appropriate locations throughout the room (e.g. nearby to secondary egress door or mounted to the underside of a table). Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ Provision of hearing augmentation may be required depending on audio visual/teleconferencing capabilities and features. Requirements to be confirmed at project level. ~ Furniture selected for the room, such as tables and chairs, should be appropriate for the various activities anticipated to be undertaken in the room as per service requirements. A nearby storage area for furniture may be required to support flexible use of the room. ~ Nearby access to a beverage bay and toilet facilities is recommended. ~ Provision of a room booking system (control panel, service requirements) may be considered at project level to suit service requirements and operational models. ~ A high level of acoustic privacy is required for confidentiality. Acoustic treatments and installation to be considered to meet requirements of the mental health environment, including for robustness. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | Full AHIA Review | 6.5 | 2700 | TRIAGE-1 | 3 | 31.03.2026 |  | 24 hours | 1 patient; 1 visitor / support person; 1 staff | The Triage - Emergency, Assessment Counter provides the space, equipment and services for initial assessment of patients presenting to the Emergency Unit. | ~ Multiple Triage Assessment Counters may be arranged together and may be combined the Reception - Emergency (RECP-E). If not directly connected to the Reception - Emergency, the triage assessment counters should be in close proximity. When multiple Triage and Reception Standard Components are combined, the final overall room configuration should include an egress that takes staff behind the secure line of the Emergency Unit. ~ Provision of a window for visual access from Reception - Emergency (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. ~ Clear line of sight to the waiting room is recommended for observation when the triage nurse is not with a patient. ~ Direct access to a Type B handwash basin is required. This basin is to be shared between multiple Triage Assessment Counters. Refer to Part D: Infection Prevention and Control for more information. ~ This Standard Component shows a counter where patients would be assessed while standing. Counters may be provided as standing height or seated height, or a mix of both, with at least one counter to provide wheelchair access as per AS1428.1 / NZS 4121. Where only one triage counter is provided, the configuration must meet requirements for wheelchair access (AS1428.1 or NZS 4121). ~ Configuration of the security glazing (size of communication slot, size of pass-through aperture for samples/paperwork, ability to use small diagnostic equipment, etc.) is to be determined at project level to suit clinical service requirements and operational models. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) and associated items (microphones, signage, etc.) is to be confirmed at project level, in consultation with accessibility experts, to suit the configuration of the counter and security glazing. ~ Acoustic treatment requirements are to be determined suit patient privacy requirements and reduce potential noise transfer to/from the adjacent waiting area. All acoustic finishes must meet IPC requirements (Refer to Part D: Infection Prevention and Control for more information). ~ Provision of height adjustable workstations in lieu of fixed joinery benches may be considered at project level and provision should be in line with local WHS policies. Where height adjustable workstations are provided the location of services and the interaction of the moving workstation surface with the static public facing counter must be carefully considered. ~ A patient flow/journey board should be located in a shared area nearby to Triage Assessment Counters/Rooms. ~ Ready access to height and weight measurement facilities, including baby weighing, is recommended. ~ Ready access to medications, including refrigerated medications, is required. Depending on model of care, access to a separate refrigerator for icepacks, oral rehydration solutions, etc. may also be required to support waiting room medicine. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical services requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins provided will be dependent on clinical services requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. Bins may be located in an area shared between multiple triage counters. ~ The requirement for Body Protection under AS/NZS 3003 is to be determined at project level depending on the use of medical equipment within the space and proximity of the counter to adjacent patient areas. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | Full AHIA Review | 13 | 2700 | TRIAGE-2 | 3 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/triage-emergency-assessment-room/?fullscreen=true&utm_source=project-link&rev=3 | 24 hours | 1 patient; 1 visitor / support person; 1-2 staff | The Triage - Emergency, Assessment Room provides the space, equipment and services for initial assessment, physical examination and commencement of first aid for patients presenting to the Emergency Unit. | ~ This room should be located adjacent or in close proximity to the Reception - Emergency (RECP-E). ~ Provision of a window for visual access from Reception - Emergency (when these rooms are collocated) may be considered to ensure staff are not isolated in the front of house area. ~ Clear line of sight to the waiting room is recommended for observation when the triage nurse is not with a patient. ~ The extent of glazing provided to the room is to be determined at project level to suit the overall department layout and requirements for waiting room observation. Provision of integral blinds or extension of the privacy curtain track over the internal observation window is to be determined to suit requirements for observation and patient privacy. ~ A Type B handwash basin is shown within this Standard Component but may instead be provided nearby and shared between multiple Triage Assessment Rooms. Removal of the handwash basin is subject to consultation with Emergency Unit and Infection Prevention and Control (IPC) staff. Refer to Part D: Infection Prevention and Control for more information. ~ A patient flow/journey board should be located in a shared area nearby to Triage Assessment Rooms. ~ Ready access to height and weight measurement facilities, including baby weighing, is recommended. ~ Ready access to medications, including refrigerated medications, is required. Depending on model of care, access to a separate refrigerator for icepacks, oral rehydration solutions, etc. may also be required to support waiting room medicine. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Input of electronic medical records (EMR) may be performed on a wall mounted computer workstation, a computer on a desk/bench, or on a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT strategies and policies. ~ The patient monitor may be mounted on the patient’s left or the patient’s right. The location of the patient monitor is to be determined at project level to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the bracket for the patient monitor. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The weight capacity of recliners selected must be considered to suit a wide range of patient requirements. The recliner must also have the ability to lay completely flat. ~ The clear area required for the use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical services requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins provided, including sharps bins, will be dependent on clinical services requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple triage rooms and possibly brought to the room as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
TRMT | Treatment Room | Ambulatory Care | Translation and QA Only | 14 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1-2 staff | The Treatment Room provides a controlled environment, privacy and facilities for carrying out consultations, examinations, treatments and minor procedures. |  | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | Translation and QA Only | 28 | 2700 |  | 1 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | 2 patients;; 2-3 staff | The Treatment Room - Hand Therapy/Splinting provides a controlled environment, privacy and facilities for carrying out treatment and rehabilitation performed by an occupational therapist or physiotherapist with patients that suffer from conditions affecting the hands and upper limbs, such as wounds, scars, burns, fractures or amputations. | ~ A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. ~ Depending on operational model, the hand therapy treatment room may be an open area adjoining a space with other allied health treatment bays. If open, floor boxes may be required for power to height adjustable tables. ~ Printing facilities to be shared within the overall department. ~ Refrigeration requirements for some materials in warmer climates may need to be considered. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
TRMT-POD | Treatment Room - Podiatry | Allied Health | Translation and QA Only | 14 | 2700 | PODTR-14 | 6 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | 1 patient; 1 visitor / support person; 1 staff | The Treatment Room - Podiatry provides space and facilities for podiatry consultation, examination and treatment. The room may be used for measuring and fitting prosthetic appliances but not for fabrication. | ~ Medication storage, clean-up facilities for instruments, sink and plaster trap facilities are to be provided nearby. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ An external outlook is desirable. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
ULTR | Ultrasound Room | Medical Imaging | Full AHIA Review | 16 | 2700 |  | 6 | 15.05.2025 |  | Up to 24 hours | 1 patient; 1 support person / carer; 1-2 staff | The Ultrasound Room provides the space and amenities for sonographers to perform diagnostic ultrasound imaging on patients. | ~ The room will require sufficient clearance for the ultrasound machine and sonographer to be positioned to either side of the examination trolley and may need to occasionally accommodate a patient on a bed to either be transferred to the examination trolley or have the ultrasound performed while they are in the bed. ~ Close access to a patient toilet and change room is required, with direct access from the room being preferred to support patients that have changed into gowns and require ultrasounds to be performed with a full bladder and then with an empty bladder. ~ A combination of dimmable general room lighting and dimmable indirect lighting (wall and/ or ceiling fixtures) is preferred to obtain appropriate lighting levels and avoid glare on the screen of the ultrasound machine. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | Full AHIA Review | 20 | 2700 |  | 2 | 15.05.2025 |  | Up to 24 hours | 1 patient; 1 support person / carer; 1-2 staff | The Ultrasound Room - Procedures provides the space and amenities for sonographers to perform ultrasound imaging in support of clinicians carrying out biopsies and interventional procedures. General anaesthesia will not be administered in this room. | ~ The room will require sufficient clearance for the ultrasound machine and sonographer to be positioned to either side of the examination trolley and may need to occasionally accommodate a patient on a bed to either be transferred to the examination trolley or have the ultrasound/procedure performed while they are in the bed. ~ The ceiling height has been nominally shown at 2700mm, however 3000mm is also acceptable and the height is to be determined based on ceiling mounted equipment and service requirements. ~ Patient transfer aids such as mobile hoists, patient slides and hover mats are to be considered for assisted patient transfers to and from the examination couch where a procedure cannot alternatively be performed on a patient bed. A ceiling mounted hoist may be considered for patient transfers. Final selection of transfer aids will be dependent on service requirements, the needs of the anticipated patient cohort (e.g. for ambulatory services, acute services, etc.), as well as WHS risk assessments/policies. Appropriate ceiling support is required for the provision of a ceiling mounted hoist. ~ A combination of dimmable general room lighting and dimmable indirect lighting (wall and/ or ceiling fixtures) is preferred to obtain appropriate lighting levels and avoid glare on the screen of the ultrasound machine. Additional directional lighting for procedures may be required and is best provided with mobile procedure lights to allow sufficient adjustability to perform tasks while ensuring the ultrasound screen can still be visualised. ~ Sufficient space for pathology staff to bring in a trolley and plug in equipment (e.g. microscopes) is required. ~ Close access to a patient toilet and change room is required, with direct access from the room being preferred to support patients that have changed into gowns and require ultrasounds to be performed with a full bladder and then with an empty bladder. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
UTRM | Uptake Room | Nuclear Medicine / PET | Translation and QA Only | 10 | 2700 |  | 1 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | 1 patient;; 1 staff | The Uptake Room is used to inject patients with a radiopharmaceutical and allow them to rest until 'uptake' has occurred before transfer to the scanning room. Patients need to be relaxed in a warm, quiet and dimmed environment to promote uptake. Uptake duration is typically 45 to 60 minutes. | ~ Visual and audio observation of the patient during this time is typically provided from the Control Room of the PET-CT Imaging Room and intercoms, cameras and display screens are to be provided to support patient observation. ~ Injections of radiopharmaceuticals can be undertaken within the room or from outside the room via an automated dose delivery system, which will be accommodated outside each uptake room with a suitable lead-lined injection port in the wall that will allow the coil to be connected to both the machine and the patient (details should be confirmed with vendor) ~ Radiation shielding is required to the room and is to be in accordance with a radiation shielding consultants advice. This will be based on the type of radiopharmaceutical, the number of patients seen on a daily basis and proximity to other services. | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WAIT-10 | Waiting, 10m2 | Public Areas | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 8 patients / visitors;; | The Waiting, 10m2 provides the space and amenities required for patients, visitors / support persons, and families to wait prior to attending an appointment and/or receiving clinical care in a department. | ~ The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ Waiting areas may be shared between departments. ~ Public amenities including baby change facilities should be located nearby. ~ A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. ~ Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. ~ Acoustic treatments may be considered as required to ensure the noise level in the space is comfortable both in the waiting area and adjacent reception areas. ~ Check-in kiosks may be located nearby and services will need to be confirmed based on system requirements. ~ Provision of a hearing augmentation system may be required where a built in amplification system is provided, if a TV monitor is installed. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection prevention and control (IPC) policies. ~ An external outlook is desirable. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WAIT-20 | Waiting, 20m2 | Public Areas | Translation and QA Only | 20 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 17 patients / visitors;; | The Waiting, 20m2 provides the space and amenities required for patients, visitors / support persons, and families to wait prior to attending an appointment and/or receiving clinical care in a department. | ~ The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ Waiting areas may be shared between departments. ~ Public amenities including baby change facilities should be located nearby. ~ A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. ~ Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. ~ Acoustic treatments may be considered as required to ensure the noise level in the space is comfortable both in the waiting area and adjacent reception areas. ~ Check-in kiosks may be located nearby and services will need to be confirmed based on system requirements. ~ Provision of a hearing augmentation system may be required where a built in amplification system is provided, if a TV monitor is installed. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection prevention and control (IPC) policies. ~ An external outlook is desirable. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WAIT-30 | Waiting, 30m2 | Public Areas | Translation and QA Only | 30 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 25 patients / visitors;; | The Waiting, 30m2 provides the space and amenities required for patients, visitors / support persons, and families to wait prior to attending an appointment and/or receiving clinical care in a department. | ~ The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ Waiting areas may be shared between departments. ~ Public amenities including baby change facilities should be located nearby. ~ A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. ~ Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. ~ Acoustic treatments may be considered as required to ensure the noise level in the space is comfortable both in the waiting area and adjacent reception areas. ~ Check-in kiosks may be located nearby and services will need to be confirmed based on system requirements. ~ In large waiting areas (e.g. Emergency Department, Main Entry) provision of facilities for phone charging may be considered. ~ Provision of a hearing augmentation system may be required where a built in amplification system is provided, if a TV monitor is installed. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection prevention and control (IPC) policies. ~ An external outlook is desirable. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WAIT-S | Waiting, Sub | Public Areas | Translation and QA Only | 5 | 2700 | WAIT-SUB | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 5 patients / visitors;; | The Waiting, Sub provides a satellite area with the space and amenities required for patients and their visitors / support persons to wait within a unit, close to procedure/imaging rooms, consult rooms or offices. | ~ The size of waiting areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ A range of occupants will need to be accommodated including adults, children, able-bodied persons and people with disabilities. In many instances bariatric capacity will also be required. ~ Consider furniture options including weight rating of all chairs and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Wall protection is recommended to protect wall linings and finishes from damage due to movement of loose furniture. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided in line with local infection prevention and control (IPC) policies. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WAIT-SEC | Waiting - Secure | Mental Health | Full AHIA Review | 6 | 2700 |  | 7 | 31.03.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 persons seated;;; | The Waiting - Secure is an area provided for visitors to a Mental Health Unit to wait in comfort prior to or during visits with consumers. Visitors will alert staff of their arrival to gain entry to the unit. | ~ The Waiting - Secure is to be located with direct access to a counter for reception area or a staff station of the Mental Health Unit. Public amenities should be located nearby to allow for ready access. ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Based on a risk assessment, ceiling height is to be confirmed at a project level in combination with considerations for FF&E selection to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Where caulking required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ Security provisions for controlled access to the Mental Health Unit are to be confirmed to suit local jurisdictional policies and operational services requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
WCAC | Toilet - Accessible | Sanitary Facilities | Translation and QA Only | 6 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 person intermittently;;; | The Toilet - Patient provides an enclosed, lockable room with an accessible toilet and handwashing basin for use by patients, visitors or staff with disabilities (with or without assistance). A baby change table may also be located in this room. | ~ The room layout and all fixtures, furniture and equipment (FF&E) are to comply with AS 1428.1 and NZ 4121. ~ Signage with tactile Braille nominating 'All Gender Accessible Toilet' required to room, including noting if the room is a right-handed or left handed room (depending on layout). ~ If the Toilet - Accessible is located in a patient care area for use by patients, the nurse call system should be included and emergency release door hardware should be installed to allow staff access in emergency situations. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system. ~ If the Toilet - Accessible is to be dedicated for use by staff, access control (e.g. a swipe card reader) may be required if this room is provided in a public area or patient care area. ~ The entrance to the room is to be flush with the adjoining floor for access in commode chairs/wheelchairs or with other assistive devices. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WCPT | Toilet - Patient | Sanitary Facilities | Translation and QA Only | 4 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1 staff assisting as required | The Toilet - Patient provides an enclosed, lockable room with a toilet and handwashing basin for use by patients (with or without assistance). | ~ Signage with tactile Braille nominating 'All Gender Patient Toilet' required to room. ~ Emergency release door hardware should be installed to allow staff access in emergency situations. ~ The entrance to the room is to be flush with the adjoining floor for access in commode chairs/wheelchairs or with other assistive devices. ~ Toilet lids and seats are to be robust and suitable for long term, high frequency use. It is recommended that the toilet lid/seat is coloured to achieve a minimum 30% luminance contrast between the lid/seat, and the toilet pan, the floor, and the adjacent walls to support patients with visual impairments. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WCPU | Toilet - Public | Sanitary Facilities | Translation and QA Only | 3 | 2700 | WCPU-3 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 person intermittently;;; | The Toilet - Public provides an enclosed, lockable room with a toilet and handwashing basin for use by the general public. | ~ Signage with tactile Braille nominating 'All Gender Public Toilet' required to room. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
WCST | Toilet - Staff | Sanitary Facilities | Translation and QA Only | 3 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 staff intermittently | The Toilet - Staff provides an enclosed, lockable room with a toilet and handwashing basin for use by staff. | ~ Signage with tactile Braille nominating 'All Gender Staff Toilet' required to room. ~ Access control (e.g. a swipe card reader) may be required if this room is provided in a public area or patient care area. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
XRAY | General X-Ray Room | Medical Imaging | Full AHIA Review | 38 | 3000 | GENXR | 5 | 15.05.2025 |  | Up to 24 hours | 1 patient;; 1-2 staff | The General X-ray Room provides the space and equipment for undertaking general radiographic imaging. This Standard Component may be located within a Medical Imaging Unit or Emergency Unit. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for services between the patient table, vertical bucky, imaging device and the control area will be required and must be coordinated with the MME vendor. ~ A unistrut type ceiling may be required depending on equipment to be installed. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room may need to accommodate a patient on a bed to either be transferred to the x-ray table or have the x-ray performed while they are on the bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and equipment selection. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | Full AHIA Review | 45 | 3000 |  | 1 | 15.05.2025 |  | Up to 24 hours | 1 patient;; 1-2 staff | The combined General X-ray and OPG Room provides the space and equipment for undertaking general radiographic imaging and orthopantomogram (OPG) imaging. | ~ Equipment is to be installed to manufacturer’s specifications with sufficient clearances for maintenance access. Installation and replacement access routes should also be considered. Additional building services connections and outlets are to be coordinated to suit equipment requirements. Cable ducts for x-ray equipment services between the patient table, vertical bucky, imaging device and the control area, and for OPG equipment services between the imaging device and control area will be required and must be coordinated with the MME vendor. ~ A unistrut type ceiling may be required depending on equipment to be installed. ~ The OPG area is designed to accommodate OPG, Lateral Cephalogram and Cone Beam CT imaging devices with minor adjustments to suit equipment and meet shielding requirements. ~ All shielding on this Standard Component is indicative. Radiation shielding to suit the overall department layout, anticipated workload and the equipment procured is to be assessed and advised by a qualified Radiation Consultant to meet relevant legislation and local radiation safety policies. ~ An ‘X-ray in Use’ light system is required with signs at each entry to the imaging room that are illuminated when the imaging device is on and turned off when it stops. The exact wording required on illuminated signs will be determined by relevant legislation and local radiation safety policies. Project teams must confirm all radiation safety signage requirements with their jurisdiction’s regulatory agency. ~ The room may need to accommodate a patient on a bed to either be transferred to the x-ray table or have the x-ray performed while they are on the bed. Bed movement into, around and out of the room, and patient transfer should be considered during planning to reduce manual handling. ~ Provision of additional speakers and microphones within the room for communication between staff and the patient from the control area will be dependent on service requirements, final room layout and equipment selection. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ The type, extent and configuration of storage within the room for consumables, linen, equipment, etc. will be dependent on service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Size, type and quantity of waste bins is dependent on waste management policies (e.g. for waste separation, frequency of waste removal, etc.) and service requirements. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The final services and configuration of the Medical Services Panel (MSP) - medical gases, nurse call, power and data - will be dependent on service requirements. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
AusHFG Standard Components - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | D+W | DOHI-116.02 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1 | optional integral blind to door panel, dependent on operational service requirements
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | MMBE-102 | BED: patient, electric, with mattress, bariatric | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | MMBE-222 | TRACK: patient lifter, traverse H-track, bariatric, ceiling mounted | 1 | 1 |  | configuration, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | MMGE-020 | CHAIR: patient, bariatric | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function may be considered at project level
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | MMBE-252 | CASSETTE MOTOR: patient lifter, bariatric, for ceiling mounted system | 1 | 1
1BR-BAR | 1 Bed Room - Bariatric | Inpatient Accommodation | FFE | MMBE-262 | SLING: patient lifter, bariatric | 1 | 1
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] ceiling tiles may also be acceptable dependent upon the acuity of patients to be accommodated and procedures to be performed within the room
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] to corridor; extent of glazing to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] to bedhead; low level for electric bed
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] adjacent to patient chair
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-106.01 | GPO: single, ceiling mounted, horizontal | 1 | 1 |  | [ELGP-101] to patient entertainment system
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 9 | 1 | Panel 1 | [ELGP-122] type and quantity to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-231.01 | GPO: double, emergency power, wall mounted, horizontal | 1 | 1 |  | [ELGP-223] to patient monitor
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1 |  | [ELBO-005]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006] on services panel
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 to general room lighting, 1 to night lighting, 1 on services panel to reading light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | [FIHR-016] optional, mobile sharps bin may be provided to be shared between multiple rooms
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004] to patient entertainment screen; configuration will be dependent on operational and ICT policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047] to door and observation window
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010] to door and observation window
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1 |  | [FQSN-051] type and extent of storage for patient property to suit operational policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013] z
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | [FQCW-044] optional, mobile sharps bin may be provided to be shared between multiple rooms
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] on services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] above services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] on services panel
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012] configuration will be dependent on operational and ICT policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1 | [ITIN-025] quantity to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to patient monitor
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | [ITNE-049] optional, to patient locker; provision dependent on operational policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | [FIJO-209] type and extent of storage for patient property to suit operational policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | [LIFX-017] switch to patient handset and wall near entry
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011] switch to patient handset and services panel
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1 |  | [MMBE-010]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMGE-019 | CHAIR: patient | 1 | 1 |  | [MMGE-019]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 |  | [MMHA-005] telemetry provision to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-010] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-002]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-001] to ensuite side
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to ensuite
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to bedroom side
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | WIFX-008.01 | WINDOW: fixed, internal, single glazed, sill at 1050H | 1 | 3 | Internal - Window 1 | [DWOB-001] optional; extent of glazing to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1 | [DWWH-005] external, natural light and outlook essential
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-IN-OU)
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing to suit clinical service requirements for patient observation and patient privacy requirements
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | optional; provision dependent on clinical service requirements for patient observation
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided in a holder on the end of the patient bed
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQTA-401 | TABLE: round, 450H, 500 diameter | 1 | 1 |  | to carer's area
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQBS-282 | RECLINER: visitor, clinical areas, fold out bed | 1 | 1 |  | selected item to suit operational models and local IPC policies
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function may be considered at project level
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to carer's area
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-CO-OU1 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-351 | BRACKET: patient entertainment system, fixed, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-IN-OU)
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing to suit clinical service requirements for patient observation and patient privacy requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | optional; provision dependent on clinical service requirements for patient observation
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQBS-282 | RECLINER: visitor, clinical areas, fold out bed | 1 | 1 |  | selected item to suit operational models and local IPC policies
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQTA-401 | TABLE: round, 450H, 500 diameter | 1 | 1 |  | to carer's area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided in a holder on the end of the patient bed
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to carer's area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function may be considered at project level
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-351 | BRACKET: patient entertainment system, fixed, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | FIHR-414 | BRACKET: patient monitor, articulated, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELSW-021 | SWITCH: light, dimmer | 1 | 1 | Pendant 1 - Arm 2 | to general room lights; to be coordinated with switch on wall
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, on pendant services head | 1 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMSP-121 | PENDANT: double arm, ceiling mounted | 1 | 1 | Pendant 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | DOSL-073.02 | DOOR: sliding, 1 leaf, 900 clear opening, fully glazed, framed with mid-rail, with integral blinds | 1 | 1 | Internal - Door 2 | optional, to support patient observation; provision is to be confirmed at project level and will be dependent on staffing models and local IPC policies/risk assessment
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | to staff write-up if provided outside room
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 2 | to staff write-up if provided outside room
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 3 | to adjacent room to support patient observation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to patient lifter track
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 2 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | to UPS outlets on medical services pendant
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | to night lights; to be coordinated with switch on medical services pendant
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights; to be coordinated with switch on medical services pendant
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | LIFX-151 | LIGHT: night, wall mounted | 2 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | WIOP-256.02 | WINDOW: operable, jockey sash, external, double glazed, sill at 750H, with integral blind | 1 | 1 | External - Window 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQBS-282 | RECLINER: visitor, clinical areas, fold out bed | 1 | 1 |  | selected item to suit clinical services requirements, operational models and local IPC policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | a privacy curtain is provided to the glazed door and panel and staff workstation at the front of the room; the use of integral blinds or switchable glass may be considered at project level based on assessment of maintenance, product lifecycle and downtime requirements
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 6 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | ability for screen to duplicate patient monitoring information for added visibility in emergency situations to be considered
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | alternative arrangement on ceiling mounted articulated arm may be considered at project level to suit clinical requirements and operational models for write-up and observation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-116 | BED: patient, electric, with mattress, intensive care | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMGE-381 | MACHINE: dialysis | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMHA-051 | DEVICE: ventilator, adult | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | ability to turn off/dim display to be considered to respond to patient preferences/needs
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYGE-082 | WALL BOX: renal dialysis, integral tundish, with 1 water supply connection and 2 drain connections | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-104 | TUNDISH: in wall, with viewing panel | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | HYDR-157 | TRAP: cooling pit, with sealed lid | 1 | 1 |  | optional, required if dialysis wall box is provided; to support cooling of wastewater from heat disinfection of dialysis machines and portable RO machines
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | D+W | DOST-074.01 | DOOR: stacking, 2 leaves + 1 fixed panel, 1800 clear opening, fully glazed, framed with mid-rail | 1 | 1 | Internal - Door 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMGE-386 | PROCESSOR: water treatment, dialysis, reverse osmosis (RO), mobile | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITCL-135 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on pendant services head | 1 | 1 | Pendant 1 - Arm 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 2
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 2 | 1 |  | quantity and type to be confirmed to suit final power provisions
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Pendant 1 - Arm 2 | to night lights; to be coordinated with switch on wall
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FIN | WLPR-006.02 | WALL PROTECTION: corner guards, to 1050 AFFL | 1 | 1 | Wall Protection | coordinated with adjacent wall protection and observation windows
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 2 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to carer's area
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMTR-092 | TROLLEY: procedure, 600W x 490D x 900H nom | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | FFE | MMTR-002.02 | TROLLEY: stainless steel, 600W x 490D x 900H nom, 2 tier | 1 | 1
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | shown to patient's right (services head R); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-ICU | 1 Bed Room - Intensive Care | Intensive Care | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 2 | shown to patient's left (services head L); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided in a holder on the end of the patient bed
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function may be considered at project level
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-IN-OU)
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing to suit clinical service requirements for patient observation and patient privacy requirements
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-IN1 | 1 Bed Room - Inboard Ensuite, Type 1 | Inpatient Accommodation | FFE | FIHR-351 | BRACKET: patient entertainment system, fixed, wall mounted | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-IN-OU)
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing to suit clinical service requirements for patient observation and patient privacy requirements
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function may be considered at project level
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided in a holder on the end of the patient bed
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-IN2 | 1 Bed Room - Inboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-351 | BRACKET: patient entertainment system, fixed, wall mounted | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | DOHI-114.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | WIOP-255.02 | WINDOW: operable, jockey sash, external, double glazed, sill at 600H, with integral blind | 1 | 1 | External - Window 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-NE)
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | DOHI-043.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel, with integral blind | 1 | 1 | Internal - Door 3 | to anteroom (see ANRM)
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to both sides
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ITCL-254 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with intercom and speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function to be confirmed to suit clinical service requirements
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door and anteroom door
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided in a holder on the end of the patient bed
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-ISO-N | 1 Bed Room - Isolation, Negative Pressure | Inpatient Accommodation | SER | ELGP-206 | GPO: double, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | DOHI-017.12 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, anti-ligature and anti-barricade, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1 | inclusion and size of vision panel to be confirmed to suit service requirements; controls for integral blind to be provided to both bedroom and corridor sides of the vision panel; switchable glass may be provided in lieu of integral blind; additional requirements for glazing in vision panel to be confirmed to suit the mental health environment
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 3 | Internal - Door 1 | optional; provision dependent on leaf material and finish
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | FLVY-102 | FLOOR FINISH: vinyl, seamless, standard slip resistance, cushioned | 1 | 1 | Floor Finish 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 13 | 1 | Floor Skirting
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 3 | 1 | Wall Finish 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | low height, for bed
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | 1 to bedhead, 1 to bench
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | 2 for general room lights (1 to entry and 1 to bedhead), 1 for ensuite lights, 1 for light over bench
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ITCL-127 | BUTTON: nurse call, patient to staff call, with cancel, joinery mounted | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | LIFX-156 | LIGHT: night, wall recessed, tamper proof, anti-ligature | 1 | 3 |  | optional; control to bedhead; an additional control may be provided outside the bedroom to support staff observation (restriction of access to external light control must be considered)
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | LIFX-168 | LIGHT: reading, ceiling recessed, tamper proof, anti-ligature | 1 | 1 |  | optional; may alternatively be integrated into the bedhead if provided
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FIBM-057 | NOTICE BOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1 |  | to bench; material and method for attaching items to be confirmed to suit operational models
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FIBM-152 | MIRROR: fixed, safety glass, toughened and laminated, frameless, tamper proof, anti-ligature | 1 | 3 |  | optional; material to be confirmed at project level to suit service requirements
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQSN-107 | BEDSIDE TABLE: fixed, patient locker, tamper proof, anti-ligature | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOBE-011 | BENCH: 500D, laminate | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOCU-406 | WARDROBE: built-in, open, fixed shelves, tamper proof, anti-ligature | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to wardrobe
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | MMBE-141 | BED: patient, electric, with mattress, mental health | 1 | 1 |  | may alternatively be provided as a fixed plinth type bed depending on service requirements
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | WIOP-255.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 600H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 1 | operability (jockey sash) as required to allow maintenance of integral blind; additional requirements for glazing to be confirmed to suit the mental health environment
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | JOBH-022 | BEDHEAD: full height, tamper proof, anti-ligature | 1 | 1
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | FFE | FQSN-123 | SAFE: small, integral to joinery | 1 | 1 |  | optional; to wardrobe; provision dependent on operational models for property storage
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | DOHI-002.03 | DOOR: hinged, 1 leaf, 850 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-MH-IN); with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; outside door for card/wristband swipe access; provision dependant clinical service requirements and operational models; door mounted hardware is also acceptable
1BR-MH-IN | 1 Bed Room - Mental Health, Inboard Ensuite | Mental Health | SER | ELSW-002 | SWITCH: light, 2-gang | 1 | 1 |  | optional; required for reading light and night light if provided; to bedhead
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | FLVY-102 | FLOOR FINISH: vinyl, seamless, standard slip resistance, cushioned | 1 | 1 | Floor Finish 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 10 | 1 | Floor Skirting
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 3 | Internal - Door 1 | optional; provision dependent on leaf material and finish
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | DOHI-017.12 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, anti-ligature and anti-barricade, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1 | inclusion and size of vision panel to be confirmed to suit service requirements; controls for integral blind to be provided to both bedroom and corridor sides of the vision panel; switchable glass may be provided in lieu of integral blind; additional requirements for glazing in vision panel to be confirmed to suit the mental health environment
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | WIOP-255.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 600H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 1 | operability (jockey sash) as required to allow maintenance of integral blind; additional requirements for glazing to be confirmed to suit the mental health environment
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | DOHI-002.03 | DOOR: hinged, 1 leaf, 850 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-MH-IN); with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; outside door for card/wristband swipe access; provision dependant clinical service requirements and operational models; door mounted hardware is also acceptable
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | low height, for bed
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | 1 to bedhead, 1 to bench
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | 2 for general room lights (1 to entry and 1 to bedhead), 1 for ensuite lights, 1 for light over bench
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ITCL-127 | BUTTON: nurse call, patient to staff call, with cancel, joinery mounted | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | LIFX-156 | LIGHT: night, wall recessed, tamper proof, anti-ligature | 1 | 3 |  | optional; control to bedhead; an additional control may be provided outside the bedroom to support staff observation (restriction of access to external light control must be considered)
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | ELSW-002 | SWITCH: light, 2-gang | 1 | 1 |  | optional; required for reading light and night light if provided; to bedhead
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | SER | LIFX-168 | LIGHT: reading, ceiling recessed, tamper proof, anti-ligature | 1 | 1 |  | optional; may alternatively be integrated into the bedhead if provided
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FIBM-057 | NOTICE BOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1 |  | to bench; material and method for attaching items to be confirmed to suit operational models
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FIBM-152 | MIRROR: fixed, safety glass, toughened and laminated, frameless, tamper proof, anti-ligature | 1 | 3 |  | optional; material to be confirmed at project level to suit service requirements
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQSN-107 | BEDSIDE TABLE: fixed, patient locker, tamper proof, anti-ligature | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOBE-011 | BENCH: 500D, laminate | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOCU-406 | WARDROBE: built-in, open, fixed shelves, tamper proof, anti-ligature | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to wardrobe
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | MMBE-141 | BED: patient, electric, with mattress, mental health | 1 | 1 |  | may alternatively be provided as a fixed plinth type bed depending on service requirements
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | JOBH-022 | BEDHEAD: full height, tamper proof, anti-ligature | 1 | 1
1BR-MH-NE | 1 Bed Room - Mental Health, Nested Ensuite | Mental Health | FFE | FQSN-123 | SAFE: small, integral to joinery | 1 | 1 |  | optional; to wardrobe; provision dependent on operational models for property storage
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-NE)
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing to suit clinical service requirements for patient observation and patient privacy requirements
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function may be considered at project level
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided in a holder on the end of the patient bed
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ELGP-206 | GPO: double, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-NE | 1 Bed Room - Nested Ensuite | Inpatient Accommodation | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 2 | 1 | Panel 1 | to clinical side (closest to entry door), 1 to each bed; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 8 | 1 | Panel 1 | 4 to each bed; quantity and type of power outlets to suit clinical service requirements
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 2 | 1 | Panel 2 | to patient/visitor side, 1 to each bed; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 4 | 1 | Panel 2 | 2 to each bed; quantity and type of power outlets to suit clinical service requirements
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 2 | 2 to each bed; quantity and type of power outlets to suit clinical service requirements
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ELGP-206 | GPO: double, ceiling mounted | 2 | 1 |  | 1 to each patient entertainment system; services to be confirmed to suit selected system
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | 1 to general room lights, 2 to night lights
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | 1 to each bed; may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 2 | 1 |  | 1 to each bed; with holder and cable management items as required; inclusion of intercom function may be considered at project level
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 2 | 1 |  | 1 to each patient entertainment system; services to be confirmed to suit selected system
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 2 | 1 |  | 1 to each patient entertainment system; services to be confirmed to suit selected system, may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 2 | 1 |  | 1 to each bed; control to bedhead and patient handset
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 2 | 1 |  | 1 to each bed; control to bedhead and patient handset
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 1 |  | for patient care information
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | 1 to each bed; may alternatively be provided as a bottle in a holder located on the end of the beds
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 3 | 1 |  | 1 to each bed, 1 to centre track
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 2 | 1 |  | 1 to each bed; configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 3 |  | optional, 1 to each bed; provision dependent on operational models
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 2 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 2 | 1
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | MMBE-211.01 | TRACK: patient lifter, fixed, ceiling mounted, straight | 2 | 3 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | 1 to each bed; with tubing storage/management accessories as required
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 4 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 2 | 3 |  | optional, 1 to each bed; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 2 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room; provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 2 | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 2 | 1 | Panel 2 | 1 to each bed; requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | optional, 1 to each bed; for telephone if provided
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 2 | 1 |  | 1 to each bed; outside curtain at foot of bed; to be coordinated with lights located in the corridor
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1 |  | 1 to each bed; to bedhead for patient/visitor use
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1 |  | 1 to each bed; to bedhead at low height for bed and mattress
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 2 | 1 |  | 1 to each bed
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 2 | 1 |  | 1 to each bed; wall protection panel with in-wall medical services panel is also acceptable
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter tracks where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter tracks where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-IN-OU)
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing to suit clinical service requirements for patient observation and patient privacy requirements
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
2BR-IN | 2 Bed Room - Inboard Ensuite | Inpatient Accommodation | FIN | WLPR-006.06 | WALL PROTECTION: corner guards, to 2100 AFFL | 1 | 1 | Wall Protection | to basin
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 8 | 1 | Panel 2 | 2 to each bed; quantity and type of power outlets to suit clinical service requirements
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 4 | 1 | Panel 2 | to patient/visitor side, 1 to each bed; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 4 | 1 | Panel 2 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 8 | 1 | Panel 2 | 2 to each bed; quantity and type of power outlets to suit clinical service requirements
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 4 | 1 | Panel 1 | to clinical side (closest to entry door), 1 to each bed; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 4 | 1 | Panel 1 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 4 | 1 | Panel 2 | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 4 | 1 | Panel 2 | 1 to each bed; requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 16 | 1 | Panel 1 | 4 to each bed; quantity and type of power outlets to suit clinical service requirements
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 4 | 1 |  | 1 to each bed; to bedhead for patient/visitor use
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 4 | 1 |  | 1 to each bed; to bedhead at low height for bed and mattress
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 4 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room; provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 4 | 1 |  | 1 to each patient entertainment system; services to be confirmed to suit selected system, may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ELGP-206 | GPO: double, ceiling mounted | 4 | 1 |  | 1 to each patient entertainment system; services to be confirmed to suit selected system
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 5 | 1 |  | 1 to general room lights, 4 to night lights
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 4 | 1 |  | 1 to each bed; may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 4 | 1 |  | 1 to each bed; with holder and cable management items as required; inclusion of intercom function may be considered at project level
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 4 | 1 |  | 1 to each patient entertainment system; services to be confirmed to suit selected system
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 4 | 1 |  | 1 to each bed; control to bedhead and patient handset
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 4 | 1 |  | 1 to each bed; control to bedhead and patient handset
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 1 |  | optional, 1 to each bed; for telephone if provided
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 4 | 1 |  | 1 to each bed; outside curtain at foot of bed; to be coordinated with lights located in the corridor
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-IN-OU)
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | to both sides
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to ensuite (see ENS-IN-OU)
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 2 | type, material and cleaning requirements of window coverings to be confirmed at project level
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 2
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FIN | WLPR-006.03 | WALL PROTECTION: corner guards, to 1200 AFFL | 1 | 1 | Wall Protection
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 4 | 3 |  | optional, 1 to each bed; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 4 | 1 |  | 1 to each bed; configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 4 | 1 |  | 1 to each bed; with tubing storage/management accessories as required
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 6 | 1 |  | 1 to each bed, 1 to track between beds
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 4 | 3 |  | optional, 1 to each bed; provision dependent on operational models
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 4 | 1
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 4 | 1 |  | 1 to each bed; for patient care information
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room, for infection control precaution and/or patient needs information; provision dependent on operational models
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment, wall mounted | 16 | 3 |  | 2 to each bed; optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 4 | 1 |  | 1 to each bed; may alternatively be provided as a bottle in a holder located on the end of the beds
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 4 | 1 |  | 1 to each bed
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 4 | 1 |  | 1 to each bed; wall protection panel with in-wall medical services panel is also acceptable
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter tracks where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 4 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
4BR-IN | 4 Bed Room - Inboard Ensuites | Inpatient Accommodation | FFE | MMBE-211.01 | TRACK: patient lifter, fixed, ceiling mounted, straight | 4 | 3 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
ADLB | ADL Bathroom | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ADLB | ADL Bathroom | Allied Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional
ADLB | ADL Bathroom | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
ADLB | ADL Bathroom | Allied Health | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014] water resistant flush set ceiling is also acceptable
ADLB | ADL Bathroom | Allied Health | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021] with privacy latch and emergency release
ADLB | ADL Bathroom | Allied Health | SER | ELGP-202.01 | GPO: double, wall mounted, power available indicator, horizontal | 1 | 1 |  | [ELGP-209]
ADLB | ADL Bathroom | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ADLB | ADL Bathroom | Allied Health | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] to basin
ADLB | ADL Bathroom | Allied Health | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-007] dressing
ADLB | ADL Bathroom | Allied Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
ADLB | ADL Bathroom | Allied Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
ADLB | ADL Bathroom | Allied Health | FFE | FIDI-282 | HOLDER: soap/shampoo, wall recessed | 2 | 1 |  | [FIDI-051]
ADLB | ADL Bathroom | Allied Health | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
ADLB | ADL Bathroom | Allied Health | FFE | FIHR-026 | HOOK: coat, wall mounted | 4 | 1 |  | [FIHR-026]
ADLB | ADL Bathroom | Allied Health | FFE | FIRT-105 | GRAB RAIL: 90 degree | 1 | 1 |  | [FIRT-048]
ADLB | ADL Bathroom | Allied Health | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 3 |  | [FIRT-006] 1 is optional, dependent on service requirements
ADLB | ADL Bathroom | Allied Health | FFE | FIRT-136 | GRAB RAIL: toilet, drop down | 1 | 3 |  | [FIRT-008] optional, dependent on service requirements and expected patient cohort
ADLB | ADL Bathroom | Allied Health | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 1 | 1 |  | [FIRT-003] may be combined with rail for hand held shower
ADLB | ADL Bathroom | Allied Health | FFE | FIRT-173 | GRAB RAIL: bath, straight, vertical | 1 | 1 |  | [FIRT-044]
ADLB | ADL Bathroom | Allied Health | FIN | FLGE-151 | SHOWER HOB: integrated with adjacent floor finish, vinyl | 1 | 3 | Floor Finish 2 | [FLGE-019] optional
ADLB | ADL Bathroom | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ADLB | ADL Bathroom | Allied Health | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] significant change in colour from adjacent corridor to be avoided, to be suitable for bare feet, tiles are also acceptable
ADLB | ADL Bathroom | Allied Health | FFE | FQGE-102 | CURTAIN: shower | 2 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ADLB | ADL Bathroom | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
ADLB | ADL Bathroom | Allied Health | FFE | FQWS-331 | BIN: sanitary waste | 1 | 3 |  | [FQCW-037] optional, dependent on waste management policy
ADLB | ADL Bathroom | Allied Health | FFE | HYBA-201 | BATH: domestic, built-in, straight | 1 | 1 |  | [HYBA-025] warm water
ADLB | ADL Bathroom | Allied Health | SER | HYDR-021 | DRAIN: floor waste, round | 2 | 1 |  | [HYDR-004]
ADLB | ADL Bathroom | Allied Health | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | [HYTP-020] to shower, vertical rail to have grabrail strength and fixings
ADLB | ADL Bathroom | Allied Health | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | [HYTP-021] to bath, vertical rail to have grabrail strength and fixings
ADLB | ADL Bathroom | Allied Health | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
ADLB | ADL Bathroom | Allied Health | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039] diverter required for shower over bath
ADLB | ADL Bathroom | Allied Health | FFE | HYTP-331 | TAPWARE: bath, spout, wall mounted | 1 | 1 |  | [HYTP-028]
ADLB | ADL Bathroom | Allied Health | FFE | HYWC-031 | TOILET SUITE: patient | 1 | 3 |  | [HYWC-006] 100mm clearout access point optional
ADLB | ADL Bathroom | Allied Health | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 3 | 3 |  | [ITCL-006] optional; + indicator button & light
ADLB | ADL Bathroom | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light
ADLB | ADL Bathroom | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
ADLB | ADL Bathroom | Allied Health | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | [MMGE-024] commode chair or combined shower/commode chair is also acceptable
ADLB | ADL Bathroom | Allied Health | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles also acceptable
ADLB | ADL Bathroom | Allied Health | FFE | HYBA-143 | BASIN: type C, handwashing, with integral double shelf | 1 | 1 |  | [HYBA-002] shelf for patient belongings may be integral or separate
ADLB | ADL Bathroom | Allied Health | FFE | MMBE-038 | TRANSFER AID: bench seat, patient self-assist transfer and positioning, freestanding | 1 | 1 |  | [FQBS-008] for over bath
ADLB | ADL Bathroom | Allied Health | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-034] optional, dependent on infection control policy
ADLB | ADL Bathroom | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ADLD | ADL Dining | Allied Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004]
ADLD | ADL Dining | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
ADLD | ADL Dining | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
ADLD | ADL Dining | Allied Health | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
ADLD | ADL Dining | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
ADLD | ADL Dining | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ADLD | ADL Dining | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
ADLD | ADL Dining | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
ADLD | ADL Dining | Allied Health | FFE | FQBS-151 | CHAIR: dining areas | 3 | 1 |  | [FQBS-015]
ADLD | ADL Dining | Allied Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1 |  | [FQGE-002]
ADLD | ADL Dining | Allied Health | FFE | FQTA-226.05 | TABLE: square, 750H nom, 1000L, adjustable height | 1 | 1 |  | [FQTA-085] height adjustable between 750-850H
ADLD | ADL Dining | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLD | ADL Dining | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLD | ADL Dining | Allied Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
ADLD | ADL Dining | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
ADLD | ADL Dining | Allied Health | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022]
ADLD | ADL Dining | Allied Health | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006]
ADLD | ADL Dining | Allied Health | D+W | WIFX-057.01 | WINDOW: fixed, internal, double glazed, sill at 900H | 1 | 1 | Internal - Window 1 | [DWWH-005] desirable
ADLK | ADL Kitchen | Allied Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004]
ADLK | ADL Kitchen | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
ADLK | ADL Kitchen | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
ADLK | ADL Kitchen | Allied Health | SER | ELGE-001 | DIRECT CONNECTION: power | 2 | 1 |  | [ELGE-001] to cooktop and oven
ADLK | ADL Kitchen | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
ADLK | ADL Kitchen | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ADLK | ADL Kitchen | Allied Health | SER | ELSW-101 | SWITCH: isolation | 1 | 1 |  | [ELBO-007] to cooktop and oven
ADLK | ADL Kitchen | Allied Health | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
ADLK | ADL Kitchen | Allied Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
ADLK | ADL Kitchen | Allied Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
ADLK | ADL Kitchen | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting | [FLSK-010]
ADLK | ADL Kitchen | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent around sink
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 1 | 1 |  | [FQCA-067] on bench
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-121 | APPLIANCE: toaster, benchtop, domestic | 1 | 1 |  | [FQCA-080]
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-141 | APPLIANCE: kettle, electric, benchtop, domestic | 1 | 1 |  | [FQCA-046]
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-272 | COOKTOP: electric, induction, domestic | 1 | 1 |  | [FQCA-089] controls to be located close to front
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-321 | RANGEHOOD: electric, domestic | 1 | 1 |  | [FQCA-072] over cooktop
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-341 | OVEN: electric, domestic | 1 | 1 |  | [FQCA-063] retractable/side opening doors
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-402 | FRIDGE: domestic, 300L nom, single door | 1 | 1 |  | [FQCA-031]
ADLK | ADL Kitchen | Allied Health | FFE | FQSM-051 | PEDESTAL: mobile, 660H nominal, 2 equal wire basket drawers | 1 | 1 |  | [FQSM-040] under bench
ADLK | ADL Kitchen | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
ADLK | ADL Kitchen | Allied Health | FFE | HYBA-323 | SINK: 1 1/2 bowl, with drainer | 1 | 1 |  | [HYBA-041] heat lined, warm water
ADLK | ADL Kitchen | Allied Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
ADLK | ADL Kitchen | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-020]
ADLK | ADL Kitchen | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-059]
ADLK | ADL Kitchen | Allied Health | FFE | JOBE-221 | BENCH SUPPORT: end panel | 3 | 1 |  | [FIJO-213]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-131]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-051 | CUPBOARD: tall, with built in oven | 1 | 1 |  | [FIJO-223]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 2 | 1 |  | [FIJO-156]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-143]
ADLK | ADL Kitchen | Allied Health | FFE | JODW-001 | DRAWER: under bench, single | 6 | 1 |  | [FIJO-205]
ADLK | ADL Kitchen | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
ADLK | ADL Kitchen | Allied Health | FFE | JOGE-011 | PANEL: fixed, infill | 5 | 1 |  | [FIJO-224] to sink and cooktop
ADLK | ADL Kitchen | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
ADLK | ADL Kitchen | Allied Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-007]
ADLK | ADL Kitchen | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | [ELGP-208]
ADLK | ADL Kitchen | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109] to range hood and fridge
ADLK | ADL Kitchen | Allied Health | D+W | WIFX-161.01 | WINDOW: fixed, external, double glazed, sill at 1500H | 1 | 1 | Internal - Window 1 | [DWWH-005] desirable
ADLL | ADL Laundry | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ADLL | ADL Laundry | Allied Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional
ADLL | ADL Laundry | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
ADLL | ADL Laundry | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
ADLL | ADL Laundry | Allied Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
ADLL | ADL Laundry | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006] type 1 10mA in accordance with AS/NZS 3003
ADLL | ADL Laundry | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ADLL | ADL Laundry | Allied Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
ADLL | ADL Laundry | Allied Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
ADLL | ADL Laundry | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
ADLL | ADL Laundry | Allied Health | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-101 | WASHING MACHINE: laundry, domestic, front loading | 1 | 1 |  | [FQCW-063]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-111 | DRYER: laundry, domestic | 1 | 1 |  | [FQGE-015]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-121 | PLINTH: washing machine, domestic | 2 | 1 |  | [MMAH-039]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-152 | APPLIANCE: iron, laundry, electric, domestic | 1 | 1 |  | [FQGE-028]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-186 | TROLLEY: laundry basket | 1 | 3 |  | [FQSM-030] optional
ADLL | ADL Laundry | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
ADLL | ADL Laundry | Allied Health | FFE | HYBA-411 | SINK: laundry, single bowl | 1 | 1 |  | [HYBA-064] with overflow drain, warm water
ADLL | ADL Laundry | Allied Health | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
ADLL | ADL Laundry | Allied Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
ADLL | ADL Laundry | Allied Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] to washing machine
ADLL | ADL Laundry | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLL | ADL Laundry | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLL | ADL Laundry | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059] with inset laundry tub
ADLL | ADL Laundry | Allied Health | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-222]
ADLL | ADL Laundry | Allied Health | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 1 | 1 |  | [FIJO-156]
ADLL | ADL Laundry | Allied Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-135]
ADLL | ADL Laundry | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
ADLL | ADL Laundry | Allied Health | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
ADLL | ADL Laundry | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
ADLL | ADL Laundry | Allied Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007]
ADLL | ADL Laundry | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] 30mA RCD protection
ADLL | ADL Laundry | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to washing machine and dryer
ADLL | ADL Laundry | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
AHBF | After Hours Blood Fridge | Pathology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
AHBF | After Hours Blood Fridge | Pathology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
AHBF | After Hours Blood Fridge | Pathology | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
AHBF | After Hours Blood Fridge | Pathology | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-003] optional, to laboratory if adjacent
AHBF | After Hours Blood Fridge | Pathology | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
AHBF | After Hours Blood Fridge | Pathology | SER | ELGP-131.01 | GPO: single, emergency power, wall mounted, horizontal | 1 | 1 |  | [ELGP-123] to fridge
AHBF | After Hours Blood Fridge | Pathology | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
AHBF | After Hours Blood Fridge | Pathology | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
AHBF | After Hours Blood Fridge | Pathology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
AHBF | After Hours Blood Fridge | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
AHBF | After Hours Blood Fridge | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
AHBF | After Hours Blood Fridge | Pathology | SER | ITBU-401 | ALARM: equipment monitoring, temperature | 1 | 1 |  | [ITBU-001] may be integral to fridge
AHBF | After Hours Blood Fridge | Pathology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to fridge for temperature monitoring
AHBF | After Hours Blood Fridge | Pathology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
AHBF | After Hours Blood Fridge | Pathology | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
AHBF | After Hours Blood Fridge | Pathology | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 1 |  | [ITNE-003]
AHBF | After Hours Blood Fridge | Pathology | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-017] laboratory grade
AHBF | After Hours Blood Fridge | Pathology | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213]
AHBF | After Hours Blood Fridge | Pathology | FFE | MMLA-212 | FRIDGE: blood, 200L nom, single door | 1 | 1 |  | [MMLA-053] sections may be lockable; BMS monitored, audible alarm 24hr; size is to suit service requirements
AHBF | After Hours Blood Fridge | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
AHBF | After Hours Blood Fridge | Pathology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
AHBF | After Hours Blood Fridge | Pathology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
AHBF | After Hours Blood Fridge | Pathology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
AHBF | After Hours Blood Fridge | Pathology | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
AHBF | After Hours Blood Fridge | Pathology | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 2 | [ITSE-038] optional
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] to corridor
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-007] optional, to pharmacy if room located with direct access
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | FQSM-211 | SHELVING UNIT: mobile, adjustable shelves, 600D x 400W x 2100H nominal | 2 | 1 |  | [FQSM-045] storage solution/mix of storage options to be tailored to suit project requirements
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to drug fridge, for temperature monitoring
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 3 |  | [ITSE-006] optional
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 3 |  | [ITSE-012] optional, provision and placement dependent on local policies
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | MMPH-021 | FRIDGE: medication/vaccine, 150L nom, single door, under bench | 1 | 1 |  | [MMGE-036]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to drug fridge
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to pharmacy side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 2 | [ITSE-038]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | FLSK-031 | SKIRTING: aluminium, concealed fixing | 1 | 1 | Floor Skirting | [FLSK-008]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 3 | [CLFS-006]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | [CLGE-001] to external door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | [CLGE-001] to internal door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | FLGE-081 | FLOOR FINISH: entrance matting, recessed, indoor | 1 | 1 | Floor Finish 2 | [FLGE-016]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AFWFI-022 | WINDOW FINISH: decal | 1 | 1 | Internal - Door 1 | to fixed glazed panel, high visibility for safety and luminance contrast requirements
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AFWFI-022 | WINDOW FINISH: decal | 1 | 1 | External - Door 1 | to fixed glazed panel, high visibility for safety and luminance contrast requirements
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDMO-011 | DOOR MOTORISATION: stacking, 1 leaf | 1 | 1 | Internal - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDMO-011 | DOOR MOTORISATION: stacking, 1 leaf | 1 | 1 | External - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-012 | DOOR SENSOR: door activation, motion detection, integral to frame | 1 | 1 | Internal - Door 1 | to adjacent internal area
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-015 | DOOR SENSOR: door activation, motion detection, ceiling mounted | 1 | 1 | Internal - Door 1 | inside airlock
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-012 | DOOR SENSOR: door activation, motion detection, integral to frame | 1 | 1 | External - Door 1 | to adjacent external area
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-015 | DOOR SENSOR: door activation, motion detection, ceiling mounted | 1 | 1 | External - Door 1 | inside airlock
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | ITSE-266 | READER: security, access control, proximity card, outdoor, wall mounted | 1 | 1 | External - Door 1 | [ITSE-050] as required for access and security to suit operational policies; may be integral to intercom
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-051] inside airlock, to enter after hours
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-051] to adjacent internal area, to exit after hours
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-101 | DOOR CONTROL: key switch, mode selection, automatic door | 1 | 1 | External - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-101 | DOOR CONTROL: key switch, mode selection, automatic door | 1 | 1 | Internal - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | External - Door 1 | [ITSE-051] inside airlock, to exit after hours
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | DOST-312.01 | DOOR: stacking, bi-parting, 2 leaves + 2 fixed panels, 1600 clear opening, fully glazed, framed with mid-rail | 1 | 1 | Internal - Door 1 | [DWGL-050] internal door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | DOST-312.01 | DOOR: stacking, bi-parting, 2 leaves + 2 fixed panels, 1600 clear opening, fully glazed, framed with mid-rail | 1 | 1 | External - Door 1 | [DWGL-050] external door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ITSE-191 | INTERCOM: audio-visual, slave, outdoor, wall mounted | 1 | 1 |  | [ITSE-049] as required for access control and security in line with local operational policies; may include integral swipe card reader; may be located to internal door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ITSE-301 | ALARM: door release, emergency, break glass, wall mounted | 1 | 1 |  | [ITSE-024]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125] to security camera
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | MESU-006 | AIR CURTAIN: external door | 1 | 3 |  | [MEEX-018] optional
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011] to security camera
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FFE | FIDI-055 | DISPENSER: umbrella cover, floor standing | 1 | 3 |  | [FIDI-055] optional
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 1 |  | [ITSE-012+FIHR-002] as required for access control and security in line with local operational policies
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | External - Door 1 | [ITSE-051] inside airlock, to exit after hours
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | DOST-019.01 | DOOR: stacking, 1 leaf + 1 fixed panel, 1200 clear opening, fully glazed, framed with mid-rail | 1 | 1 | Internal - Door 1 | [DWGL-026] internal door
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FFE | FIDI-055 | DISPENSER: umbrella cover, floor standing | 1 | 3 |  | [FIDI-055] optional
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | FLGE-081 | FLOOR FINISH: entrance matting, recessed, indoor | 1 | 1 | Floor Finish 2 | [FLGE-016]
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011] to security camera
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 1 |  | [ITSE-012+FIHR-002] as required for access control and security in line with local operational policies
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | SER | MESU-006 | AIR CURTAIN: external door | 1 | 3 |  | [MEEX-018] optional
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | FLSK-031 | SKIRTING: aluminium, concealed fixing | 1 | 1 | Floor Skirting | [FLSK-008]
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 3 | [CLFS-006]
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | DOST-019.01 | DOOR: stacking, 1 leaf + 1 fixed panel, 1200 clear opening, fully glazed, framed with mid-rail | 1 | 1 | External - Door 1 | [DWGL-026] external door
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AFWFI-022 | WINDOW FINISH: decal | 1 | 1 | Internal - Door 1 | to fixed glazed panel, high visibility for safety and luminance contrast requirements
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AFWFI-022 | WINDOW FINISH: decal | 1 | 1 | External - Door 1 | to fixed glazed panel, high visibility for safety and luminance contrast requirements
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDMO-011 | DOOR MOTORISATION: stacking, 1 leaf | 1 | 1 | Internal - Door 1
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDMO-011 | DOOR MOTORISATION: stacking, 1 leaf | 1 | 1 | External - Door 1
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDSS-012 | DOOR SENSOR: door activation, motion detection, integral to frame | 1 | 1 | Internal - Door 1 | to adjacent internal area
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDSS-015 | DOOR SENSOR: door activation, motion detection, ceiling mounted | 1 | 1 | Internal - Door 1 | inside airlock
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDSS-012 | DOOR SENSOR: door activation, motion detection, integral to frame | 1 | 1 | External - Door 1 | to adjacent external area
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDSS-015 | DOOR SENSOR: door activation, motion detection, ceiling mounted | 1 | 1 | External - Door 1 | inside airlock
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | ITSE-266 | READER: security, access control, proximity card, outdoor, wall mounted | 1 | 1 | External - Door 1 | [ITSE-050] as required for access and security to suit operational policies; may be integral to intercom
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | SER | ITSE-191 | INTERCOM: audio-visual, slave, outdoor, wall mounted | 1 | 1 |  | [ITSE-049] as required for access control and security in line with local operational policies; may include integral swipe card reader; may be located to internal door
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-051] inside airlock, to enter after hours
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-051] to adjacent internal area, to exit after hours
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | SER | ITSE-301 | ALARM: door release, emergency, break glass, wall mounted | 1 | 1 |  | [ITSE-024]
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | [CLGE-001] to external door
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | [CLGE-001] to internal door
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDEC-101 | DOOR CONTROL: key switch, mode selection, automatic door | 1 | 1 | External - Door 1
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | D+W | AHDEC-101 | DOOR CONTROL: key switch, mode selection, automatic door | 1 | 1 | Internal - Door 1
AIRLE-6 | Airlock - Entry, 6m2 | Public Areas | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125] to security camera
ANAES | Anaesthetic Preparation Room | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
ANAES | Anaesthetic Preparation Room | Operating | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
ANAES | Anaesthetic Preparation Room | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
ANAES | Anaesthetic Preparation Room | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ANAES | Anaesthetic Preparation Room | Operating | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ANAES | Anaesthetic Preparation Room | Operating | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2
ANAES | Anaesthetic Preparation Room | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ANAES | Anaesthetic Preparation Room | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | MGFP-051 | ADAPTER: scavenge | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITCL-211 | BUTTON: nurse call, orderly/porter, with cancel, wall mounted | 1 | 1 |  | optional - depending on operational processes
ANAES | Anaesthetic Preparation Room | Operating | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 3 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 3 | 1 |  | to bench
ANAES | Anaesthetic Preparation Room | Operating | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 1 | 1 |  | controlled from operating room
ANAES | Anaesthetic Preparation Room | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | controlled from operating room
ANAES | Anaesthetic Preparation Room | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to bench
ANAES | Anaesthetic Preparation Room | Operating | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to telephone
ANAES | Anaesthetic Preparation Room | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to operating room (see OR-GEN), cover required to vision panel if laser is to be used
ANAES | Anaesthetic Preparation Room | Operating | D+W | DOSL-212.01 | DOOR: sliding, bi-parting, 2 leaves, 1600 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | to corridor
ANAES | Anaesthetic Preparation Room | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
ANAES | Anaesthetic Preparation Room | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2
ANAES | Anaesthetic Preparation Room | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
ANAES | Anaesthetic Preparation Room | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
ANAES | Anaesthetic Preparation Room | Operating | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-237 | BIN: clinical waste, 120L | 1 | 1 |  | optional - provision dependent on waste management policy
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-072 | BIN: recycling, commingled, 30L | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | computer may alternatively be on a bench top or wall mounted
ANAES | Anaesthetic Preparation Room | Operating | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | LIFX-121 | LIGHT: procedure, minor, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | a recessed ceiling examination light may be provided in lieu of small procedure light to suit service requirements
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMOP-161 | MACHINE: anaesthetic | 1 | 1 |  | optional - may be provided within the anaesthetic preparation room or within the operating room (see OR-GEN)
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 5 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | optional - drug safe may alternatively be located in the operating room; with card reader, safe location and type of medication stored is dependent on the operational policies and medication management regulations in different jurisdictions
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | HYTP-076 | TAPWARE: basin, sensor, wall mounted | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
ANAES | Anaesthetic Preparation Room | Operating | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | MMTR-013.01 | TROLLEY: stainless steel, wire mesh drawers, 900W x 490D x 900H nom, 3 drawers | 3 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | FIDI-251 | DISPENSER: alcohol-based hand rub, surgical, antimicrobial, chlorhexidine, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | Operating | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | flush to wall
ANAES | Anaesthetic Preparation Room | Operating | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | Operating | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
ANAES | Anaesthetic Preparation Room | Operating | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ANTE | Anteroom | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ANTE | Anteroom | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
ANTE | Anteroom | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ANTE | Anteroom | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ANTE | Anteroom | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
ANTE | Anteroom | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
ANTE | Anteroom | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ANTE | Anteroom | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor
ANTE | Anteroom | Inpatient Accommodation | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1
ANTE | Anteroom | Inpatient Accommodation | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 2
ANTE | Anteroom | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to bedroom
ANTE | Anteroom | Inpatient Accommodation | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1
ANTE | Anteroom | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ANTE | Anteroom | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ANTE | Anteroom | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ANTE | Anteroom | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
ANTE | Anteroom | Inpatient Accommodation | FFE | FIDI-271 | DISPENSER: moisturiser, wall mounted | 1 | 1
ANTE | Anteroom | Inpatient Accommodation | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | optional, provision dependent on PPE requirements
ANTE | Anteroom | Inpatient Accommodation | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ANTE | Anteroom | Inpatient Accommodation | FFE | FQSN-152 | STORAGE SOLUTION: modular system, floor standing, 400D x 600W x 2100H nominal | 1 | 1 |  | type, configuration and extent of storage to be confirmed to suit clinical service requirements, operational models and local IPC policies
ANTE | Anteroom | Inpatient Accommodation | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
ANTE | Anteroom | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
ANTE | Anteroom | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | basin and tapware selection to be coordinated to ensure compatibility
ANTE | Anteroom | Inpatient Accommodation | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | with intercom function to patient handset in adjacent isolation room
ANTE | Anteroom | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 1 | 1
ANTE | Anteroom | Inpatient Accommodation | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
ANTE | Anteroom | Inpatient Accommodation | D+W | AHDEC-111 | DOOR CONTROL: connection, interlocking system | 1 | 1 | Internal - Door 1 | to ensure door is closed before the door to the bedroom is opened and vice versa
ANTE | Anteroom | Inpatient Accommodation | D+W | AHDEC-111 | DOOR CONTROL: connection, interlocking system | 1 | 1 | Internal - Door 2 | to ensure door is closed before the door to the corridor is opened and vice versa
ANTE | Anteroom | Inpatient Accommodation | D+W | ITSE-301 | ALARM: door release, emergency, break glass, wall mounted | 1 | 1 | Internal - Door 1 | for override of interlock system and release of corridor door to mitigate risk of staff entrapment
ANTE | Anteroom | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ANTE | Anteroom | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ANTE | Anteroom | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ANTE | Anteroom | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
ANTE | Anteroom | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
AUD-CR | Audiology Control Room | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 2 | 1 | Internal - Door 1 | [DWPR-001] to control room side
AUD-CR | Audiology Control Room | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
AUD-CR | Audiology Control Room | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
AUD-CR | Audiology Control Room | Allied Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 2 | 1 | Internal - Door 1 | [DWGL-005] to corridor
AUD-CR | Audiology Control Room | Allied Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
AUD-CR | Audiology Control Room | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
AUD-CR | Audiology Control Room | Allied Health | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
AUD-CR | Audiology Control Room | Allied Health | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
AUD-CR | Audiology Control Room | Allied Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
AUD-CR | Audiology Control Room | Allied Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
AUD-CR | Audiology Control Room | Allied Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
AUD-CR | Audiology Control Room | Allied Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 6 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
AUD-CR | Audiology Control Room | Allied Health | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
AUD-CR | Audiology Control Room | Allied Health | FFE | FQDW-134.04 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1600W | 1 | 1 |  | [FQDW-031]
AUD-CR | Audiology Control Room | Allied Health | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007]
AUD-CR | Audiology Control Room | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
AUD-CR | Audiology Control Room | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
AUD-CR | Audiology Control Room | Allied Health | SER | ITIN-151 | AV PANEL: power and data outlets, wall mounted | 1 | 3 |  | [MMSP-032] optional
AUD-CR | Audiology Control Room | Allied Health | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
AUD-CR | Audiology Control Room | Allied Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | [ITNE-007] optional
AUD-CR | Audiology Control Room | Allied Health | FFE | MMAH-201 | BOOTH: audiometric, integrated system | 1 | 1 |  | [MMAH-005] one way window (non-reflective); acoustic seals to suit testing requirements
AUD-CR | Audiology Control Room | Allied Health | FFE | MMAH-211 | CONTROL CONSOLE: audiology, audiometric booth | 1 | 3 |  | [MMAH-036] optional, dependent on service requirements
AUD-CR | Audiology Control Room | Allied Health | FFE | MMAH-216 | DEVICE: audiology, tympanometer | 1 | 1 |  | [MMAH-042]
AUD-CR | Audiology Control Room | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
AUD-CR | Audiology Control Room | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] provision of emergency power to be determined based on service requirements
AUD-CR | Audiology Control Room | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
AUD-CR | Audiology Control Room | Allied Health | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 2 | [DWGL-005] to testing room, acoustic seals to suit testing requirements
AUD-CR | Audiology Control Room | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-001] to control room side
AUD-CR | Audiology Control Room | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-001] to testing room side
AUD-TR | Audiology Testing Room | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to testing room side
AUD-TR | Audiology Testing Room | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
AUD-TR | Audiology Testing Room | Allied Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] acoustic seals to suit testing requirements
AUD-TR | Audiology Testing Room | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
AUD-TR | Audiology Testing Room | Allied Health | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029] for headphones
AUD-TR | Audiology Testing Room | Allied Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-161 | CHAIR: play areas, child | 1 | 1 |  | [FQBS-012]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1 |  | [FQDW-001]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQTA-096 | TABLE: play areas, child | 1 | 1 |  | [FQTA-003]
AUD-TR | Audiology Testing Room | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
AUD-TR | Audiology Testing Room | Allied Health | SER | ITIN-151 | AV PANEL: power and data outlets, wall mounted | 4 | 3 |  | [MMSP-032] optional, as required for remote operation of equipment
AUD-TR | Audiology Testing Room | Allied Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
AUD-TR | Audiology Testing Room | Allied Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
AUD-TR | Audiology Testing Room | Allied Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-145]
AUD-TR | Audiology Testing Room | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-201 | BOOTH: audiometric, integrated system | 1 | 1 |  | [MMAH-005] with one way window (non-reflective)
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-207 | SPEAKER: audiology, wall mounted | 2 | 1 |  | [ITAV-061] wall mounted, calibrated for testing space
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-211 | CONTROL CONSOLE: audiology, audiometric booth | 1 | 1 |  | [MMAH-036]
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-217 | DEVICE: audiology, visual reinforcement audiometry | 2 | 1 |  | [MMAH-043] wall mounted, may be provided as a screen or puppet box, inclusion is dependent on service requirements
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-251 | ARMCHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-039]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1 |  | [FQBS-014]
AUD-TR | Audiology Testing Room | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208] provision of emergency power to be determined based on service requirements
AUD-TR | Audiology Testing Room | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to control room side
BATH | Bathroom | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
BATH | Bathroom | Sanitary Facilities | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021] privacy latch
BATH | Bathroom | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
BATH | Bathroom | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] over basin
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1 |  | [FIDI-049] soap dispenser is also acceptable, to shower
BATH | Bathroom | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-191 | BACK REST: toilet, accessible | 1 | 1 |  | [FIGE-011]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-166 | GRAB RAIL: shower, T-shaped, vertical and horizontal | 1 | 1 |  | [FIRT-045] with bracket for hand held accessible shower mounted on vertical rail
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-206 | RAIL: towel, wall mounted | 1 | 1 |  | [FIRT-016] with grab rail strength/fixings
BATH | Bathroom | Sanitary Facilities | FFE | FQGE-102 | CURTAIN: shower | 2 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
BATH | Bathroom | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
BATH | Bathroom | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
BATH | Bathroom | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 2 | 1 |  | [HYDR-004] special floor drain required if height adjustable bath provided
BATH | Bathroom | Sanitary Facilities | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | [HYTP-020]
BATH | Bathroom | Sanitary Facilities | FFE | HYSH-057 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail, accessible | 1 | 1 |  | [HYTP-045]
BATH | Bathroom | Sanitary Facilities | FFE | HYTP-052 | TAPWARE: basin, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-035] selection of basin and tapware to be coordinated to ensure compatibility
BATH | Bathroom | Sanitary Facilities | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039]
BATH | Bathroom | Sanitary Facilities | FFE | HYWC-033 | TOILET SUITE: patient, accessible | 1 | 1 |  | [HYWC-001]
BATH | Bathroom | Sanitary Facilities | FFE | MMBE-161 | TROLLEY: patient, shower, hydraulic | 1 | 1 |  | [FQSM-033] height adjustable bath is also acceptable
BATH | Bathroom | Sanitary Facilities | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | [MMGE-024] commode chair is also acceptable
BATH | Bathroom | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
BATH | Bathroom | Sanitary Facilities | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
BATH | Bathroom | Sanitary Facilities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
BATH | Bathroom | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
BATH | Bathroom | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
BATH | Bathroom | Sanitary Facilities | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable
BATH | Bathroom | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-138 | GRAB RAIL: toilet, drop down, with bracket for nurse call button | 1 | 1 |  | [FIRT-008]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-137 | GRAB RAIL: toilet, drop down, with holder for toilet roll | 1 | 1 |  | [FIRT-008]
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-308 | DISPENSER: toilet paper, to drop-down grab rail | 1 | 1 |  | [FIRT-008]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-061 | TRACK: curtain, shower | 2 | 3 |  | [FIRT-034] 1 to entry door, 1 to shower; optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
BATH | Bathroom | Sanitary Facilities | FFE | HYBA-148 | BASIN: type C, handwashing, accessible, with integral double shelf | 1 | 1 |  | [HYBA-005] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-153 | GRAB RAIL: shower, straight, vertical | 1 | 1 |  | with bracket for hand held shower mounted on vertical rail
BATH | Bathroom | Sanitary Facilities | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-004] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 0 | 1 |  | [ITCL-008] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-006] IPX4 rating required; to shower
BATH | Bathroom | Sanitary Facilities | SER | ITCL-130 | BUTTON: nurse call, patient to staff call, with cancel, to drop-down grab rail, wet area | 1 | 1 |  | [ITCL-006] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to shower
BATH | Bathroom | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to shower
BATH | Bathroom | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
BATH | Bathroom | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
BBEV | Bay - Beverage | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, lighting and controls to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10/pendulum P3 or agreed equivalent around sink; coordinated with adjacent area, significant change in colour to be avoided
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 1 | 1 |  | [FQCA-067]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQCA-231 | ICE MACHINE: commercial, benchtop | 1 | 3 |  | [FQCA-015] optional; item to comply with infection control requirements
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQCA-402 | FRIDGE: domestic, 300L nom, single door | 1 | 1 |  | [FQCA-032] clear area for fridge to allow for adequate ventilation and full opening of door
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] size, type and quantity of bins dependent on local waste management policies
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | [FQCW-062] size, type and quantity of bins dependent on local waste management policies
BBEV | Bay - Beverage | Logistics / Support Services | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | [HYBA-080]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | [HYGE-003] + [HYTP-029] instant hot/cold water tap to sink; provide grille in joinery for ventilation
BBEV | Bay - Beverage | Logistics / Support Services | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] to boiling/ chilled water unit
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-069] minimum depth 600mm; where an ice machine is provided the depth may need to increase to accommodate
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOCU-041 | CUPBOARD: tall, with 1 microwave shelf unit | 1 | 1 |  | [FIJO-163]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 3 |  | [FIJO-143] optional; configuration of joinery to meet storage requirements
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 2 | 1 |  | [FIJO-104]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | [FIJO-212] optional, provide if wall mounted joinery provided, plasterboard bulkhead is also acceptable
BBEV | Bay - Beverage | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BBEV | Bay - Beverage | Logistics / Support Services | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-007] to back of bench and return wall
BBEV | Bay - Beverage | Logistics / Support Services | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | [WLPR-010] coordinated with adjacent wall protection
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
BBEV | Bay - Beverage | Logistics / Support Services | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] over bench
BBEV | Bay - Beverage | Logistics / Support Services | SER | ELGP-101 | GPO: single, wall mounted | 3 | 1 |  | [ELGP-109] 1 to fridge, 1 to microwave, 1 to boiling/ chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | to be coordinated with adjacent area
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | 1 to fridge, 1 to boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | optional; to be coordinated with lighting controls for adjacent area
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQCA-401 | FRIDGE: domestic, 120L nom, single door, under bench | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | size, type and quantity of waste bins will be dependent on service requirements and operational models for waste management
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | size, type and quantity of waste bins will be dependent on service requirements and operational models for waste management
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | filter unit to be in lockable cupboard; ventilation requirements to be confirmed to suit selection
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | optional; extent of storage to be confirmed to suit service requirements; lockable
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | lockable; confirm ventilation requirements for boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 2 | 1 |  | lockable
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | optional; to wall mounted cupboards if provided
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | to boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 1 | 1 | Wall Finish 3 | to be coordinated with adjacent wall protection
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink tapware
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
BBLD | Bay - Blood Fridge | Pathology | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] coordinated with adjacent area
BBLD | Bay - Blood Fridge | Pathology | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
BBLD | Bay - Blood Fridge | Pathology | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] coordinated with adjacent area
BBLD | Bay - Blood Fridge | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BBLD | Bay - Blood Fridge | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BBLD | Bay - Blood Fridge | Pathology | SER | ITBU-401 | ALARM: equipment monitoring, temperature | 2 | 1 |  | [ITBU-001] may be integral to fridge
BBLD | Bay - Blood Fridge | Pathology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016] for temperature monitoring
BBLD | Bay - Blood Fridge | Pathology | FFE | MMLA-212 | FRIDGE: blood, 200L nom, single door | 2 | 1 |  | [MMLA-053] sections may be lockable; BMS monitored, audible alarm 24hr; quantity and size is to suit service requirements
BBLD | Bay - Blood Fridge | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BBLD | Bay - Blood Fridge | Pathology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BBLD | Bay - Blood Fridge | Pathology | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123.1]
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided; coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] flush set ceiling is also acceptable; to be coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional; provide for connection to BMS where temperature monitoring required for fluids; alternative connection may be required depending on BMS or equipment requirements
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FFE | MMGE-473 | CABINET: fluid/blanket warmer, floor standing | 1 | 1 |  | [MMGE-010] for fluids only, blankets only or a combination of fluids and blankets; configuration to suit service requirements
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BBW | Bay - Blanket / Fluid Warmer | Perioperative | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
BES | Bay - Emergency Shower | Pathology | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] coordinated with adjacent area
BES | Bay - Emergency Shower | Pathology | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
BES | Bay - Emergency Shower | Pathology | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
BES | Bay - Emergency Shower | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
BES | Bay - Emergency Shower | Pathology | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
BES | Bay - Emergency Shower | Pathology | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
BES | Bay - Emergency Shower | Pathology | FFE | HYSH-111 | STATION: emergency, safety, shower and eye wash, wall mounted | 1 | 1 |  | [HYTP-023]
BES | Bay - Emergency Shower | Pathology | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | [WLWA-019]
BES | Bay - Emergency Shower | Pathology | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | [WLPR-011] coordinated with adjacent wall protection
BES | Bay - Emergency Shower | Pathology | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to shower and eye wash station
BHW | Bay - Height/ Weight | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BHW | Bay - Height/ Weight | Ambulatory Care | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BHW | Bay - Height/ Weight | Ambulatory Care | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208]
BHW | Bay - Height/ Weight | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BHW | Bay - Height/ Weight | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BHW | Bay - Height/ Weight | Ambulatory Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, dependent on equipment requirements
BHW | Bay - Height/ Weight | Ambulatory Care | FFE | MMGE-207 | SCALES: digital, standing, with stadiometer | 1 | 1 |  | [MMGE-188] bariatric capacity will be dependent on service requirements; stadiometer may be separate wall mounted or floor standing item; scales may include integral grab rails for support
BHW | Bay - Height/ Weight | Ambulatory Care | FFE | MMGE-211 | SCALES: digital, chair | 1 | 3 |  | [MMGE-089] optional, dependent on service requirements
BHW | Bay - Height/ Weight | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BHW | Bay - Height/ Weight | Ambulatory Care | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022] height dependent on type and height of mobile equipment, crash rails are also acceptable
BHW | Bay - Height/ Weight | Ambulatory Care | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] coordinated with adjacent area
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] drop-in ceiling tiles are also acceptable; to be coordinated with adjacent area
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | [FLVY-003] floor finish of adjacent area may continue under basin but must have a minimum slip rating R10/pendulum P3 or agreed equivalent or an inset section of non-slip vinyl is required; significant change in colour to be avoided.
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | WLFI-101 | SPLASHBACK: vinyl | 3 | 1 | Wall Finish 2 | [WLWA-007]
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] if bay is recessed
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
BHWS-A | Bay - Handwashing, Type A | Clinical Support Set 1 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] coordinated with adjacent area
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] drop-in ceiling tiles are also acceptable; to be coordinated with adjacent area
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 3 |  | [FIDI-031] optional, dependent on service requirements
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | [FLVY-003] floor finish of adjacent area may continue under basin but must have a minimum slip rating R10/pendulum P3 or agreed equivalent or an inset section of non-slip vinyl is required; significant change in colour to be avoided.
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | WLFI-101 | SPLASHBACK: vinyl | 3 | 1 | Wall Finish 2 | [WLWA-007]
BHWS-B | Bay - Handwashing, Type B | Clinical Support Set 1 | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] if bay is recessed
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] low level for patient bed
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ELGP-106.01 | GPO: single, ceiling mounted, horizontal | 1 | 1 |  | [ELGP-101] to patient entertainment system
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ELGP-131.01 | GPO: single, emergency power, wall mounted, horizontal | 1 | 1 |  | [ELGP-123]
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] 2 to staff write-up, 1 to lounge
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | [ELBO-012] 1 to entry door, 1 to staff write up for general room lights
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1 |  | [FIDI-014]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-019]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIDI-247 | HOLDER: alcohol-based hand rub, bed mounted | 1 | 1 |  | [FIHR-068]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019] 1 to bedhead cupboard, 1 to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016] mounted on trolley
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019] to staff write-up
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051] for suturing and small procedures
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQBS-372 | SOFA BED: 2 seat | 1 | 1 |  | [FQBS-044]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1 |  | [FQSN-051] type and extent of storage for patient property to suit operational policies
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to staff write-up for wall mounted phone
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to staff write-up
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment system, may be replaced with data outlet depending on ICT policies
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | [ITNE-049] optional, to patient locker
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053] to staff write-up
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] to staff write-up, dual monitors may be provided as required to suit operational, EMR and ICT requirements; a workstation on wheels is also acceptable
BIRM-A | Birthing Room, Without Pool | Maternity | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] to staff write-up
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-020]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213] below FIJO-156 to separate dirty linen trolley from hand wash, storage for clean and dirty linen to suit local operational policies
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099] to staff write-up bench
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-129] type and extent of storage to suit service requirements
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOCU-006 | CUPBOARD: tall, single door, for medical services panel | 1 | 1 |  | [FIJO-162]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 1 | 1 |  | [FIJO-156]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-145] to staff write-up
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | [FIJO-209] wardrobe, type and extent of storage for patient property to suit operational policies
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOGE-001 | BULKHEAD: joinery | 3 | 1 |  | [FIJO-212]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOSH-401 | SHELF: wall mounted, laminate | 2 | 1 |  | [FIJO-194] to equipment store cupboard, type and quantity of storage options to be determined based on service requirements
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | JOSP-001 | JOINERY UNIT: bespoke, birthing, tall, infant resuscitaire storage | 1 | 1 |  | [FIJO-233] Configuration of joinery to suit resuscitare equipment selected, including consideration of maneuverability and provision of sufficient space for emergency resuscitation procedures. Confirm design with users at project level.
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
BIRM-A | Birthing Room, Without Pool | Maternity | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | [LIFX-017] to bedhead
BIRM-A | Birthing Room, Without Pool | Maternity | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011] to bedhead
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMBE-126 | BED: patient, electric, with mattress, birthing | 1 | 1 |  | [MMBE-005]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100] 1 to bedhead cupboard, 1 to infant resuscitaire cupboard
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMMA-031 | BASSINET: infant, mobile | 1 | 3 |  | [FQBS-001] optional
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMMA-051 | DEVICE: patient, fetal, cardiotocography (CTG) | 1 | 1 |  | [MMMA-031] to equipment store cupboard
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMMA-061 | RESUSCITAIRE: infant, mobile | 1 | 1 |  | [MMMA-015] Mobile resuscitaire shown. Item may be wall mounted where suitable product is available.
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMMA-116 | SUPPORT FIXTURE: birthing, ladder, wall mounted | 1 | 1 |  | [MMMA-041]
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMMA-121 | SUPPORT FIXTURE: birthing, hook, ceiling mounted | 1 | 3 |  | [MMMA-043] optional, provision dependent on birthing aids/supportive equipment to be used
BIRM-A | Birthing Room, Without Pool | Maternity | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1 |  | [FQSM-016] to equipment store cupboard
BIRM-A | Birthing Room, Without Pool | Maternity | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
BIRM-A | Birthing Room, Without Pool | Maternity | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
BIRM-A | Birthing Room, Without Pool | Maternity | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
BIRM-A | Birthing Room, Without Pool | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
BIRM-A | Birthing Room, Without Pool | Maternity | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005]
BIRM-A | Birthing Room, Without Pool | Maternity | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 1 | [DWWD-004]
BIRM-A | Birthing Room, Without Pool | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
BIRM-A | Birthing Room, Without Pool | Maternity | D+W | DOFD-301 | DOOR: folding, bi-parting, 4 leaves, 1800 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWGE-017] to equipment storage area
BIRM-A | Birthing Room, Without Pool | Maternity | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] with hold open device to support bed movement as required
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006]
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-010] to basin
BIRM-A | Birthing Room, Without Pool | Maternity | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-002]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | [ELBO-015] to reading light
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 2 | [MGAS-022]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 3 | [MGAS-022]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 2 | [MGAS-032]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 2 | [MGAS-042]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 3 | [MGAS-042]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 2 | [MGAS-053]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2 | [MGAS-062]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 3 | [MGAS-062]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 3 | [MGFP-002]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2 | [MGFP-004]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 3 | [MGFP-004]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2 | [ELPR-006]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 2 | [MGFP-002]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Panel 1 | [ITCL-028]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] with indicator button and light
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] with indicator button and light
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 1 | [ELPR-006]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 3 | [ELPR-006]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Panel 2 | [MMGE-001]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 5 | 1 | Panel 1 | [ELGP-122]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2 | [ELGP-122]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 6 | 1 | Panel 3 | [ELGP-122]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 2 | [ITIN-025]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 3 | [ITIN-025]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2 | [MMGE-002]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 3 | [MMGE-002]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MGFP-082 | BLENDER: oxygen (O2) and nitrous oxide (N20) | 1 | 1 | Panel 2 | [MMMA-011]
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026] to bedhead
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | [MMSP-026] to bedhead cupboard
BIRM-A | Birthing Room, Without Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 3 | [MMSP-026] to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
BIRM-B | Birthing Room, With Pool | Maternity | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | DOFD-301 | DOOR: folding, bi-parting, 4 leaves, 1800 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWGE-017] to equipment storage area
BIRM-B | Birthing Room, With Pool | Maternity | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] with hold open device to support bed movement as required
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] low level for patient bed
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-106.01 | GPO: single, ceiling mounted, horizontal | 1 | 1 |  | [ELGP-101] to patient entertainment system
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-131.01 | GPO: single, emergency power, wall mounted, horizontal | 1 | 1 |  | [ELGP-123]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 5 | 1 | Panel 1 | [ELGP-122]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2 | [ELGP-122]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 6 | 1 | Panel 3 | [ELGP-122]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] 2 to staff write-up, 1 to lounge
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | [ELBO-015] to reading light
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | [ELBO-012] 1 to entry door, 1 to staff write up for general room lights
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1 |  | [FIDI-014]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-019]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-247 | HOLDER: alcohol-based hand rub, bed mounted | 1 | 1 |  | [FIHR-068]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019] 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016] mounted on trolley
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
BIRM-B | Birthing Room, With Pool | Maternity | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 2 | [FLVY-009] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051] for suturing and small procedures
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQBS-372 | SOFA BED: 2 seat | 1 | 1 |  | [FQBS-044]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1 |  | [FQSN-051] type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYBA-281 | POOL: birthing, back to wall | 1 | 1 |  | [HYBA-023] birthing pools can vary significantly in shape and the pool shown is indicative only. Final selection will have implications for required area and clearances. Ergonomic assessment of birthing pool options should be undertaken prior to selection.
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] to birthing pool area
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028] to birthing pool area
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | [HYTP-021] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039] 1 to shower, 1 to spout for birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYTP-381 | TAPWARE: birthing pool, spout, high flow, wall mounted | 1 | 1 |  | [HYTP-048]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to staff write-up for wall mounted phone
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 2 | [ITIN-025]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 3 | [ITIN-025]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment system, may be replaced with data outlet depending on ICT policies
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | [ITNE-049] optional, to patient locker
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] to staff write-up, dual monitors may be provided as required to suit operational, EMR and ICT requirements; a workstation on wheels is also acceptable
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | [ITSE-006] 1 to staff write-up, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-020]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOBE-221 | BENCH SUPPORT: end panel | 2 | 1 |  | [FIJO-213] 1 below FIJO-156 to separate dirty linen trolley from hand wash, storage for clean and dirty linen to suit local operational policies, 1 below write-up bench
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099] to staff write-up bench
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-129] type and extent of storage to suit service requirements
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-006 | CUPBOARD: tall, single door, for medical services panel | 1 | 1 |  | [FIJO-162]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-145] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | [FIJO-209] wardrobe, type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOGE-001 | BULKHEAD: joinery | 5 | 1 |  | [FIJO-212]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOSH-401 | SHELF: wall mounted, laminate | 2 | 1 |  | [FIJO-194] to equipment store cupboard, type and quantity of storage options to be determined based on service requirements
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOSP-001 | JOINERY UNIT: bespoke, birthing, tall, infant resuscitaire storage | 1 | 1 |  | [FIJO-233] Configuration of joinery to suit resuscitare equipment selected, including consideration of maneuverability and provision of sufficient space for emergency resuscitation procedures. Confirm design with users at project level.
BIRM-B | Birthing Room, With Pool | Maternity | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
BIRM-B | Birthing Room, With Pool | Maternity | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | [LIFX-017] to bedhead
BIRM-B | Birthing Room, With Pool | Maternity | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011] to bedhead
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 2 | [MGAS-022]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 3 | [MGAS-022]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 2 | [MGAS-032]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 4 | [MGAS-032]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 2 | [MGAS-042]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 3 | [MGAS-042]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 4 | [MGAS-042]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 2 | [MGAS-053]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 4 | [MGAS-053]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2 | [MGAS-062]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 3 | [MGAS-062]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 3 | [MGFP-002]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2 | [MGFP-004]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 3 | [MGFP-004]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 4 | [MGFP-004]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2 | [MMGE-002]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 3 | [MMGE-002]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-082 | BLENDER: oxygen (O2) and nitrous oxide (N20) | 1 | 1 | Panel 2 | [MMMA-011]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMBE-126 | BED: patient, electric, with mattress, birthing | 1 | 1 |  | [MMBE-005]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100] 1 to bedhead cupboard, 1 to resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-031 | BASSINET: infant, mobile | 1 | 3 |  | [FQBS-001] optional
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-051 | DEVICE: patient, fetal, cardiotocography (CTG) | 1 | 1 |  | [MMMA-031] to equipment store cupboard
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-061 | RESUSCITAIRE: infant, mobile | 1 | 1 |  | [MMMA-015]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-116 | SUPPORT FIXTURE: birthing, ladder, wall mounted | 1 | 1 |  | [MMMA-041]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-121 | SUPPORT FIXTURE: birthing, hook, ceiling mounted | 1 | 3 |  | [MMMA-043] optional, provision dependent on birthing aids/supportive equipment to be used
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026] to bedhead
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | [MMSP-026] to bedhead cupboard
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 3 | [MMSP-026] to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 4 | [MMSP-026] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1 |  | [FQSM-016] to equipment store cupboard
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-010] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2 | [ELPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 2 | [MGFP-002]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] to bedhead
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Panel 1 | [ITCL-028]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] with indicator button and light
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] with indicator button and light
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 1 | [ELPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 3 | [ELPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Panel 4 | [MMGE-001]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Panel 2 | [MMGE-001]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-002]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
BIRM-B | Birthing Room, With Pool | Maternity | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 1 | [DWWD-004]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | WIFX-108.01 | WINDOW: fixed, external, single glazed, sill at 1050H | 1 | 1 | External - Window 2 | [DWWH-005]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 2 | [DWWD-004]
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to birthing pool tapware
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to birthing pool tapware
BLIN | Bay - Linen | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided; coordinated with adjacent area
BLIN | Bay - Linen | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] flush set ceiling is also acceptable; to be coordinated with adjacent area
BLIN | Bay - Linen | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, lighting and controls to be coordinated with adjacent area, may be provided if bay is enclosed
BLIN | Bay - Linen | Logistics / Support Services | FFE | FIHR-029 | HOOK: equipment, wall mounted | 3 | 3 |  | [FIHR-029] optional, for storage of linen bags
BLIN | Bay - Linen | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BLIN | Bay - Linen | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BLIN | Bay - Linen | Logistics / Support Services | FFE | FQCL-253 | TROLLEY: clean linen, large | 1 | 1 |  | [MMGE-109] with cover as required to suit infection prevention and control policies
BLIN | Bay - Linen | Logistics / Support Services | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 3 |  | [FIJO-129] optional, for storage of additional items such as pillows, privacy curtains, shower curtains, etc.
BLIN | Bay - Linen | Logistics / Support Services | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | [FIJO-212] optional, to joinery cupboard if provided, plasterboard bulkhead is also acceptable
BLIN | Bay - Linen | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BLIN | Bay - Linen | Logistics / Support Services | FIN | WLFI-011.05 | WALL FINISH: vinyl, to 1800 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-021]
BLIN | Bay - Linen | Logistics / Support Services | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 3 |  | [FIHR-030] optional
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 3 |  | [MMBE-042] optional
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-020] height dependent on type and height of mobile equipment, crash rails are also acceptable
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] type, quantity and configuration of outlets to be determined based on equipment requirements
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 2 | [WLWA-004] to suit clinical areas and associated cleaning regimes/products depending on unit
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FFE | FQWS-098 | BIN: recycling, paper/cardboard, 240L | 1 | 1 |  | [FQCW-029] type, size and quantity of bins is to suit waste management policies and may be consolidated with bins provided in adjacent areas
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-129] configuration and extent of stationary storage to suit service requirements, floor standing and mobile storage solutions are also acceptable
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FFE | ITNE-302 | MULTIFUNCTION DEVICE: printer/copier/scanner/fax, floor standing | 1 | 1 |  | [ITNE-021] recommended manufacturer clearance zones to be considered, bins and other easily moveable items may be within clearance zones
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FFE | FQWS-218 | BIN: confidential document, secure, 240L | 1 | 1 |  | [FQCW-038] type, size and quantity of bins is to suit waste management policies and may be consolidated with bins provided in adjacent areas
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1 | [CLTI-007] coordinated with adjacent area
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | [WLPR-010] height to align with adjacent wall protection and suit equipment movement in adjacent area
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] locate to suit reach of cords and for access without moving multifunction device
BMFD-3 | Bay - Multifunction Device, 3m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] locate to suit reach of cords and for access without moving multifunction device
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 2 | [WLWA-004] to suit clinical areas and associated cleaning regimes/products depending on unit
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1 | [CLTI-007] coordinated with adjacent area
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | [WLPR-010] height to align with adjacent wall protection and suit equipment movement in adjacent area
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] locate to suit reach of cords and for access without moving multifunction device
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] locate to suit reach of cords and for access without moving multifunction device
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] over bench
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | FQWS-098 | BIN: recycling, paper/cardboard, 240L | 1 | 1 |  | [FQCW-029] type, size and quantity of bins is to suit waste management policies and may be consolidated with bins provided in adjacent areas
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] 1 to tall cupboard, 1 to wall mounted shelf units
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-129] configuration and extent of stationary storage to suit service requirements, floor standing and mobile storage solutions are also acceptable
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | ITNE-302 | MULTIFUNCTION DEVICE: printer/copier/scanner/fax, floor standing | 1 | 1 |  | [ITNE-021] recommended manufacturer clearance zones to be considered, bins and other easily moveable items may be within clearance zones
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | FQWS-218 | BIN: confidential document, secure, 240L | 1 | 1 |  | [FQCW-038] type, size and quantity of bins is to suit waste management policies and may be consolidated with bins provided in adjacent areas
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-136]
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
BMFD-7 | Bay - Multifunction Device, 7m2 | Administration | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152]
BMT | Bay - Meal Trolley | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided; coordinated with adjacent area
BMT | Bay - Meal Trolley | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] flush set ceiling is also acceptable; to be coordinated with adjacent area
BMT | Bay - Meal Trolley | Logistics / Support Services | SER | ELGP-312 | ISOLATOR: three phase, with socket outlet, wall mounted | 2 | 3 |  | [ELGP-140] optional, power requirements will be dependent on type of meal trolley
BMT | Bay - Meal Trolley | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BMT | Bay - Meal Trolley | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BMT | Bay - Meal Trolley | Logistics / Support Services | FFE | FQCA-082 | TROLLEY: food delivery, hot/cold | 2 | 1 |  | [FQCA-082] type of meal trolley will be dependent on food service delivery model
BMT | Bay - Meal Trolley | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BMT | Bay - Meal Trolley | Logistics / Support Services | FIN | WLFI-011.05 | WALL FINISH: vinyl, to 1800 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-021]
BMT | Bay - Meal Trolley | Logistics / Support Services | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BMT | Bay - Meal Trolley | Logistics / Support Services | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] power requirements will be dependent on type of meal trolley
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044] with wide opening
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] quantity and type of bins to be based on local waste management policies
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005] quantity and type of bins to be based on local waste management policies
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITBU-401 | ALARM: equipment monitoring, temperature | 1 | 1 |  | [ITBU-001] to fridge, dependent on requirements, may be integral to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026] quantity to suit project specific equipment requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] to computer
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049] may be wall mounted
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 3 |  | [ITNE-003] optional, dependent on software requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-056]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-069] laboratory grade
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141] lockable; extent of storage to suit testing requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106] lockable; extent of storage to suit testing requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | MMLA-003 | DEVICE: analyser, blood gas, point of care | 2 | 1 |  | [MMLA-049] quantity and type to suit service requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | MMLA-201 | FRIDGE: laboratory, 150L nom, single door, under bench | 1 | 1 |  | [MMLA-055] lockable; temperature monitored
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | WLFI-116 | SPLASHBACK: laminate, prefinished | 3 | 1 | Wall Finish 2 | [WLWA-009] coved, integral to bench
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 5 | 1 |  | [ELGP-223] quantity to suit project specific equipment requirements, confirm UPS requirements
BPROP | Bay - Property, Staff | Staff Amenities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BPROP | Bay - Property, Staff | Staff Amenities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] to be coordinated with adjacent area
BPROP | Bay - Property, Staff | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BPROP | Bay - Property, Staff | Staff Amenities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BPROP | Bay - Property, Staff | Staff Amenities | FFE | FQSN-321 | LOCKER: floor standing, 2 door | 2 | 1 |  | [FQSN-048] quantity and size of lockers to be based on staffing and service requirements; built-in joinery items are also acceptable
BPROP | Bay - Property, Staff | Staff Amenities | FFE | FQSN-341 | LOCKER: floor standing, 4 door | 6 | 1 |  | [FQSN-050] quantity and size of lockers to be based on staffing and service requirements; built-in joinery items are also acceptable
BPROP | Bay - Property, Staff | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | [FIJO-212] optional, plasterboard bulkhead is also acceptable
BPROP | Bay - Property, Staff | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 2 | 1 | Wall Finish 1 | [WLWA-004]
BPROP | Bay - Property, Staff | Staff Amenities | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] align height with locker doors
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | SER | ELGE-001 | DIRECT CONNECTION: power | 1 | 1 |  | [ELGE-001] direct connection to station
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-451 | STATION: pneumatic tube | 1 | 1 |  | [MMGE-097] with audible alarm
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-452 | BASKET: pneumatic tube | 1 | 1 |  | [FQSN-001] may be lockable depending on location, service and security requirements
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-453 | RACK: pneumatic tube, canister | 1 | 1 |  | [MMLA-072] quantity to suit service requirements
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-454 | LIGHT: pneumatic tube, alert light | 1 | 1 |  | [LIFX-015]
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 3 |  | [FIHR-030] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | FIHR-173 | BRACKET: gas cylinder, single, trolley mounted | 1 | 3 |  | [FIHR-090] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MGGE-011.01 | CYLINDER: medical gas, C size, oxygen | 1 | 3 |  | [MMHA-033] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 3 |  | [MMBE-042] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002]
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMHA-016 | DEVICE: variable suction and oxygen unit (twin-o-vac) | 1 | 1 |  | [MMHA-016]
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1 |  | [MMHA-027] type dependent on service requirements
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-020] crash rails are also acceptable
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | [ELGP-223]
B-SCRUB | Bay - Scrub | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
B-SCRUB | Bay - Scrub | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] coordinated with adjacent area
B-SCRUB | Bay - Scrub | Operating | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent
B-SCRUB | Bay - Scrub | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
B-SCRUB | Bay - Scrub | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1
B-SCRUB | Bay - Scrub | Operating | FIN | WLPR-006.07 | WALL PROTECTION: corner guards, full height | 1 | 1 | Wall Finish 2
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | for non-sterile gloves
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-131 | HOLDER: PPE, goggles, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-271 | DISPENSER: moisturiser, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-201 | DISPENSER: scrub brush, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | 900H x 450W, at 900H AFFL
B-SCRUB | Bay - Scrub | Operating | FFE | JOSH-402 | SHELF: wall mounted, stainless steel | 1 | 1 |  | optional; mounted above scrub trough
B-SCRUB | Bay - Scrub | Operating | FFE | HYBA-112 | SCRUB TROUGH: type A, handwashing, floor mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | HYTP-121 | TAPWARE: scrub trough, sensor tap and plate, trough mounted | 3 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-251 | DISPENSER: alcohol-based hand rub, surgical, antimicrobial, chlorhexidine, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-266.01 | DISPENSER: hand wash, surgical, antimicrobial, chlorhexidine, wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FIDI-266.02 | DISPENSER: hand wash, surgical, antimicrobial, povidone-iodine (PVI), wall mounted | 1 | 1
B-SCRUB | Bay - Scrub | Operating | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
B-SCRUB | Bay - Scrub | Operating | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 3 | 1 |  | 1 to each sensor tap spout
B-SCRUB | Bay - Scrub | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
B-SCRUB | Bay - Scrub | Operating | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | flush to wall
B-SCRUB | Bay - Scrub | Operating | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to scrub trough
BVM | Bay - Vending Machine | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BVM | Bay - Vending Machine | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] to be coordinated with adjacent area
BVM | Bay - Vending Machine | Public Areas | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 2 | 1 |  | [ELGP-109] 1 to each vending machine; service requirements to be confirmed with supplier
BVM | Bay - Vending Machine | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BVM | Bay - Vending Machine | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BVM | Bay - Vending Machine | Public Areas | FFE | FQGE-131 | VENDING MACHINE: food/drinks, refrigerated | 1 | 1 |  | [FQCA-055] quantity and type of vending machine is to be confirmed at project level to suit service requirements
BVM | Bay - Vending Machine | Public Areas | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016] 1 to each vending machine; service requirements to be confirmed with supplier
BVM | Bay - Vending Machine | Public Areas | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | [FIJO-212] optional, as required to prevent tipping or access to top/back of machines; may be removable for repairs and maintenances
BVM | Bay - Vending Machine | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BVM | Bay - Vending Machine | Public Areas | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] height to be coordinated with adjacent wall protection
BVM | Bay - Vending Machine | Public Areas | FFE | FQGE-132 | VENDING MACHINE: food/drinks, non-refrigerated | 1 | 1 |  | [FQCA-057] quantity and type of vending machine is to be confirmed at project level to suit service requirements
BWC | Bay - Wheelchair Park | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BWC | Bay - Wheelchair Park | Ambulatory Care | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BWC | Bay - Wheelchair Park | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BWC | Bay - Wheelchair Park | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BWC | Bay - Wheelchair Park | Ambulatory Care | FFE | MMBE-081 | WHEELCHAIR: patient | 2 | 1 |  | [MMBE-045] quantity to suit service requirements
BWC | Bay - Wheelchair Park | Ambulatory Care | FFE | MMBE-082 | WHEELCHAIR: patient, bariatric | 1 | 1 |  | [MMBE-050] quantity to suit service requirements
BWC | Bay - Wheelchair Park | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BWC | Bay - Wheelchair Park | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-020] crash rails are also acceptable
BWC | Bay - Wheelchair Park | Ambulatory Care | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BWC | Bay - Wheelchair Park | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 3 |  | [ELGP-208] optional
BWTR | Bay - Water Fountain | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BWTR | Bay - Water Fountain | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] to be coordinated with adjacent area
BWTR | Bay - Water Fountain | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
BWTR | Bay - Water Fountain | Public Areas | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | [FLVY-003] floor finish of adjacent area may continue under water fountain but must have a minimum slip rating R10/pendulum P3 or agreed equivalent or an inset section of non-slip vinyl is required; significant change in colour to be avoided.
BWTR | Bay - Water Fountain | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
BWTR | Bay - Water Fountain | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BWTR | Bay - Water Fountain | Public Areas | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-025]
BWTR | Bay - Water Fountain | Public Areas | FFE | FIDI-196 | DISPENSER: disposable cup, wall mounted | 1 | 1 |  | [FQCA-014]
BWTR | Bay - Water Fountain | Public Areas | FFE | HYGE-052 | DRINKING FOUNTAIN: wall mounted, accessible | 1 | 1 |  | [HYGE-011]
BWTR | Bay - Water Fountain | Public Areas | SER | ELGP-102 | GPO: single, wall mounted, power available indicator | 1 | 3 |  | [ELGP-111] optional, for refrigerated units only
CHPT | Change Cubicle - Patient | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
CHPT | Change Cubicle - Patient | Sanitary Facilities | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-002] drop-in ceiling tiles are also acceptable
CHPT | Change Cubicle - Patient | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] outward opening, with privacy latch; cubicle partition system or curtain track with privacy curtain are also acceptable
CHPT | Change Cubicle - Patient | Sanitary Facilities | SER | ELSW-031 | SWITCH: light, motion sensor, ceiling mounted | 1 | 1 |  | [ITSE-044] manual light switch is also acceptable
CHPT | Change Cubicle - Patient | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-005]
CHPT | Change Cubicle - Patient | Sanitary Facilities | FFE | FIGE-021 | BENCH SEAT: fixed, indoor, wall mounted | 1 | 1 |  | [FIGE-003] colour of seating to contrast with flooring and walls as per AS1428 luminance contrast requirements
CHPT | Change Cubicle - Patient | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
CHPT | Change Cubicle - Patient | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CHPT | Change Cubicle - Patient | Sanitary Facilities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CHPT | Change Cubicle - Patient | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] low height for access from seated position or floor
CHPT | Change Cubicle - Patient | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
CHPT | Change Cubicle - Patient | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
CHPT | Change Cubicle - Patient | Sanitary Facilities | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]
CHPT | Change Cubicle - Patient | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-002]
CHPT | Change Cubicle - Patient | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
CHPT | Change Cubicle - Patient | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHPT | Change Cubicle - Patient | Sanitary Facilities | FFE | FIRT-105 | GRAB RAIL: 90 degree | 1 | 1 |  | [FIRT-006]
CHPT | Change Cubicle - Patient | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] privacy latch, with emergency release
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 2 | 1 |  | [FIRT-006] Ambulant provision.
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 3 |  | [FQGE-005] optional
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 3 |  | [FQCW-037] optional, to be provided to female change rooms
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | HYWC-031 | TOILET SUITE: patient | 1 | 1 |  | [HYWC-006]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 2 | 1 |  | [ITCL-006] 1 to toilet cubicle, 1 to change cubicle
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | MMTR-121 | TROLLEY: gowns/scrubs, 1060W x 490D x 1830H nominal | 1 | 3 |  | [MMGE-122] optional
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | WLPT-051 | PARTITION SYSTEM: cubicle, changing | 1 | 1 | Wall Finish 3 | [WLPT-001]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | WLPT-062 | PARTITION SYSTEM: cubicle, toilet, ambulant | 1 | 1 | Wall Finish 2 | [WLPT-005]
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 4 | [WLWA-007] to basin
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-002] square set cornice acceptable if flush set ceiling is provided
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] flush set ceiling is also acceptable
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FIN | WLPT-054 | PARTITION SYSTEM: integral seat, changing | 1 | 1 | Wall Finish 3 | [FIGE-003] chair is also acceptable; confirm weight capacity requirements
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FQSN-322 | LOCKER: floor standing, 2 door, on plinth | 4 | 1 |  | [FQSN-048] quantity and size of lockers to suit service requirements
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | FQSN-342 | LOCKER: floor standing, 4 door, on plinth | 2 | 1 |  | [FQSN-050] quantity and size of lockers to suit service requirements
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 1 |  | [FIJO-191] over basin; provision of basin with integral shelf is also acceptable
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 3 |  | [ELGP-208] optional
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
CHPT-12 | Change Room - Patient (Male/Female), 12m2 | Sanitary Facilities | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-002] drop-in ceiling tiles are also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-002]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] outward opening, with privacy latch; cubicle partition system or curtain track with privacy curtain are also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ELSW-031 | SWITCH: light, motion sensor, ceiling mounted | 1 | 1 |  | [ITSE-044] manual light switch is also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] low height for access from seated position or floor
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIRT-105 | GRAB RAIL: 90 degree | 1 | 1 |  | [FIRT-006]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-005]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIGE-021 | BENCH SEAT: fixed, indoor, wall mounted | 1 | 1 |  | [FIGE-003] colour of seating to contrast with flooring and walls as per AS1428 luminance contrast requirements
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026] 1 mounted at accessible height to AS1428.1 requirements
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with closer as required for privacy
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | [FIDI-030] 1 to basin, 1 to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 3 |  | [FIDI-049] optional, to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIGE-021 | BENCH SEAT: fixed, indoor, wall mounted | 2 | 1 |  | [FIGE-003] to changing area
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026] 1 to toilet cubicle, 1 to shower cubicle
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 12 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQSN-323 | LOCKER: floor standing, 2 door, with shoe storage | 2 | 1 |  | [FQSN-054]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQSN-343 | LOCKER: floor standing, 4 door, with shoe storage | 2 | 1 |  | [FQSN-055]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 3 |  | [FQCW-037] optional, to toilet in female change rooms
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYSH-001 | SHOWER: fixed rose, wall mounted | 1 | 1 |  | [HYTP-018]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1 |  | [HYTP-039]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYWC-021 | TOILET SUITE: standard | 1 | 1 |  | [HYWC-008] with clear out access point
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | [FIJO-212] optional, over lockers; plasterboard bulkhead is also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 6 | 1 | Wall Finish 1 | [WLWA-004]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 4 | 1 | Wall Finish 2 | [WLWA-023] to shower; tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLPT-061 | PARTITION SYSTEM: cubicle, toilet | 1 | 1 | Wall Finish 5 | [WLPT-005] lift off hinges to inward opening sanitary compartment doors
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLPT-071 | PARTITION SYSTEM: cubicle, shower | 1 | 1 | Wall Finish 4 | [WLPT-004]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-033] optional
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYBA-143 | BASIN: type C, handwashing, with integral double shelf | 1 | 1 |  | [HYBA-012]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional, to changing area; quantity to be based on staffing and service requirements
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIGE-023 | BENCH SEAT: fixed, indoor, wet area, wall mounted | 1 | 1 |  | [FIGE-003] to shower cubicle
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with closer as required for privacy
CHST-35 | Change - Staff, 35m2 | Staff Amenities | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] to basins
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-007]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basins
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 4 | 1 |  | [FIDI-030] 2 x to basins, 2 x to showers
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 2 | 3 |  | [FIDI-049] optional, to showers
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 3 | 1 |  | [FIDI-036]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIGE-021 | BENCH SEAT: fixed, indoor, wall mounted | 2 | 1 |  | [FIGE-003] to showers, material to be suitable for wet areas
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIHR-026 | HOOK: coat, wall mounted | 16 | 3 |  | [FIHR-026] optional, quantity and configuration to be determined to suit operational requirements
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIRT-061.01 | TRACK: curtain, shower, straight | 2 | 3 |  | [FIRT-033] optional
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 2 | 1 |  | [FIRT-006] to ambulant toilet
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 33 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] to be suitable for bare feet; tiles are also acceptable
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQBS-321 | BENCH SEAT: freestanding, indoor | 1 | 1 |  | [FQBS-007]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 2 | 1 |  | [MMGE-048]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQCL-253 | TROLLEY: clean linen, large | 1 | 1 |  | [MMGE-109]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQGE-102 | CURTAIN: shower | 2 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQSN-323 | LOCKER: floor standing, 2 door, with shoe storage | 6 | 1 |  | [FQSN-054]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQSN-343 | LOCKER: floor standing, 4 door, with shoe storage | 17 | 1 |  | [FQSN-055]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQWS-051 | BIN: general waste, 20L | 2 | 1 |  | [FQCW-016] to basins
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | FQWS-331 | BIN: sanitary waste | 3 | 3 |  | [FQCW-037] optional, to toilets in female change rooms
CHST-35 | Change - Staff, 35m2 | Staff Amenities | SER | HYDR-021 | DRAIN: floor waste, round | 3 | 1 |  | [HYDR-004] 2 to shower cubicles, 1 to basin area
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | HYSH-001 | SHOWER: fixed rose, wall mounted | 2 | 1 |  | [HYTP-018]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 2 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | HYWC-021 | TOILET SUITE: standard | 2 | 1 |  | [HYWC-008] with 100mm clearout access point
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | HYWC-022 | TOILET SUITE: ambulant | 1 | 1 |  | [HYWC-010] with 100mm clearout access point
CHST-35 | Change - Staff, 35m2 | Staff Amenities | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to wall phone if provided
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 3 |  | [ITNE-052] optional
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 3 | 3 |  | [FIJO-212] optional, over lockers, plasterboard bulkhead is also acceptable
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 16 | 1 | Wall Finish 1 | [WLWA-004]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 8 | 1 | Wall Finish 2 | [WLWA-023] to shower; tiles are also acceptable
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basins
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | WLPT-061 | PARTITION SYSTEM: cubicle, toilet | 2 | 1 | Wall Finish 5 | [WLPT-005] lift off hinges to inward opening sanitary compartment doors
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | WLPT-062 | PARTITION SYSTEM: cubicle, toilet, ambulant | 1 | 1 | Wall Finish 6 | [WLPT-016]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FIN | WLPT-071 | PARTITION SYSTEM: cubicle, shower | 2 | 1 | Wall Finish 4 | [WLPT-004]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-001] with closer as required for privacy
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-001] to room side
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHST-35 | Change - Staff, 35m2 | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2 | [ITSE-038]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | FFE | HYBA-143 | BASIN: type C, handwashing, with integral double shelf | 1 | 1 |  | [HYBA-012]
CHST-35 | Change - Staff, 35m2 | Staff Amenities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | to basins
CHST-35 | Change - Staff, 35m2 | Staff Amenities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 4 | 1 |  | 2 to basins, 2 to showers
CHST-35 | Change - Staff, 35m2 | Staff Amenities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 4 | 1 |  | 2 to basins, 2 to showers
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] at 3000 mm AFFL
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 1 | [ELGP-121]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 2 - Arm 1 | [ELGP-121]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [ELGP-132]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [ELGP-132]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-256 | GPO: double, emergency power, in floor box | 3 | 1 |  | [ELGP-225]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 2 | 1 |  | [ELPR-004] 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 2 | 1 |  | [ELPR-007]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1 |  | [ELBO-005]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006] 1 to each pendant, 1 for wall mounted outlets and 1 for floor box outlets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 4 | 1 |  | [ELBO-012]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 1 |  | [ELBO-003]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 3 |  | [ELBO-001] optional, for equipment shut-off
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 4 | 1 |  | [FIHR-019] on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] for slave monitor
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 2 | 1 |  | [FQBS-052]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | [FQCW-008]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITBU-474 | CLOCK: digital display, dual sided, electric, synchronised slave, wired internet protocol (IP), wall mounted, cantilevered | 1 | 1 |  | [ITCL-023]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | [ITCL-021]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | [ITCL-008] to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | [ITCL-004] to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1 |  | [ITIN-022]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [ITIN-024]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 2 - Arm 1 | [ITIN-024]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1 |  | [ITIN-143] under table
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 2 | 1 |  | [ITNE-008+MMGE-164]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] handsfree to control room, outside room, to control room, delete from room list if listed in adjacent accessway
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | [ITSE-025]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOCU-023 | CUPBOARD: tall, double door, glazed | 1 | 1 |  | [FIJO-221]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 3 | 1 |  | [FIJO-108]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106] under bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] over cupboards
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOSP-121 | JOINERY UNIT: bespoke, endoscopy, tall, catheter hanging | 1 | 1 |  | [FIJO-220]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] over bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | [LIFX-002] outside all entry points. Delete from room list if listed in adjacent room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | MEEX-046 | GRILLE: return air, wall mounted, low level | 4 | 1 |  | [MEEX-016]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [MGAS-021]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [MGAS-021]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | [MGAS-031] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 3 | Pendant 2 - Arm 1 | [MGAS-031] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [MGAS-041]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [MGAS-041]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | [MGAS-051] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 3 | Pendant 2 - Arm 1 | [MGAS-051] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [MGAS-061]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [MGAS-061]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1 |  | [MGFP-001]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 1 | [MGFP-002]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 2 - Arm 1 | [MGFP-002]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1 | [MGFP-004]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 2 - Arm 1 | [MGFP-004]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-006 | IMAGING DEVICE: catheter lab, dual plane, floor mounted and on ceiling mounted track | 1 | 1 |  | [MMMI-385]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-009 | TABLE: patient, catheter lab | 1 | 1 |  | [MMMI-389]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-041 | DEVICE: catheter lab, electrophysiology (EP) | 1 | 1 |  | [MMMI-398]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIGE-001 | SHIELD: radiation, mobile | 2 | 1 |  | [MMMI-390] ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1 |  | [MMMI-377] on bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIGE-051 | INJECTOR: contrast, pedestal, mobile | 1 | 3 |  | [MMMI-100] optionally can be on table or ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1 |  | [MMMI-329]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMGE-045 | POLE: IV, mobile | 2 | 1 |  | [MMGE-045]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMGE-191 | CANNISTER: suction bottle | 4 | 1 |  | [MMGE-100] on pendant mounted brackets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002] on resus trolley
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1 |  | [MMHA-027]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMOP-161 | MACHINE: anaesthetic | 1 | 3 |  | [MMOP-040] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 3 |  | [MMGE-088] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1 |  | [MMGE-032] on wall bracket
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | LIFX-141 | LIGHT: operating, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [MMSP-029]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMTR-121 | TROLLEY: gowns/scrubs, 1060W x 490D x 1830H nominal | 1 | 1 |  | [MMGE-122]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | [WLWA-019]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1 | [MMSP-018]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | [MMSP-018] anaesthetic pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-181 | MEDICAL SERVICES HEAD: horizontal, on pendant arm | 1 | 1 | Pendant 2 - Arm 1 | [MMSP-015]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MICC-062 | DISPLAY SCREEN: catheter lab, multi-modality | 1 | 1 | Pendant 3 - Arm 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 3 - Arm 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-114 | PENDANT: single arm, on imaging system track | 1 | 1 | Pendant 2 | [MMSP-015] electrophysiology pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-007 | TRACK: catheter lab, imaging device, ceiling mounted | 1 | 1 |  | [MMMI-400]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-008 | BRACKET: catheter lab, imaging device cable management, ceiling mounted | 1 | 1 |  | [MMMI-400]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 9 | 1 |  | [ELGP-123.1]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] 2 above bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] to control room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to procedure room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to control room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 3 | [DWGL-006] staff access to sterile stock/ scrub areas, with sliding cover for privacy
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 2 | [DWGL-006] to control room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to sterile stock side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 3 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to procedure room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to procedure room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-034] to corridor
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1 | [MMGE-002]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 2 - Arm 1 | [MMGE-002]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to procedure room side
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] at 3000 mm AFFL
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-034] to corridor
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 1 | [ELGP-121]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [ELGP-132]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELGP-256 | GPO: double, emergency power, in floor box | 3 | 1 |  | [ELGP-225]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | [ELPR-004] 1 to pendant
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | [ELPR-007]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1 |  | [ELBO-005]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006] 1 to pendant, 1 for wall mounted outlets, 1 for floor box outlets
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 4 | 1 |  | [ELBO-012]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 1 |  | [ELBO-003]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 3 |  | [ELBO-001] optional, for equipment shut-off
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019] on pendant/s
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] for slave monitor
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 2 | 1 |  | [FQBS-052]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | [FQCW-008]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | [ITCL-008] to wall, + indicator button & light
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | [ITCL-004] to wall, + indicator button & light
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1 |  | [ITIN-022]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [ITIN-024]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1 |  | [ITIN-143] under table
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 2 | 1 |  | [ITNE-008+MMGE-164]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] handsfree to control room
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | [ITSE-025]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | JOCU-023 | CUPBOARD: tall, double door, glazed | 1 | 1 |  | [FIJO-221]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 3 | 1 |  | [FIJO-108]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106] under bench
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] over cupboards
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | JOSP-121 | JOINERY UNIT: bespoke, endoscopy, tall, catheter hanging | 1 | 1 |  | [FIJO-220]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] over bench
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | [LIFX-002] outside all entry points, delete from room list if listed in adjacent room
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | MEEX-046 | GRILLE: return air, wall mounted, low level | 4 | 1 |  | [MEEX-016]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [MGAS-021]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [MGAS-031]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [MGAS-041]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [MGAS-051]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [MGAS-061]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1 |  | [MGFP-001]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1 - Arm 1 | [MGFP-002]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1 | [MGFP-004]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MICC-009 | TABLE: patient, catheter lab | 1 | 1 |  | [MMMI-388]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1 |  | [MMMI-377] on bench
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MIGE-055 | INJECTOR: contrast, table mounted | 1 | 3 |  | [MMMI-108] optionally can be mobile or ceiling mounted
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1 |  | [MMMI-329]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMGE-045 | POLE: IV, mobile | 2 | 1 |  | [MMGE-045]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100] on pendant mounted brackets
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002] on resus trolley
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1 |  | [MMHA-027]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | [MMGE-088]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1 |  | [MMGE-032] on wall bracket
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | LIFX-141 | LIGHT: operating, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [MMSP-029]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1 | [MMSP-015]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MMTR-121 | TROLLEY: gowns/scrubs, 1060W x 490D x 1830H nominal | 1 | 1 |  | [MMGE-122]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 5 | 1 | Wall Finish 1 | [WLWA-005]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 20 | 1 | Wall Finish 2 | [WLWA-023]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MMSP-181 | MEDICAL SERVICES HEAD: horizontal, on pendant arm | 1 | 1 | Pendant 1 - Arm 1
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MMSP-114 | PENDANT: single arm, on imaging system track | 1 | 1 | Pendant 2
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MICC-062 | DISPLAY SCREEN: catheter lab, multi-modality | 1 | 1 | Pendant 2 - Arm 1
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 2 - Arm 1
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MIGE-003 | SHIELD: radiation, ceiling mounted | 1 | 1 |  | [MMMI-390]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MICC-007 | TRACK: catheter lab, imaging device, ceiling mounted | 1 | 1 |  | [MMMI-400]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | FFE | MICC-002 | IMAGING DEVICE: catheter lab, single plane, on ceiling mounted track | 1 | 1 |  | [MMMI-387]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 9 | 1 |  | [ELGP-123.1]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125]
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1 |  | [ELGP-223] 2 above bench
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] to control room
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to procedure room side
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to control room side
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 3 | [DWGL-006] staff access to sterile stock/ scrub areas, with sliding cover for privacy
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 2 | [DWGL-006] to control room
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to sterile stock side
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 3 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to procedure room side
CLAB-I | Catheter Laboratory - Interventional | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1 | [MMGE-002]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004] to observation window for patient privacy; refer to local infection control policies
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-002]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ELGP-161 | GPO: single, UPS, wall mounted | 15 | 1 |  | [ELGP-130]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 3 |  | [ELBO-001] optional
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1 |  | [FIHR-075]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 2 | 1 |  | [FIHR-070] for reporting station
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | FQBS-171 | CHAIR: office, ergonomic | 4 | 1 |  | [FQBS-018]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | FQSN-281 | CABINET: floor standing, 660H nominal, tambour unit | 1 | 1 |  | [FQSN-031]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 2 | 1 |  | [ITAV-014] part of communications system integrated with imaging system
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 3 |  | [ITAV-057] optional
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 1 |  | [ITBU-013] patient journey board
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 4 | 1 |  | [ITIN-016]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 6 | 1 |  | [ITIN-026] 2 outlets for telephone
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 3 |  | [ITNE-049] on bench, 1 cordless optional
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | [ITNE-068]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITNE-171 | DISPLAY SCREEN: computer | 2 | 1 |  | [ITNE-063]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | [ITNE-069]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] for reporting station
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | [FIJO-031]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | JOBE-251 | CAP: cable access | 6 | 1 |  | [FIJO-099]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] for control room temperature, optional
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1 |  | [MGFP-001]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | MICC-071 | CONTROL WORKSTATION: catheter lab, acquisition, dual display screens, keyboard and mouse, control console, microphone and speaker, desktop | 1 | 1 |  | [MMMI-386]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | MICC-073 | CONTROL WORKSTATION: catheter lab, electrophysiology (EP) control, dual display screens, keyboard and mouse, desktop | 1 | 1 |  | [MMMI-397]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | MICC-074 | CONTROL WORKSTATION: catheter lab, electrophysiology (EP) recording, dual display screens, keyboard and mouse, desktop | 1 | 1 |  | [MMMI-399]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | MICC-061 | DISPLAY SCREEN: catheter lab | 1 | 1 |  | [MMMI-392] haemodynamic monitoring display
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 1 |  | [MMMI-369]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FFE | MMGE-332 | DEVICE: cardiac pacing | 1 | 1 |  | [MMGE-182]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 3 | 1 |  | [ELGP-123]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 7 | 1 |  | [ELGP-223]
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLCR-EP | Catheter Laboratory EP Control Room | Cardiac Investigations | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] observation window to procedure room
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004] to observation window for patient privacy; refer to local infection control policies
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | DOHI-013.05 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass | 1 | 1 | Internal - Door 1 | [DWGL-006] to procedure room
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 2 | [DWGL-002] to corridor
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-161 | GPO: single, UPS, wall mounted | 7 | 1 |  | [ELGP-130]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 3 |  | [ELBO-001] optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 3 | 1 |  | [FIHR-075]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | [FIHR-070]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FQBS-171 | CHAIR: office, ergonomic | 3 | 1 |  | [FQBS-018]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 2 | 1 |  | [ITAV-014] part of communications system integrated with imaging system
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 3 |  | [ITAV-057] optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 1 |  | [ITBU-013] patient journey board
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 6 | 1 |  | [ITIN-026] 2 outlets for telephone
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 3 |  | [ITNE-049] on bench, 1 cordless optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | [ITNE-009]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 3 | 1 |  | [ITNE-068]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | [ITNE-069]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] for reporting station
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | [FIJO-031]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOBE-251 | CAP: cable access | 5 | 1 |  | [FIJO-099]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-143]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | [LIFX-002]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] for control room temperature, optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1 |  | [MGFP-001]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | MICC-071 | CONTROL WORKSTATION: catheter lab, acquisition, dual display screens, keyboard and mouse, control console, microphone and speaker, desktop | 2 | 1 |  | [MMMI-386]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 1 |  | [MMMI-369]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 8 | 1 |  | [ELGP-223]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to procedure room side
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] to procedure room
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-003]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FFE | FQSM-152 | STORAGE SOLUTION: modular system, mobile, 400D x 600W x 2100H nominal | 5 | 1 |  | [FQSM-046] type and quantity of storage options to be determined based on service requirements
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FFE | FQSM-202 | SHELVING UNIT: mobile, adjustable shelves, 400D x 600W x 2100H nominal | 2 | 1 |  | [FQSM-048] type and quantity of storage options to be determined based on service requirements
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059] desk is also acceptable
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 2 | 1 |  | [FIJO-108] remove if desk provided in lieu of bench
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-023] extent dependent on type and height storage solution
CLN-10 | Clean Store, 10m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-072 | DISPENSER: sticker roll, wall mounted | 1 | 3 |  | [FIDI-052] optional
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQSM-152 | STORAGE SOLUTION: modular system, mobile, 400D x 600W x 2100H nominal | 5 | 1 |  | [FQSM-046] type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQSM-202 | SHELVING UNIT: mobile, adjustable shelves, 400D x 600W x 2100H nominal | 4 | 1 |  | [FQSM-048] type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQWS-271 | BIN: pharmaceutical waste, 20L | 1 | 1 |  | [FQCW-061]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 3 |  | [ITSE-012] optional, provision and placement dependent on local policies
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-145]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 8 | 1 |  | [FIJO-108]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | MMPH-002 | SAFE: dangerous drugs, wall mounted, medium | 1 | 1 |  | [MMGE-087] size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | MMPH-024 | FRIDGE: medication/vaccine, 1000L nom, double door | 1 | 1 |  | [MMGE-034] size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 3 | [WLWA-020] extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023] extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-003]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 3 |  | [ELGP-223] optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to drug fridge
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 3 |  | [ITIN-026] optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] to task light
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to drug fridge, for temperature monitoring
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] under wall mounted joinery
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-010] 2-way
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FIDI-072 | DISPENSER: sticker roll, wall mounted | 1 | 3 |  | [FIDI-052] optional
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FQSM-152 | STORAGE SOLUTION: modular system, mobile, 400D x 600W x 2100H nominal | 3 | 1 |  | [FQSM-046] type and quantity of storage options to be determined based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FQSM-202 | SHELVING UNIT: mobile, adjustable shelves, 400D x 600W x 2100H nominal | 2 | 1 |  | [FQSM-048] type and quantity of storage options to be determined based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | FQWS-271 | BIN: pharmaceutical waste, 20L | 1 | 1 |  | [FQCW-061]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 3 |  | [ITSE-012] optional, provision and placement dependent on local policies
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 1 | 1 |  | [FIJO-157]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-140]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 2 | 1 |  | [FIJO-108]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | MMPH-002 | SAFE: dangerous drugs, wall mounted, medium | 1 | 1 |  | [MMGE-087] size and quantity to be based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FFE | MMPH-021 | FRIDGE: medication/vaccine, 150L nom, single door, under bench | 1 | 1 |  | [MMGE-036] size and quantity to be based on service requirements
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 3 | [WLWA-020] extent dependent on type and height storage solution
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023] extent dependent on type and height storage solution
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-003]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | [ELGP-223] optional, for future provision of automated dispensing cabinets
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to drug fridge
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, for future provision of automated dispensing cabinets
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to drug fridge, for temperature monitoring
CLN-MED-S | Clean Store / Medication Room, Sub | Clinical Support Set 1 | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008] under wall mounted joinery
CLNUP | Clean-Up Room | Operating | D+W | DOHI-015.01 | DOOR: hinged, 1 leaf, 1000 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | sliding door may also be acceptable dependent on infection prevention and control and work health and safety policies, provision of manual hold open device to be confirmed to suit operational requirements
CLNUP | Clean-Up Room | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both side of the door leaf
CLNUP | Clean-Up Room | Operating | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent
CLNUP | Clean-Up Room | Operating | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
CLNUP | Clean-Up Room | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLNUP | Clean-Up Room | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CLNUP | Clean-Up Room | Operating | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1
CLNUP | Clean-Up Room | Operating | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1
CLNUP | Clean-Up Room | Operating | SER | HYDR-103 | TUNDISH: wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to sink tapware
CLNUP | Clean-Up Room | Operating | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink
CLNUP | Clean-Up Room | Operating | SER | ELGP-133 | GPO: single, emergency power, wall mounted, waterproof | 1 | 1 |  | optional - to surgical waste docking station if provided
CLNUP | Clean-Up Room | Operating | SER | ELSW-001 | SWITCH: light | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | with integral stainless steel splashback
CLNUP | Clean-Up Room | Operating | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | JOSH-403 | SHELF: wall mounted, wire | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYBA-451 | SINK: cleaner, with grate, wall mounted | 1 | 1 |  | optional - depending on operating room cleaning equipment and procedures
CLNUP | Clean-Up Room | Operating | FFE | HYBA-301 | SINK: single bowl | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYTP-182 | TAPWARE: sink, tap set, wall mounted, lever handles | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | HYTP-066 | TAPWARE: basin, tap set, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FQWS-063 | BIN: general waste, slimline, 90L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
CLNUP | Clean-Up Room | Operating | FFE | FQWS-151 | BIN: recycling, glass, 20L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-123 | BIN: recycling, plastics, slimline, 90L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-171 | BIN: recycling, metal, 20L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-103 | BIN: recycling, paper/cardboard, slimline, 90L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-131 | BIN: recycling, soft plastics, 20L | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FQWS-143 | BIN: recycling, soft plastics, slimline, 90L | 1 | 1 |  | for sterile wraps
CLNUP | Clean-Up Room | Operating | FFE | FQCL-052 | BUCKET: cleaner, mopping | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIHR-039 | RACK: broom/mop, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | quantity is dependent on service requirements (e.g. use of single use drapes)
CLNUP | Clean-Up Room | Operating | FFE | MMOP-401 | MACHINE: surgical waste management system | 1 | 1 |  | optional - machine and docking station may be required only in a selection of clean up rooms across the unit (i.e. approx. 1 per 4 OR's)
CLNUP | Clean-Up Room | Operating | FFE | MMOP-406 | DOCKING STATION: surgical waste management system | 1 | 1 |  | optional, direct connect waste outlet to sewer system; docking station may be required only in a selection of clean up rooms across the unit (i.e. approx. 1 per 4 OR's)
CLNUP | Clean-Up Room | Operating | SER | HYDR-151 | TRAP: plaster | 1 | 1 |  | optional
CLNUP | Clean-Up Room | Operating | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1 |  | optional - for laparoscopic sharps as required
CLNUP | Clean-Up Room | Operating | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1 |  | optional - to laparoscopic sharps bin if provided
CLNUP | Clean-Up Room | Operating | FFE | MMIC-496 | TROLLEY: transfer, instruments, dirty | 1 | 1 |  | optional - depending on RMD sterilizing transport processes, stored in room prior to transfer to sterilising unit
CLNUP | Clean-Up Room | Operating | FFE | LIFX-121 | LIGHT: procedure, minor, single articulated arm, 1 light head, ceiling mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | FFE | FIHR-143 | RACK: bottle, wall mounted | 1 | 1
CLNUP | Clean-Up Room | Operating | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to sink
CLNUP | Clean-Up Room | Operating | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CLRM | Cleaner's Room | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
CLRM | Cleaner's Room | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208] quantity to suit equipment charging requirements
CLRM | Cleaner's Room | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 3 |  | [FIDI-021] optional, type of PPE dispensers to be provided to suit service requirements
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-211 | HOLDER: eye wash bottles, wall mounted | 1 | 3 |  | [FIDI-057] optional, provide as required depending chemical safety data sheets and WHS policies
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-296 | DISPENSER: detergent/chemical mixer, wall mounted | 1 | 1 |  | [FIDI-010]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIHR-039 | RACK: broom/mop, wall mounted | 1 | 1 |  | [FIHR-040]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FQCL-041 | TROLLEY: cleaner | 1 | 1 |  | [FQSM-021]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FQCL-051 | BUCKET: cleaner | 1 | 1 |  | [FQCW-045] on cleaner's trolley
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYBA-451 | SINK: cleaner, with grate, wall mounted | 1 | 1 |  | [HYBA-040]
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to cleaner's sink
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYTP-431 | OUTLET: water, cold | 1 | 3 |  | [HYTP-008] optional, provision dependent on detergent/chemical mixer requirements
CLRM | Cleaner's Room | Logistics / Support Services | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 |  | [ITSE-038] optional, dependent on security requirements
CLRM | Cleaner's Room | Logistics / Support Services | FFE | JOSH-402 | SHELF: wall mounted, stainless steel | 1 | 1 |  | [FIJO-196] type and extent of storage to suit service requirements and operational policies for the decanting and storage of chemicals and consumables
CLRM | Cleaner's Room | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023]
CLRM | Cleaner's Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLRM | Cleaner's Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLRM | Cleaner's Room | Logistics / Support Services | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] to corridor
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FQWS-098 | BIN: recycling, paper/cardboard, 240L | 1 | 3 |  | [FQCW-029] optional
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | [FQCW-008]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | FQWS-253 | BIN: cytotoxic waste, 50L | 1 | 3 |  | [FQCW-060] optional
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010] elbow action levers
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052] hot water
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 1 | 1 |  | [HYTP-038]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] 1 to sink, 1 to basin
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | MMIC-351 | DISINFECTOR: ultrasound probes, freestanding | 1 | 3 |  | [MMIC-122] optional
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1 |  | [FQSM-016]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1 | [WLWA-005]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FIN | WLFI-011.05 | WALL FINISH: vinyl, to 1800 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-021]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-196] + [FIJO-197]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
CLUP-7 | Clean-Up Room, 7m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
COMM | Communications Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
COMM | Communications Room | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
COMM | Communications Room | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
COMM | Communications Room | Logistics / Support Services | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
COMM | Communications Room | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ELGP-261 | GPO: double, UPS, wall mounted | 4 | 1 |  | [ELGP-235] to suit project requirements, power may be wall mounted or delivered via ceiling mounted umbilicals for access depending on server selection.
COMM | Communications Room | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
COMM | Communications Room | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
COMM | Communications Room | Logistics / Support Services | FIN | FLVY-103 | FLOOR FINISH: vinyl, seamless, standard slip resistance, static dissipative | 1 | 1 | Floor Finish 1 | [FLVY-001]
COMM | Communications Room | Logistics / Support Services | FFE | FQGE-162 | STOOL: step, safety | 1 | 1 |  | [FQGE-095]
COMM | Communications Room | Logistics / Support Services | SER | ITBU-151 | HEAD END: IPTV system | 1 | 3 |  | [ITBU-015] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITBU-171 | HEAD END: MATV system | 1 | 3 |  | [ITBU-016] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-201 | ICT RACK: server equipment, floor standing | 1 | 1 |  | [ITNE-011] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-211 | ICT RACK: network communications equipment, floor standing | 1 | 1 |  | [ITNE-005] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-211 | ICT RACK: network communications equipment, floor standing | 1 | 1 |  | [ITIN-123] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-221 | ICT RACK: main distribution frame (MDF) | 1 | 1 |  | [ITIN-139] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-231 | ICT RACK: intermediate distribution frame (IDF) | 1 | 3 |  | [ITIN-128] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-052]
COMM | Communications Room | Logistics / Support Services | SER | ITSE-054 | CONTROL PANEL: security, duress | 1 | 3 |  | [ITSE-020] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITSE-221 | SENSOR: safety, motion detection, for staff alert, wall mounted | 1 | 1 |  | [ITSE-046]
COMM | Communications Room | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
COMM | Communications Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
COMM | Communications Room | Logistics / Support Services | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
CONS | Consult Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CONS | Consult Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS | Consult Room | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CONS | Consult Room | Ambulatory Care | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
CONS | Consult Room | Ambulatory Care | D+W | DOHI-012.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-077] optional, second door for egress
CONS | Consult Room | Ambulatory Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] 1 1/2 leaf door is also acceptable as required
CONS | Consult Room | Ambulatory Care | MSP | ELGP-216 | GPO: double, on services panel | 1 | 1 | Panel 1 | [ELGP-205]
CONS | Consult Room | Ambulatory Care | MSP | ELGP-246 | GPO: double, emergency power, on services panel | 1 | 1 | Panel 1 | [ELGP-222]
CONS | Consult Room | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
CONS | Consult Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 to exam light
CONS | Consult Room | Ambulatory Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
CONS | Consult Room | Ambulatory Care | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
CONS | Consult Room | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CONS | Consult Room | Ambulatory Care | FFE | FIDI-223 | DISPENSER: paper bed roll, exam couch mounted | 1 | 1 |  | [FIDI-003] may be provided as an attachment to exam couch
CONS | Consult Room | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CONS | Consult Room | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CONS | Consult Room | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CONS | Consult Room | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CONS | Consult Room | Ambulatory Care | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
CONS | Consult Room | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 3 |  | [FIHR-019] optional, provide if suction required
CONS | Consult Room | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
CONS | Consult Room | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
CONS | Consult Room | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CONS | Consult Room | Ambulatory Care | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
CONS | Consult Room | Ambulatory Care | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1 |  | [FQDW-037]
CONS | Consult Room | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
CONS | Consult Room | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
CONS | Consult Room | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CONS | Consult Room | Ambulatory Care | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CONS | Consult Room | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CONS | Consult Room | Ambulatory Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light
CONS | Consult Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
CONS | Consult Room | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028]
CONS | Consult Room | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
CONS | Consult Room | Ambulatory Care | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] to desk
CONS | Consult Room | Ambulatory Care | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-050]
CONS | Consult Room | Ambulatory Care | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] high resolution monitor for PACS viewing
CONS | Consult Room | Ambulatory Care | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
CONS | Consult Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] in discreet location easily accessible by staff
CONS | Consult Room | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
CONS | Consult Room | Ambulatory Care | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
CONS | Consult Room | Ambulatory Care | FFE | LIFX-114 | LIGHT: examination, single articulated arm, 1 light head, wall mounted | 1 | 1 |  | [LIFX-026] may be ceiling mounted
CONS | Consult Room | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | [MGAS-022] optional
CONS | Consult Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 3 | Panel 1 | [MGAS-042] optional
CONS | Consult Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 3 | Panel 1 | [MGAS-062] optional
CONS | Consult Room | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 3 | Panel 1 | [MGFP-002] optional, provide if medical air required
CONS | Consult Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 3 | Panel 1 | [MGFP-004] optional, provide if oxygen required
CONS | Consult Room | Ambulatory Care | FFE | MMBE-171 | COUCH: patient, examination, electric | 1 | 1 |  | [MMBE-023] hi/low operation
CONS | Consult Room | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 3 |  | [MMGE-100] optional, provide if suction required
CONS | Consult Room | Ambulatory Care | FFE | MMGE-231 | DIAGNOSTIC SET: otoscope and ophthalmoscope, portable | 1 | 1 |  | [MMGE-030] may be wall mounted/mobile on stand
CONS | Consult Room | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
CONS | Consult Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CONS | Consult Room | Ambulatory Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-025] to patient/visitor chairs
CONS | Consult Room | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 2 | 1 | Wall Finish 3 | [WLWA-020] to exam couch
CONS | Consult Room | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 4 | [WLWA-007] to basin
CONS | Consult Room | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
CONS | Consult Room | Ambulatory Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 3 | 1 |  | [FQBS-058] consider weight capacity of chairs
CONS | Consult Room | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low level, for electric couch
CONS | Consult Room | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] 2x below desk, 1x above desk
CONS | Consult Room | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] for exam light
CONS | Consult Room | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
CONS | Consult Room | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CONS | Consult Room | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CONS | Consult Room | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CONS | Consult Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CONS | Consult Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CONS | Consult Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
CONS | Consult Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS | Consult Room | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 3 | Panel 1 | [MMGE-002] optional, provide if suction required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin and eye wash station or an inset section of non-slip vinyl is required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin and eye wash station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to room side
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | 1 to entry door, 1 to examination chair; located to support quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 to entry door, 1 to examination chair; may be combined on a single face plate with patient to staff call button; located to support quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional, to medication fridge if provided; for temperature monitoring BMS connection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | optional, provision dependent on clinical services requirements and local ICT strategies and policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMPH-021 | FRIDGE: medication/vaccine, 150L nom, single door, under bench | 1 | 3 |  | optional, with temperature monitoring; provision is dependent on operational models for medication management
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | optional, to shelving over computer workstation if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 3 |  | optional, over computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to articulated examination light
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to slit lamp and retinal camera
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | optional
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | collocated with alcohol based hand rub
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | with removable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-406 | DEVICE: eye examination, retinal camera | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-401 | DEVICE: eye examination, slit lamp | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 3 |  | optional, to patient monitor if provided; with cable and accessory management items as required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 3 |  | optional, provision and configuration of monitoring to be confirmed to suit clinical services requirements
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to tall cupboard
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | for storage of consumables and specialist equipment
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for examination chair
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYSH-106 | STATION: emergency, safety, eye wash, wall mounted | 1 | 1 |  | disposable eye wash bottles may be considered in conjunction with or instead of a fixed eye wash station depending clinical services requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-396 | MIRROR: eye examination, to testing chart display screen | 1 | 1 |  | align with eye chart; locate to achieve 6m distance to patient when chart is reflected
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | cover to vision panel required to control light for eye examinations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 3 | Internal - Door 2 | optional, for secondary staff egress; provision dependent on local WHS policies; cover to vision panel required to control light for eye examinations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 3 | Panel 1 | optional, to articulated examination light; controls may be integral to light fitting
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to eye washing station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-391 | DISPLAY SCREEN: eye examination, testing chart | 1 | 1 |  | align with mirror; locate to achieve 6m distance to patient when chart is reflected
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to slit lamp and retinal camera
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMBE-176 | CHAIR: patient, examination, electric | 1 | 1 |  | suitable for ENT examinations and minor treatments
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to medication fridge if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; located to ensure visibility along paths of travel
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to eye chart display screen
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | over desk, for charging portable devices
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to eye washing station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to corridor side
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-007]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-223 | DISPENSER: paper bed roll, exam couch mounted | 1 | 1 |  | [FIDI-003] may be provided as an attachment to exam couch
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 3 |  | [FIHR-019] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1 |  | [FQDW-037]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-050]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] high resolution monitor for PACS viewing
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027] may be wall mounted
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MGFP-061 | ADAPTER: suction | 1 | 3 |  | [MMGE-002] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-172 | COUCH: patient, examination, electric, bariatric | 1 | 1 |  | [MMBE-064] hi/low operation
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | [MMBE-056]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | [MMBE-052] for patient lifter track
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-261 | SLING: patient lifter | 1 | 3 |  | [MMBE-054] optional, for patient lifter motor
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 3 |  | [MMGE-100] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMGE-233 | DIAGNOSTIC SET: otoscope and ophthalmoscope, wall mounted | 1 | 1 |  | [MMGE-031] may be portable/mobile on stand
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-025] to patient/visitor chairs
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 3 | [WLWA-020] to exam couch
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 4 | [WLWA-007] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 3 | 1 |  | [FQBS-058] consider weight capacity of chairs
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-031]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low level, for electric couch
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] 2x below desk, 1x above desk
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] for exam light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 to exam light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] to desk
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] in discreet location easily accessible by staff
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | DWGL-033]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-005] optional, second door for egress
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | [MGAS-022] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 3 | Panel 1 | [MGAS-042] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 3 | Panel 1 | [MGAS-062] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 3 | Panel 1 | [MGFP-002] optional, provide if medical air required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 3 | Panel 1 | [MGFP-004] optional, provide if oxygen required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 3 | Panel 1 | [MMGE-002] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | ELGP-216 | GPO: double, on services panel | 1 | 1 | Panel 1 | [ELGP-205]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | ELGP-246 | GPO: double, emergency power, on services panel | 1 | 1 | Panel 1 | [ELGP-222]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] quantity and location to comply with mandatory requirements.
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001] quantity to suit layout and infection control policies
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 16 | 1 | Floor Skirting | [FLSK-010]
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 1 |  | [ITCL-001] ceiling mounted; quantity to suit layout and service requirements
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | WLPR-006 | WALL PROTECTION: corner guards | 6 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | WLPR-026 | WALL PROTECTION: rigid wall sheeting | 12 | 1 | Wall Protection | [WLPR-026] height dependent on service requirements, crash rails are also acceptable
CORR | Corridor - Patient Treatment Areas | Clinical Support Set 2 | FIN | WLPR-101 | HANDRAIL: wall mounted | 4 | 1 | Wall Protection | [FIRT-010] provided to at least one side of the corridor, to be continuous wherever practical; may be combined with crash rail if provided
CTIR | CT Imaging Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
CTIR | CT Imaging Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CTIR | CT Imaging Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
CTIR | CT Imaging Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
CTIR | CT Imaging Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
CTIR | CT Imaging Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
CTIR | CT Imaging Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CTIR | CT Imaging Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | from corridor
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to imaging room side
CTIR | CT Imaging Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room (see CTIR-CTRL)
CTIR | CT Imaging Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to CT equipment room if provided
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to equipment room side
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
CTIR | CT Imaging Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
CTIR | CT Imaging Room | Medical Imaging | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 2 | to control room (see CTIR-CTRL)
CTIR | CT Imaging Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 6 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
CTIR | CT Imaging Room | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
CTIR | CT Imaging Room | Medical Imaging | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 1
CTIR | CT Imaging Room | Medical Imaging | MSP | ELGP-176 | GPO: single, UPS, on services panel | 2 | 1 | Panel 1 | extent of UPS to be confirmed to suit service and equipment requirements
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CTIR | CT Imaging Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CTIR | CT Imaging Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above medical services panel
CTIR | CT Imaging Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1
CTIR | CT Imaging Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control room entry
CTIR | CT Imaging Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | outside all room entries, to automatically turn on when modality is in use
CTIR | CT Imaging Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
CTIR | CT Imaging Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor on mobile stand
CTIR | CT Imaging Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to patient observation camera, in front of gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to patient observation camera, behind gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to clock
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional - to patient observation camera, in front of gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient observation camera, behind gantry
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | for foot pedal recharge
CTIR | CT Imaging Room | Medical Imaging | D+W | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 | Internal - Door 1 | to support bed movement
CTIR | CT Imaging Room | Medical Imaging | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | to support bed movement, delayed action closing
CTIR | CT Imaging Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
CTIR | CT Imaging Room | Medical Imaging | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | optional - patient transfer methods and equipment to meet local WHS policies
CTIR | CT Imaging Room | Medical Imaging | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | optional - provide if patient slide required
CTIR | CT Imaging Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
CTIR | CT Imaging Room | Medical Imaging | FFE | MICT-001 | IMAGING DEVICE: computerised tomography (CT), gantry | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MICT-006 | TABLE: patient, computerised tomography (CT) | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MIGE-053 | INJECTOR: contrast, ceiling mounted | 1 | 1 |  | mobile and table mounted injectors are also acceptable
CTIR | CT Imaging Room | Medical Imaging | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | optional - in front of gantry, location as required for adequate patient observation
CTIR | CT Imaging Room | Medical Imaging | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 5 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
CTIR | CT Imaging Room | Medical Imaging | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
CTIR | CT Imaging Room | Medical Imaging | FFE | FQSN-214 | SHELVING UNIT: floor standing, adjustable shelves, 600D x 900W x 2100H nominal | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
CTIR | CT Imaging Room | Medical Imaging | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1 |  | for phantoms
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | MMPM-012 | MONITOR: patient, medium acuity, on stand, mobile | 1 | 1 |  | may be wall mounted
CTIR | CT Imaging Room | Medical Imaging | MSP | ITCL-353 | DISPLAY SCREEN: patient treatment information, touch screen | 1 | 1 | Pendant 1 - Arm 1
CTIR | CT Imaging Room | Medical Imaging | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | location as required for adequate patient observation
CTIR | CT Imaging Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to patient monitor on mobile stand
CTIR | CT Imaging Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
CTIR | CT Imaging Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1
CTIR | CT Imaging Room | Medical Imaging | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1
CTIR | CT Imaging Room | Medical Imaging | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1
CTIR | CT Imaging Room | Medical Imaging | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 1 - Arm 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to control room side
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | optional - staff entry from corridor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to imaging room side
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to slave patient monitor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 7 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to each door
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | to imaging room entries, to automatically turn on when modality is in use
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | to slave patient monitor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | to control console, extent of UPS to be confirmed to suit service and equipment requirements
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to display screen for physiological monitoring if provided
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | optional - to display screen for physiological monitoring if provided
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | optional - for anaesthetic assist
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 1 | to imaging room
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOBE-211 | BENCH SUPPORT: bracket | 3 | 1 |  | leg support is also acceptable
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 3 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | to slave patient monitor
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to CT control CPU, 1 to PACS CPU
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | display/processing workstation, on dual arm bracket
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 4 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOBE-071 | BENCH: 800D, laminate | 1 | 1 |  | bench height to be confirmed; adjustable height desks may be considered depending on WHS policies and coordination with services and observation window
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-341 | BRACKET: display screen, single, articulated, wall mounted | 1 | 1 |  | optional - to display screen for physiological monitoring if provided
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to display/processing workstation
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITCL-381 | DISPLAY SCREEN: patient observation | 1 | 1 |  | optional - for physiological monitoring
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MICT-011 | CONTROL CONSOLE: computerised tomography (CT), dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | MICT-016 | COMPUTER: computerised tomography (CT), central processing unit (CPU) | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-311 | PRINTER: desktop | 1 | 1
CTIR-CTRL | CT Imaging Control Room | Medical Imaging | FFE | ITNE-341 | SCANNER: desktop, document, flatbed, desktop | 1 | 1
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 3 | 1 | Internal - Door 1 | [DWPR-005] to imaging room side
CTPR | CT Planning Room | Radiation Oncology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CTPR | CT Planning Room | Radiation Oncology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
CTPR | CT Planning Room | Radiation Oncology | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | [DWSC-005] to control room
CTPR | CT Planning Room | Radiation Oncology | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-034] to corridor
CTPR | CT Planning Room | Radiation Oncology | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-122]
CTPR | CT Planning Room | Radiation Oncology | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
CTPR | CT Planning Room | Radiation Oncology | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CTPR | CT Planning Room | Radiation Oncology | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
CTPR | CT Planning Room | Radiation Oncology | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | [ELBO-001]
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | [FIHR-030] for patient slide
CTPR | CT Planning Room | Radiation Oncology | FFE | FIHR-091 | HOOK: anchor point, for attaching patient self-assist positioning aid, wall mounted | 1 | 1 |  | [FIHR-092]
CTPR | CT Planning Room | Radiation Oncology | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
CTPR | CT Planning Room | Radiation Oncology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
CTPR | CT Planning Room | Radiation Oncology | FIN | FLVY-103 | FLOOR FINISH: vinyl, seamless, standard slip resistance, static dissipative | 1 | 1 | Floor Finish 1 | [FLVY-001] floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CTPR | CT Planning Room | Radiation Oncology | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142]
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
CTPR | CT Planning Room | Radiation Oncology | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CTPR | CT Planning Room | Radiation Oncology | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CTPR | CT Planning Room | Radiation Oncology | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
CTPR | CT Planning Room | Radiation Oncology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
CTPR | CT Planning Room | Radiation Oncology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
CTPR | CT Planning Room | Radiation Oncology | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 1 | 1 |  | [ITCL-012 + FIHR-078] for patient observation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
CTPR | CT Planning Room | Radiation Oncology | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
CTPR | CT Planning Room | Radiation Oncology | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
CTPR | CT Planning Room | Radiation Oncology | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | [ITSE-025]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-135]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
CTPR | CT Planning Room | Radiation Oncology | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOSP-032 | JOINERY UNIT: bespoke, radiotherapy, tall, horizontal patient device storage | 2 | 1 |  | [FIJO-166]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOSP-033 | JOINERY UNIT: bespoke, radiotherapy, tall, vertical patient device storage | 1 | 1 |  | [FIJO-167]
CTPR | CT Planning Room | Radiation Oncology | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038] desirable
CTPR | CT Planning Room | Radiation Oncology | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | [LIFX-002] outside room doors, auto-on when modality in use
CTPR | CT Planning Room | Radiation Oncology | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
CTPR | CT Planning Room | Radiation Oncology | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
CTPR | CT Planning Room | Radiation Oncology | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
CTPR | CT Planning Room | Radiation Oncology | FFE | MICT-002 | IMAGING DEVICE: computerised tomography (CT), gantry, wide bore | 1 | 1 |  | [MMMI-109]
CTPR | CT Planning Room | Radiation Oncology | FFE | MICT-006 | TABLE: patient, computerised tomography (CT) | 1 | 1 |  | [MMMI-105]
CTPR | CT Planning Room | Radiation Oncology | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1 |  | [MMMI-377] may be located in control room
CTPR | CT Planning Room | Radiation Oncology | FFE | MIGE-053 | INJECTOR: contrast, ceiling mounted | 1 | 1 |  | [MMMI-107] may be mobile
CTPR | CT Planning Room | Radiation Oncology | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | [MMBE-042] patient transfer devices to be based on operational requirements and WHS policies
CTPR | CT Planning Room | Radiation Oncology | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-056 | LASER: patient positioning, radiotherapy, table tracking | 1 | 1 |  | [MMRA-019]
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-061 | LASER: patient positioning, radiotherapy, bridge | 1 | 1 |  | [MMRA-014] wall and ceiling mounted lasers are also acceptable
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-071 | DEVICE: surface guided radiation therapy system, ceiling mounted | 1 | 1 |  | [MMRA-008 + FIHR-089] as required for respiratory gating / motion management / surface guidance systems, to suit service requirements
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-151 | DEVICE: oven, thermoplastic warming, radiotherapy moulds | 1 | 1 |  | [MMRA-020]
CTPR | CT Planning Room | Radiation Oncology | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
CTPR | CT Planning Room | Radiation Oncology | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | [MMGE-139]
CTPR | CT Planning Room | Radiation Oncology | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
CTPR | CT Planning Room | Radiation Oncology | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 7 | 1 | Wall Finish 2 | [WLWA-020]
CTPR | CT Planning Room | Radiation Oncology | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007]
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
CTPR | CT Planning Room | Radiation Oncology | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 3 |  | [ITCL-012 + FIHR-077] optional; for patient observation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
CTPR | CT Planning Room | Radiation Oncology | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CTPR | CT Planning Room | Radiation Oncology | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CTPR | CT Planning Room | Radiation Oncology | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to clock
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to patient observation camera
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 3 |  | [ELGP-101] optional, to additional patient observation camera if provided
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011] to patient observation camera
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to imaging room side
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to control room side
CTPR | CT Planning Room | Radiation Oncology | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] safety glass, to control room
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-011] optional, to additional patient observation camera if provided
CTPR | CT Planning Room | Radiation Oncology | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry door
CTPR | CT Planning Room | Radiation Oncology | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
CTPR | CT Planning Room | Radiation Oncology | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-010] to bench
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | LIFX-108 | LIGHT: task, integral to joinery | 5 | 1 |  | [LIFX-008]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 3 |  | [ELGP-208] optional; to workstation if provided
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 2 x task light
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | MGAS-153 | OUTLET: compressed air, wall mounted | 1 | 1 |  | [MGAS-008] to forming machine
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-165 | DEVICE: dental, mixing vibrator | 1 | 1 |  | [MMDN-024] a vacuum mixer may also be considered
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-161 | DEVICE: dental, micromotor, benchtop | 1 | 3 |  | [MMDN-004] optional
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-162 | DEVICE: dental, model trimmer, benchtop | 1 | 1 |  | [MMDN-005] plumbed to sink
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-171 | DEVICE: dental, dust extraction unit | 1 | 1 |  | [MMDN-023]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-164 | DEVICE: dental, moulder, forming machine, benchtop | 1 | 1 |  | [MMDN-013]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-163 | DEVICE: dental, lathe, benchtop | 1 | 1 |  | [MMDN-009] extraction is required if not integral to equipment
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | [ITNE-007] optional, to workstation if provided
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 3 |  | [ITNE-003] optional; to workstation if provided
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYTP-061 | TAPWARE: basin, tap set, fixture mounted | 1 | 1 |  | [HYTP-038]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYTP-151 | TAPWARE: sink, mixer, fixture mounted | 1 | 1 |  | [HYTP-037]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | HYDR-151 | TRAP: plaster | 1 | 1 |  | [HYDR-008]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-052]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 2 | 1 |  | [FIJO-021]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 2 | 1 |  | [FIJO-100 + FIJO-197] some shelves may be removable or omitted to allow for storage of bulk items on mobile dolly
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 5 | 1 |  | [FIJO-152]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 6 | 1 |  | [FQSN-006]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 4 | 1 |  | [FQSN-006]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQBS-207 | STOOL: office areas, mobile, high | 1 | 1 |  | [FQBS-052]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQDW-131.01 | WORKSTATION: straight, adjustable height, 720H nom, 600D x 1000W | 1 | 3 |  | [FQDW-052] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | [HYTP-008] to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | HYDR-206 | DIRECT CONNECTION: wastewater, dental chair | 1 | 1 |  | [HYDR-001] to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGE-002 | DIRECT CONNECTION: power, emergency | 1 | 1 |  | [ELGE-004] to dental chair
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional, depending on service requirements
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] to general room lighting
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITIN-012 | OUTLET: data, single RJ45, in floor box | 1 | 1 |  | [ITIN-010] connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | [ELPR-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 3 |  | [LIFX-008] optional, under wall mounted joinery if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELSW-001 | SWITCH: light | 2 | 3 |  | [ELBO-015] optional, to task lighting if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-123] to x-ray unit
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | MGAS-099 | DIRECT CONNECTION: suction, dental | 1 | 1 |  | [MGAS-090] to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | MGAS-029 | DIRECT CONNECTION: medical air | 1 | 1 |  | [MGAS-020] to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 3 | Wall Finish 3 | [WLWA-010] optional, to sink if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | WIFX-157.04 | WINDOW: fixed, external, double glazed, sill at 900H, with integral blind | 1 | 1 | External - Window 1 | [DWWH-005 + DWWD-007] desirable
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1 |  | [FIDI-014]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYBA-421 | SINK: dental, single bowl | 1 | 3 |  | [HYBA-079] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYTP-066 | TAPWARE: basin, tap set, wall mounted | 1 | 1 |  | [HYTP-037]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYTP-151 | TAPWARE: sink, mixer, fixture mounted | 1 | 3 |  | [HYTP-038] optional, to sink if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-031 | CHAIR: dental, electric | 1 | 1 |  | [MMDN-002]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-041 | DELIVERY SYSTEM: instrumentation, dentist, chair mounted | 1 | 1 |  | [MMDN-021]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-051 | DELIVERY SYSTEM: instrumentation, assistant, chair mounted | 1 | 1 |  | [MMDN-022]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-072 | LIGHT: dental, ceiling mounted | 1 | 1 |  | [MMDN-020]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-061 | DISPLAY SCREEN: dental, chair mounted | 1 | 3 |  | [MMDN-025] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-091 | IMAGING DEVICE: dental x-ray, wall mounted | 1 | 1 |  | [MMDN-018]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-096 | CONTROL PANEL: dental x-ray, remote activation | 1 | 1 |  | [MMDN-018]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | [ITNE-063]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1 |  | [ITNE-067]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-121 | TROLLEY: dental, procedure | 1 | 1 |  | [MMDN-016]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-059]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135] below sink if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 3 |  | [FIJO-145] optional, extent of storage dependent on service requirements and approach to consumables storage
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 3 |  | [FIJO-212] optional, over wall mounted joinery if provided; plasterboard bulkhead is also acceptable
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-211 | BRACKET: computer display screen, single, articulated, bench/desk mounted | 1 | 1 |  | [FIHR-088] articulated with smooth action, reach to be sufficient for left handed and right handed setup
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-121 | RACK: lead apron, single, wall mounted | 1 | 3 |  | [FIHR-091] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-028]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQBS-202 | STOOL: clinical areas, mobile | 2 | 1 |  | [FQBS-051]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional
DENSR-2 | Dental Surgery, Type 2 | Oral Health | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional
DENSR-2 | Dental Surgery, Type 2 | Oral Health | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 3 | Wall Finish 3 | [WLWA-010] optional, to sink if provided
DENSR-2 | Dental Surgery, Type 2 | Oral Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DENSR-2 | Dental Surgery, Type 2 | Oral Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DENSR-2 | Dental Surgery, Type 2 | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DENSR-2 | Dental Surgery, Type 2 | Oral Health | D+W | WIFX-157.04 | WINDOW: fixed, external, double glazed, sill at 900H, with integral blind | 1 | 1 | External - Window 1 | [DWWH-005 + DWWD-007] desirable
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | [HYTP-008] to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | HYDR-206 | DIRECT CONNECTION: wastewater, dental chair | 1 | 1 |  | [HYDR-001] to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELGE-002 | DIRECT CONNECTION: power, emergency | 1 | 1 |  | [ELGE-004] to dental chair
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional, depending on service requirements
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] to general room lighting
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ITIN-012 | OUTLET: data, single RJ45, in floor box | 1 | 1 |  | [ITIN-010] connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | [ELPR-006]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 3 |  | [LIFX-008] optional, under wall mounted joinery if provided
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELSW-001 | SWITCH: light | 2 | 3 |  | [ELBO-015] optional, to task lighting if provided
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-123] to x-ray unit
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | MGAS-099 | DIRECT CONNECTION: suction, dental | 1 | 1 |  | [MGAS-090] to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | Oral Health | SER | MGAS-029 | DIRECT CONNECTION: medical air | 1 | 1 |  | [MGAS-020] to dental chair, dependent on service requirements and vendor specifications
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1 |  | [FIDI-014]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | HYBA-421 | SINK: dental, single bowl | 1 | 3 |  | [HYBA-079] optional
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | HYTP-066 | TAPWARE: basin, tap set, wall mounted | 1 | 1 |  | [HYTP-037]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | HYTP-151 | TAPWARE: sink, mixer, fixture mounted | 1 | 3 |  | [HYTP-038] optional, to sink if provided
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-041 | DELIVERY SYSTEM: instrumentation, dentist, chair mounted | 1 | 1 |  | [MMDN-021]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-061 | DISPLAY SCREEN: dental, chair mounted | 1 | 3 |  | [MMDN-025] optional
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-091 | IMAGING DEVICE: dental x-ray, wall mounted | 1 | 1 |  | [MMDN-018]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1 |  | [ITNE-067]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-121 | TROLLEY: dental, procedure | 1 | 1 |  | [MMDN-016]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-031 | CHAIR: dental, electric | 1 | 1 |  | [MMDN-002]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-051 | DELIVERY SYSTEM: instrumentation, assistant, chair mounted | 1 | 1 |  | [MMDN-022]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-072 | LIGHT: dental, ceiling mounted | 1 | 1 |  | [MMDN-020]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMDN-096 | CONTROL PANEL: dental x-ray, remote activation | 1 | 1 |  | [MMDN-018]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | [ITNE-063]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-059]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135] below sink if provided
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 3 |  | [FIJO-145] optional, extent of storage dependent on service requirements and approach to consumables storage
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 3 |  | [FIJO-212] optional, over wall mounted joinery if provided; plasterboard bulkhead is also acceptable
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIHR-211 | BRACKET: computer display screen, single, articulated, bench/desk mounted | 1 | 1 |  | [FIHR-088] articulated with smooth action, reach to be sufficient for left handed and right handed setup
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FIHR-121 | RACK: lead apron, single, wall mounted | 1 | 3 |  | [FIHR-091] optional
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-028]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FQBS-202 | STOOL: clinical areas, mobile | 2 | 1 |  | [FQBS-051]
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DENSR-2 | Dental Surgery, Type 2 | Oral Health | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DINR | Dining - Patient | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DINR | Dining - Patient | Logistics / Support Services | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 2 | 1 | External - Window 1 | [DWWD-004]
DINR | Dining - Patient | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DINR | Dining - Patient | Logistics / Support Services | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
DINR | Dining - Patient | Logistics / Support Services | D+W | DOHI-144.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-031] with hold open device to support trolley movement as required
DINR | Dining - Patient | Logistics / Support Services | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] to meal trolley parking area; power requirements dependent on type of meal trolley
DINR | Dining - Patient | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208]
DINR | Dining - Patient | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 3 |  | [ELGP-208] optional, to television
DINR | Dining - Patient | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | [FIHR-006] optional
DINR | Dining - Patient | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
DINR | Dining - Patient | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10/pendulum P3 or agreed equivalent to extend under basin; significant change in colour to be avoided
DINR | Dining - Patient | Logistics / Support Services | FFE | FQBS-151 | CHAIR: dining areas | 16 | 1 |  | [FQBS-015] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
DINR | Dining - Patient | Logistics / Support Services | FFE | FQCA-082 | TROLLEY: food delivery, hot/cold | 1 | 1 |  | [FQCA-082] as required to suit food service model
DINR | Dining - Patient | Logistics / Support Services | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1 |  | [FQGE-002]
DINR | Dining - Patient | Logistics / Support Services | FFE | FQTA-226.01 | TABLE: square, 750H, 1000L | 4 | 1 |  | [FQTA-059] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
DINR | Dining - Patient | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] size, type and quantity of bins dependent on local waste management policies
DINR | Dining - Patient | Logistics / Support Services | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | [FQCW-062] size, type and quantity of bins dependent on local waste management policies
DINR | Dining - Patient | Logistics / Support Services | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DINR | Dining - Patient | Logistics / Support Services | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 3 |  | [ITBU-011] optional
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 2 | 3 |  | [ITCL-006] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | [ITCL-008] with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 3 |  | [ITCL-028] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to wall mounted telephone
DINR | Dining - Patient | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, to television, MATV outlet may also be provided depending on local ICT policies
DINR | Dining - Patient | Logistics / Support Services | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
DINR | Dining - Patient | Logistics / Support Services | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
DINR | Dining - Patient | Logistics / Support Services | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 1 | 1 |  | [FIJO-104]
DINR | Dining - Patient | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
DINR | Dining - Patient | Logistics / Support Services | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 2 | 1 | Wall Finish 2 | [WLWA-025] to meal trolley parking area
DINR | Dining - Patient | Logistics / Support Services | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
DINR | Dining - Patient | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DINR | Dining - Patient | Logistics / Support Services | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] natural light and external outlook is essential
DINR | Dining - Patient | Logistics / Support Services | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 2 | [DWWH-005] natural light and external outlook is essential
DINR | Dining - Patient | Logistics / Support Services | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 2
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] lockable or secure staff access, hold open hardware may be required
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQCL-273 | TROLLEY: dirty linen collection, large | 1 | 1 |  | [MMGE-143]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-059 | BIN: general waste, 660L (skip) | 1 | 1 |  | [FQCW-022] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-098 | BIN: recycling, paper/cardboard, 240L | 1 | 1 |  | [FQCW-029] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-238 | BIN: clinical waste, 240L | 1 | 1 |  | [FQCW-006] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010] may be provided outside of room depending on local infection control policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 3 |  | [FIJO-194] optional, for storage of small sharps bins
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FQCL-273 | TROLLEY: dirty linen collection, large | 1 | 1 |  | [MMGE-143]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FQWS-058 | BIN: general waste, 240L | 1 | 1 |  | [FQCW-017] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FQWS-059 | BIN: general waste, 660L (skip) | 2 | 1 |  | [FQCW-022] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FQWS-098 | BIN: recycling, paper/cardboard, 240L | 1 | 1 |  | [FQCW-029] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | FQWS-238 | BIN: clinical waste, 240L | 2 | 1 |  | [FQCW-006] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010] may be provided outside of room depending on local infection control policies
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 3 |  | [FIJO-194] optional, for storage of small sharps bins
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023]
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] lockable or secure staff access, hold open hardware may be required
DISP-15 | Disposal Room, 15m2 | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 2 | 1 |  | [ELGP-106] for washer sanitisers
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | ELGP-301 | ISOLATOR: one phase, wall mounted | 1 | 1 |  | [ELPR-003]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | [FIHR-029] optional, for clean linen bags
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIHR-131 | HOOK: catheter bag, wall mounted | 2 | 3 |  | [FIHR-025] optional
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIHR-141 | RACK: bed pan, wall mounted | 1 | 1 |  | [FIHR-038] quantity to be based on service requirements
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FIHR-144 | RACK: urinal/bottle, wall mounted | 1 | 1 |  | [FIHR-053] quantity to be based on service requirements
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 3 | 1 |  | [MMGE-048]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FQWS-058 | BIN: general waste, 240L | 1 | 1 |  | [FQCW-017] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | FQWS-238 | BIN: clinical waste, 240L | 1 | 1 |  | [FQCW-006] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052] hot water
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYDR-101 | TUNDISH: fixture mounted | 1 | 3 |  | [HYDR-006] optional, dependent on machine requirements
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 1 | 1 |  | [HYTP-038] to sink
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | [HYTP-008] for washer sanitisers
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 2 | 1 |  | [HYTP-013] for washer sanitisers
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, for urinalysis machine
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | MMIC-361 | WASHER SANITISER: pan | 1 | 1 |  | [MMIC-095] combined utensil/pan sanitiser may be provided
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | MMIC-362 | WASHER SANITISER: utensil | 1 | 3 |  | [MMIC-097] optional, combined utensil/pan sanitiser may be provided
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | MMLA-013 | DEVICE: analyser, urinalysis | 1 | 3 |  | [MMLA-013] optional
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-023]
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] pull handle/push plate, closer
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to sink, 1 to basin
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to basin tapware
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | [ELGP-109.1] optional, for urinalysis machine
DTUR-10 | Dirty Utility, 10m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-196] + [FIJO-197]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 2 | 1 |  | [ELGP-106] for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | ELGP-301 | ISOLATOR: one phase, wall mounted | 1 | 1 |  | [ELPR-003]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | [FIHR-029] optional, for clean linen bags
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIHR-131 | HOOK: catheter bag, wall mounted | 2 | 3 |  | [FIHR-025] optional
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIHR-141 | RACK: bed pan, wall mounted | 1 | 1 |  | [FIHR-038] quantity to be based on service requirements
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FIHR-144 | RACK: urinal/bottle, wall mounted | 1 | 1 |  | [FIHR-053] quantity to be based on service requirements
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 3 | 1 |  | [MMGE-048]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FQWS-058 | BIN: general waste, 240L | 1 | 1 |  | [FQCW-017] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | FQWS-238 | BIN: clinical waste, 240L | 1 | 1 |  | [FQCW-006] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYDR-101 | TUNDISH: fixture mounted | 1 | 3 |  | [HYDR-006] optional, dependent on machine requirements
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 1 | 1 |  | [HYTP-038] to sink
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | [HYTP-008] for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 2 | 1 |  | [HYTP-013] for washer sanitisers
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, for urinalysis machine
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | MMIC-361 | WASHER SANITISER: pan | 1 | 1 |  | [MMIC-095] combined utensil/pan sanitiser may be provided
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | MMIC-362 | WASHER SANITISER: utensil | 1 | 1 |  | [MMIC-097] combined utensil/pan sanitiser may be provided
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | MMLA-013 | DEVICE: analyser, urinalysis | 1 | 3 |  | [MMLA-013] optional
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-023]
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] pull handle/push plate, closer
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109.1] optional, for urinalysis machine
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to basin tapware
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to sink, 1 to basin
DTUR-12 | Dirty Utility, 12m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-196] + [FIJO-197]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 2 | 1 |  | [ELGP-106] for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELGP-301 | ISOLATOR: one phase, wall mounted | 1 | 1 |  | [ELPR-003]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-010]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | [FIHR-029] optional, for clean linen bags
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-131 | HOOK: catheter bag, wall mounted | 2 | 3 |  | [FIHR-025] optional
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-141 | RACK: bed pan, wall mounted | 1 | 1 |  | [FIHR-038] quantity to be based on service requirements
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-144 | RACK: urinal/bottle, wall mounted | 1 | 1 |  | [FIHR-053] quantity to be based on service requirements
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 3 | 1 |  | [MMGE-048]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-058 | BIN: general waste, 240L | 1 | 1 |  | [FQCW-017] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-238 | BIN: clinical waste, 240L | 1 | 1 |  | [FQCW-006] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052] hot water
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYDR-101 | TUNDISH: fixture mounted | 1 | 3 |  | [HYDR-006] optional, dependent on machine requirements
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 1 | 1 |  | [HYTP-038] to sink
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | [HYTP-008] for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 2 | 1 |  | [HYTP-013] for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, for urinalysis machine
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | MMIC-361 | WASHER SANITISER: pan | 1 | 1 |  | [MMIC-095] combined utensil/pan sanitiser may be provided
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | MMIC-362 | WASHER SANITISER: utensil | 1 | 1 |  | [MMIC-097] combined utensil/pan sanitiser may be provided
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | MMLA-013 | DEVICE: analyser, urinalysis | 1 | 3 |  | [MMLA-013] optional
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 6 | 1 | Wall Finish 2 | [WLWA-023]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] pull handle/push plate, closer
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | [DWGL-005] pull handle/push plate, closer
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-196] + [FIJO-197]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to sink, 1 to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to basin tapware
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109.1] optional, for urinalysis machine
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] pull handle/push plate, closer
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 1 | 1 |  | [ELGP-106] for washer sanitiser
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | [FIHR-029] optional, for clean linen bags
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIHR-131 | HOOK: catheter bag, wall mounted | 2 | 3 |  | [FIHR-025] optional
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIHR-141 | RACK: bed pan, wall mounted | 1 | 1 |  | [FIHR-038] quantity to be based on service requirements
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FIHR-144 | RACK: urinal/bottle, wall mounted | 1 | 1 |  | [FIHR-053] quantity to be based on service requirements
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 2 | 1 |  | [MMGE-048]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | FQWS-238 | BIN: clinical waste, 240L | 1 | 1 |  | [FQCW-006] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 1 | 1 |  | [HYTP-038] to sink
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] for washer sanitiser
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 1 | 1 |  | [HYTP-013] for washer sanitiser
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, for urinalysis machine
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | MMIC-361 | WASHER SANITISER: pan | 1 | 1 |  | [MMIC-095] combined utensil/pan sanitiser may be provided
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | MMLA-013 | DEVICE: analyser, urinalysis | 1 | 3 |  | [MMLA-013] optional
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-023]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to sink, 1 to basin
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to basin tapware
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-196]+[FIJO-197]
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | [ELGP-109.1] optional, for urinalysis machine
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DTUR-S | Dirty Utility, Sub | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 2 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-003] optional, to patient wc
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | [ELGP-122]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] on services panel
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELSW-001 | SWITCH: light | 2 | 3 |  | [ELBO-015] 1 optional, to optional clean up room
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-019]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MIUS-036 | ERGONOMIC AID: ultrasound, arm/wrist support sling, on articulated arm, ceiling mounted | 1 | 1 |  | [MMGE-169]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-025]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010] to entry door
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | [FQSN-006]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQSM-056 | PEDESTAL: mobile, 840H nominal, 3 equal wire basket drawers | 2 | 1 |  | [FQSM-003]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 5 | 1 |  | [ITIN-026]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-071]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-131]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MIUS-051 | IMAGING DEVICE: echocardiography | 1 | 1 |  | [MMMI-325]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MMBE-157 | TROLLEY: patient, examination, echocardiography | 1 | 1 |  | [MMBE-069]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | [MMGE-088]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MMPM-066 | MONITOR: patient, blood pressure/SPO2 | 1 | 1 |  | [MMGE-062]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1 |  | [FQSM-016]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FFE | MMTR-052 | TROLLEY: airway/intubation, 600W x 490D x 900H nom | 1 | 1 |  | [MMGE-126]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-025]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to exam light
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELGP-201 | GPO: double, wall mounted | 5 | 1 |  | [ELGP-208]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1 |  | [ELGP-223]
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to toilet/change room side
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ECHO-TOE | Echocardiography - Transoesophageal | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 2 | 1 |  | [FQCW-016] to basin and under bench
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 2 | 1 |  | [HYBA-055] hot water
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 2 | 1 |  | [HYTP-037] to sinks
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] Wet edge, inset sink
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152] over bench
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 2 | 3 |  | [FQSM-016] optional
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | D+W | DOHI-017.01 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-020] lockable
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 3 | 1 |  | 2 to sinks, 1 to basin
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 3 | 1 |  | 2 to sink tapware, 1 to basin tapware
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 2 | 1 |  | to sink tapware
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-197]
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 3 |  | [FIJO-124] optional
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 3 |  | [FIJO-124] optional
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | FFE | HYTP-236 | TAPWARE: sink, spray hose, hand-held, connection and bracket on wall | 1 | 1 |  | [HYTP-004] optional
ECL-10 | Equipment Clean-Up, 10m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 3 |  | optional; to spray hose if provided
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-018]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 3 |  | [FIDI-001] Optional
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-271 | DISPENSER: moisturiser, wall mounted | 1 | 3 |  | [FIDI-022] optional
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-291 | DISPENSER: laundry detergent, wall mounted | 1 | 1 |  | [FIDI-008] To sink.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIGE-009 | PLATFORM: equipment washing, wall mounted | 1 | 1 |  | [FIGE-009] Stainless steel, grated, height adjustable, wall mounted.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 3 |  | [HYBA-010] Refer to BHWS-B (similar). Elbow action levers or handsfree optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-055] hot water
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] to wash bay
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYGE-151 | HOSE REEL: retractable | 1 | 1 |  | [HYTP-003]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 3 |  | [HYTP-037] to basin. Elbow action levers or handsfree optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | [HYTP-008] hose reel and spray hose connection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 2 | 1 |  | [HYTP-013] hose reel and spray hose connection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] Wet edge and inset sink/s. Length to suit layout, refer RLS or project specific requirements.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 3 |  | [FIJO-117] Optional. Number to suit layout.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152] Over bench. Number to suit layout, refer RLS or project specific requirements.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 3 |  | [MMGE-119] Optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-197] shelf at 350mm AFFL or underbench, stainless steel cupboard.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYTP-236 | TAPWARE: sink, spray hose, hand-held, connection and bracket on wall | 1 | 3 |  | [HYTP-006] above sink, optional. Depends on operational/infection control policies.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 3 |  | optional; to spray hose if provided
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | DOHI-017.01 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-020] lockable
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 1 | 3 |  | [ELGP-106] utensil washer, optional
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | ELGP-301 | ISOLATOR: one phase, wall mounted | 1 | 1 |  | [ELPR-003]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 2 | 1 |  | [FQCW-016] to basin and under bench
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 3 |  | [HYBA-010] Refer BHWS-B (similar). Elbow action levers or handsfree optional.
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 2 | 1 |  | [HYBA-055] hot water
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 2 | 1 |  | [HYTP-037] to sinks
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 3 |  | [HYTP-037] to basin. Elbow action levers or handsfree optional.
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 1 | 1 |  | [HYTP-013]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] wet edge, inset sinks
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | JOCU-021 | CUPBOARD: tall, double door | 2 | 3 |  | [FIJO-117] optional
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152] over bench
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | MMIC-362 | WASHER SANITISER: utensil | 1 | 3 |  | [MMIC-097] optional
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 3 | 3 |  | [MMGE-119] optional
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | HYTP-236 | TAPWARE: sink, spray hose, hand-held, connection and bracket on wall | 1 | 3 |  | [HYTP-004] optional
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-197]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | 2 to sinks, 1 to basin
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 3 | 1 |  | 2 to sink tapware, 1 to basin tapware
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 2 | 1 |  | to sink tapware
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | D+W | DOHI-017.01 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-020] lockable
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020]
ECL-14 | Equipment Clean-Up, 14m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 3 |  | optional; to spray hose if provided
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | D+W | DOHI-017.01 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-020] lockable
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010] Refer BHWS-B (similar)
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 2 | 1 |  | [HYBA-055] hot water
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 2 | 1 |  | [HYTP-037] to sinks
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] wet edge, inset sink
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 3 |  | [FIJO-117] optional
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152] over bench
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020]
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 3 | 1 |  | 2 to sinks, 1 to basin
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 3 | 1 |  | 2 to sink tapware, 1 to basin tapware
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 2 | 1 |  | to sink tapware
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ECL-8 | Equipment Clean-Up, 8m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-197]
ENPR | Procedure Room - Endoscopy | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to corridor, cover required to vision panel if laser is to be used
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
ENPR | Procedure Room - Endoscopy | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
ENPR | Procedure Room - Endoscopy | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 3 | optional - to dirty scope room if floor plan supports direct access
ENPR | Procedure Room - Endoscopy | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 3 | to both sides
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 3
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 3
ENPR | Procedure Room - Endoscopy | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 2 | to both sides
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 2
ENPR | Procedure Room - Endoscopy | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 2
ENPR | Procedure Room - Endoscopy | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | optional - to clean scope room if floor plan supports direct access
ENPR | Procedure Room - Endoscopy | Operating | FIN | CLFI-003 | CEILING FINISH: paint, sterile areas | 1 | 1 | Ceiling Finish 2
ENPR | Procedure Room - Endoscopy | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
ENPR | Procedure Room - Endoscopy | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ENPR | Procedure Room - Endoscopy | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | alternative impermeable seamless materials may also be acceptable, confirm material selection to suit infection prevention and control requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 3 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITCL-213 | BUTTON: nurse call, orderly/porter, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 12 | 1 | Pendant 1 - Arm 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 4 | 1 | Pendant 1 - Arm 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-001 | OUTLET: carbon dioxide (CO2), on pendant services head | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITIN-014 | OUTLET: data, single RJ45, on pendant services head | 4 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | optional; required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 3 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-034 | PANEL: UPS status indicator, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMOP-303 | DISPLAY SCREEN: digital operating room (DOR) integration, on pendant arm | 1 | 1 | Pendant 2 - Arm 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | LIFX-149 | LIGHT HEAD: operating, on pendant arm | 1 | 1 | Pendant 2 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMOP-352 | PATCH PANEL: digital room operating (DOR) integration, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MGAS-002 | OUTLET: carbon dioxide (CO2), on services panel | 1 | 1 | Panel 2 | for endoscopy stack
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 3 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-176 | GPO: single, UPS, on services panel | 3 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | SER | ELSW-042 | SWITCH: light, laser in use | 1 | 1 |  | optional - to be provided if laser to be used, may be integrated on lighting control panel
ENPR | Procedure Room - Endoscopy | Operating | SER | ELSW-043 | SWITCH: light, x-ray in use | 1 | 1 |  | optional - to be provided if x-ray to be used, may be integrated on lighting control panel
ENPR | Procedure Room - Endoscopy | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 3 | 1 |  | located outside doors, optional - to be provided if laser to be used
ENPR | Procedure Room - Endoscopy | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | located outside doors, optional - to be provided if x-ray to be used
ENPR | Procedure Room - Endoscopy | Operating | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ELSW-051 | CONTROL PANEL: lighting | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | to UPS power outlets on medical services pendants
ENPR | Procedure Room - Endoscopy | Operating | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
ENPR | Procedure Room - Endoscopy | Operating | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1 |  | for removal of anaesthetic gases, rectilinear or triangular ducts are also acceptable
ENPR | Procedure Room - Endoscopy | Operating | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | MMOP-346 | CONTROL PANEL: operating lights, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | Operating | MSP | ELGP-318 | ISOLATOR: three phase, with socket outlet, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | optional - depending on equipment requirements, may be wall mounted
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | to digital operating room (DOR) display screen
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIHR-327 | BRACKET: keyboard and mouse, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-311 | CAMERA: patient observation, digital operating room (DOR) integration, ceiling mounted | 1 | 1 |  | optional
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-341 | CONTROL PANEL: digital operating room (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-302 | DISPLAY SCREEN: digital operating room (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-211 | KICKBUCKET: with stand | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-166 | TROLLEY: anaesthetic | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-162 | MACHINE: anaesthetic, with patient monitor, high acuity | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-171 | MACHINE: electrosurgical, diathermy | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-351 | PATCH PANEL: digital room operating (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-202 | STAND: bowl, single | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-371 | SYSTEM CABINET: digital integration in operating rooms (DOR) | 1 | 1 |  | located in ICT/AV cupboard (see EXIT)
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-171 | TROLLEY: mayo table | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-123 | TROLLEY: gowns/scrubs, 1220W x 610D x 1830H nominal | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQWS-005 | BIN: sharps, clinical, extra large | 1 | 1 |  | on cart
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FQWS-396 | TROLLEY: waste bag | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-331 | SPEAKER: digital operating room (DOR) integration, ceiling recessed | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-123 | STOOL: mobile, surgeon | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | plasterboard bulkhead is also acceptable
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMIC-301 | CABINET: endoscope, drying and storage, single door, pass-through | 1 | 1 |  | optional - to clean scope room if floor plan supports direct access, interlocking mechanisms requried
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | with card reader
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMBE-151 | TROLLEY: patient, transport | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-052 | TROLLEY: airway/intubation, 600W x 490D x 900H nom | 1 | 1 |  | difficult airway (DVA)
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-252 | DEVICE: processor, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-262 | DEVICE: light source, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-272 | DEVICE: insufflator, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-282 | TROLLEY: endoscopy stack, equipment | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-297 | CONTAINER: endoscope, transport | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMOP-242 | CAMERA: endoscopic | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-096 | TROLLEY: scout, 490W x 490D x 900H nom | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-108 | TROLLEY: set-up, table 1250W x 800D x 900H nom | 1 | 1 |  | with drawers
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | for biopsies, with drawers
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-077 | TROLLEY: instruments, 600W x 490D x 900H nom | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-072 | TROLLEY: equipment, 600W x 490D x 900H nom | 1 | 1 |  | endoscope equipment and accessories
ENPR | Procedure Room - Endoscopy | Operating | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | endoscope clean/dirty transport
ENPR | Procedure Room - Endoscopy | Operating | FFE | JOCU-023 | CUPBOARD: tall, double door, glazed | 3 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 |  | to wall mounted display screen
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 | Panel 2 | for connection of endoscopy stack to digital operating room (DOR) system
ENPR | Procedure Room - Endoscopy | Operating | FIN | CLFS-012 | CEILING: flush set, suspended, acoustic | 1 | 1 | Ceiling Finish 1 | finish to be suitable for sterile environments, refer to local engineering services guidance for acoustic performance (i.e. reverberation time control, sound absorption class, etc.)
ENPR | Procedure Room - Endoscopy | Operating | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | SER | ITBU-436 | CONTROL PANEL: time and elapsed time, synchronised slave clock | 1 | 1
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-121 | PENDANT: double arm, ceiling mounted | 1 | 1 | Pendant 2
ENPR | Procedure Room - Endoscopy | Operating | MSP | MMSP-181 | MEDICAL SERVICES HEAD: horizontal, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | ergonomic control handles required; configuration (horizontal or vertical) to suit services requirements; services allocations are indicative - type and number of services on the pendant to suit service requirements
ENPR | Procedure Room - Endoscopy | Operating | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 2 - Arm 2
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | tiles are also acceptable
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | tiles are also acceptable
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 1 | 1 |  | may be combined with vertical shower rail
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | 1 to basin, 1 to shower
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | type, size and placement to be confirmed at project level and coordinated with selected toilet, grabrails, assistive equipment and nurse call buttons in line with AS 1428.1 / NZS 4121
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIRT-101 | GRAB RAIL: straight, horizontal | 1 | 1 |  | for use as a towel rail while ensuring adequate strength and fixings if used for support
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FQGE-102 | CURTAIN: shower | 1 | 1 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 1 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | MGFP-041 | FLOWMETER: oxygen | 1 | 1 |  | optional; for oxygen outlet if provided; provision dependent on patient cohort requirements
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | HYSH-057 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail, accessible | 1 | 1 |  | vertical rail may be combined with horizontal grab rail
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | HYTP-052 | TAPWARE: basin, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-035] selection of basin and tapware to be coordinated to ensure compatibility
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | HYTP-252 | TAPWARE: shower, mixer, accessible | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | HYWC-033 | TOILET SUITE: patient, accessible | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIGE-037 | BENCH SEAT: fold up/down, with folding legs, wet area, wall mounted | 1 | 1 |  | in-wall structural support required; a shower chair/commode may be used in lieu of a built-in bench
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | 1 to basin, 1 to shower
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | HYTP-433 | OUTLET: water, warm | 2 | 1 |  | 1 to basin, 1 to shower
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] optional, to support grooming (i.e. shaving, hair drying, etc.); inclusion to be informed by local policies on the provision and maintenance of electrical outlets in wet areas
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | floor slope/fall to comply with relevant building code requirements
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | 1 |  | optional, may be considered in ensuites on selected specialised units to suit patient cohort requirements in line with local jurisdictional policies
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside door
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision and selection of lifter and track type to be confirmed at project level to suit patient cohort requirements and local WHS policies
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | MMBE-231 | TRACK: patient lifter, linking mechanism, ceiling mounted | 1 | 1 |  | optional; for continuation of track from adjacent bedroom if provided
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | HYBA-148 | BASIN: type C, handwashing, accessible, with integral double shelf | 1 | 1 |  | with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | D+W | DOHI-004.01 | DOOR: hinged, 1 leaf, 950 clear opening, solid | 1 | 1 | Internal - Door 1 | lock with occupancy indicator and emergency release hardware required; outward swing recommended, emergency release is required hardware to allow for outward opening if an inward swing is provided; 1 1/2 leaf door may be provided depending on clinical service requirements including transfer of patients from adjacent bedroom via patient lifting track
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to toilet; placement to be coordinated with grabrails and toilet paper dispenser to ensure reach from seated position on toilet and from the floor in case of a fall
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1
ENS-ACC | Ensuite - Accessible | Inpatient Accommodation | FFE | FIRT-127 | GRAB RAIL: toilet, 90 degree, wrap around corner, with backrest | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | tiles are also acceptable
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | tiles are also acceptable
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | 1 to basin, 1 to shower
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIRT-101 | GRAB RAIL: straight, horizontal | 1 | 1 |  | for use as a towel rail while ensuring adequate strength and fixings if used for support
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | HYBA-142 | BASIN: type C, handwashing, with integral single shelf | 1 | 1 |  | [HYBA-078] with detachable shroud to pipework and in-wall structural supports to meet weight rating/SWL and downward force requirements; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 1 | 1 |  | may be combined with vertical shower rail
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | vertical rail may be combined with horizontal grab rail
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | MGFP-041 | FLOWMETER: oxygen | 1 | 1 |  | optional; for oxygen outlet if provided; provision dependent on patient cohort requirements
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | HYWC-034 | TOILET SUITE: patient, bariatric | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | HYTP-002 | FLUSH BUTTON: toilet suite | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIRT-142 | GRAB RAIL: toilet, drop down with folding leg, with holder for toilet roll | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIRT-143 | GRAB RAIL: toilet, drop down with folding leg, with bracket for nurse call button | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIDI-282 | HOLDER: soap/shampoo, wall recessed | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | MMBE-222 | TRACK: patient lifter, traverse H-track, bariatric, ceiling mounted | 1 | 1 |  | selection of lifter and track type to be confirmed at project level to suit patient cohort requirements and local WHS policies
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | MMBE-232 | TRACK: patient lifter, linking mechanism, bariatric, ceiling mounted | 1 | 1 |  | for continuation of track from adjacent bedroom
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | 1 to basin, 1 to shower
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | HYTP-433 | OUTLET: water, warm | 2 | 1 |  | 1 to basin, 1 to shower
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] optional, to support grooming (i.e. shaving, hair drying, etc.); inclusion to be informed by local policies on the provision and maintenance of electrical outlets in wet areas
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | HYDR-021 | DRAIN: floor waste, round | 2 | 1 |  | floor slope/fall to comply with relevant building code requirements
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | 1 |  | optional, may be considered in ensuites on selected specialised units to suit patient cohort requirements in line with local jurisdictional policies
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside door
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | D+W | DOHI-103.01 | DOOR: hinged, 1 1/2 leaves, 1300 clear opening, solid | 1 | 1 | Internal - Door 1 | lock with occupancy indicator and emergency release hardware required; an outward swinging door is recommended to mitigate risk of accidental barricade in the event of a fall or loss of consciousness and to meet clearance requirements for bariatric equipment and assisting staff; door height to be to ceiling with slot required to frame for continuation of patient lifter track from adjacent bedroom
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | MMGE-016 | CHAIR: commode, bariatric | 1 | 1 |  | set out of the toilet suite and grab rails is to be tested with assistive equipment to ensure appropriate clearances
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | FFE | FIDI-308 | DISPENSER: toilet paper, to drop-down grab rail | 1 | 1
ENS-BAR | Ensuite - Bariatric | Inpatient Accommodation | SER | ITCL-130 | BUTTON: nurse call, patient to staff call, with cancel, to drop-down grab rail, wet area | 1 | 1 |  | to toilet; placement to be coordinated with grabrails and toilet paper dispenser to ensure reach from seated position on toilet and from the floor in case of a fall
ENS-BR | Ensuite - Birthing | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | DWPR-005] to ensuite side
ENS-BR | Ensuite - Birthing | Maternity | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ENS-BR | Ensuite - Birthing | Maternity | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
ENS-BR | Ensuite - Birthing | Maternity | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
ENS-BR | Ensuite - Birthing | Maternity | D+W | DOHI-007.01 | DOOR: hinged, 1 leaf, 1100 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-011] outward opening, with privacy latch and emergency release
ENS-BR | Ensuite - Birthing | Maternity | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208] to be classified as a shaver outlet
ENS-BR | Ensuite - Birthing | Maternity | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] located outside room
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] over basin
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1 |  | [FIDI-049]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1 |  | [FIRT-006]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-191 | BACK REST: toilet, accessible | 1 | 1 |  | [FIGE-011]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 2 | 1 |  | [FIRT-003]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-206 | RAIL: towel, wall mounted | 1 | 1 |  | [FIRT-016] strength and fixings, including in-wall support, to be equivalent to grab rails
ENS-BR | Ensuite - Birthing | Maternity | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ENS-BR | Ensuite - Birthing | Maternity | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] to be suitable for bare feet; tiles are also acceptable
ENS-BR | Ensuite - Birthing | Maternity | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-BR | Ensuite - Birthing | Maternity | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
ENS-BR | Ensuite - Birthing | Maternity | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
ENS-BR | Ensuite - Birthing | Maternity | SER | HYDR-021 | DRAIN: floor waste, round | 2 | 1 |  | [HYDR-004]
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 2 | 1 |  | [HYTP-020]
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039]
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYWC-033 | TOILET SUITE: patient, accessible | 1 | 1 |  | [HYWC-001] accessible suite to assist with mobility and support during labor
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | [MGAS-032]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | [MGAS-053]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
ENS-BR | Ensuite - Birthing | Maternity | FFE | MMMA-117 | SUPPORT FIXTURE: birthing, ladder, wall mounted, wet area | 1 | 3 |  | [MMMA-019] optional; strength and fixings, including in-wall support, to be equivalent to heavy duty grab rails
ENS-BR | Ensuite - Birthing | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
ENS-BR | Ensuite - Birthing | Maternity | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-034] optional, dependent on project/service requirements
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYBA-143 | BASIN: type C, handwashing, with integral double shelf | 1 | 1 |  | [HYBA-002]
ENS-BR | Ensuite - Birthing | Maternity | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-BR | Ensuite - Birthing | Maternity | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 3 | 1 |  | 1 to basin tapware, 2 to showers
ENS-BR | Ensuite - Birthing | Maternity | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 3 | 1 |  | 1 to basin tapware, 2 to showers
ENS-BR | Ensuite - Birthing | Maternity | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 2 | 1 |  | [ITCL-006] with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | Maternity | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-008] with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | Maternity | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-004] with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | DWPR-005] to birthing room side
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Panel 1 | [MMGE-001]
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | lock with occupancy indicator and emergency release hardware required; outward swing recommended, emergency release is required hardware to allow for outward opening if an inward swing is provided; clear opening requirements to be confirmed to suit patient cohort requirements and selected assistance equipment; if patient lifter track provided, door height to be to ceiling with slot required to frame to allow for continuation of track from adjacent bedroom
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | tiles are also acceptable
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | tiles are also acceptable
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | 1 to basin, 1 to shower
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIRT-101 | GRAB RAIL: straight, horizontal | 1 | 1 |  | for use as a towel rail while ensuring adequate strength and fixings if used for support
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FQGE-102 | CURTAIN: shower | 1 | 1 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | HYBA-142 | BASIN: type C, handwashing, with integral single shelf | 1 | 1 |  | [HYBA-078] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 1 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 1 | 1 |  | may be combined with vertical shower rail
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | HYWC-031 | TOILET SUITE: patient | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | vertical rail may be combined with horizontal grab rail
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | may be shared between multiple rooms and stored in central equipment store
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | MGFP-041 | FLOWMETER: oxygen | 1 | 1 |  | optional; for oxygen outlet if provided; provision dependent on patient cohort requirements
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision and selection of lifter and track type to be confirmed at project level to suit patient cohort requirements and local WHS policies for patient handling
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | MMBE-231 | TRACK: patient lifter, linking mechanism, ceiling mounted | 1 | 1 |  | optional; for continuation of track from adjacent bedroom if provided
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | 1 to basin, 1 to shower
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | HYTP-433 | OUTLET: water, warm | 2 | 1 |  | 1 to basin, 1 to shower
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] optional, to support grooming (i.e. shaving, hair drying, etc.); inclusion to be informed by local policies on the provision and maintenance of electrical outlets in wet areas
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | floor slope/fall to comply with relevant building code requirements
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | 1 |  | optional, may be considered in ensuites on selected specialised units to suit patient cohort requirements in line with local jurisdictional policies
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside door
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | optional; to patient lifter if provided
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIRT-137 | GRAB RAIL: toilet, drop down, with holder for toilet roll | 1 | 1 |  | ensure adequate in-wall supports
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIRT-138 | GRAB RAIL: toilet, drop down, with bracket for nurse call button | 1 | 1 |  | ensure adequate in-wall supports
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | FFE | FIDI-308 | DISPENSER: toilet paper, to drop-down grab rail | 1 | 1 |  | ensure adequate in-wall supports
ENS-HA | Ensuite - High Assistance | Inpatient Accommodation | SER | ITCL-130 | BUTTON: nurse call, patient to staff call, with cancel, to drop-down grab rail, wet area | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | 1 to basin, 1 to shower
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | HYTP-433 | OUTLET: water, warm | 2 | 1 |  | 1 to basin, 1 to shower
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | lock with occupancy indicator and emergency release hardware required; outward swing recommended, emergency release and hinge to allow for outward opening if an inward swing is provided
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | tiles are also acceptable
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | tiles are also acceptable
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] optional, to support grooming (i.e. shaving, hair drying, etc.); inclusion to be informed by local policies on the provision and maintenance of electrical outlets in wet areas
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | floor slope/fall to comply with relevant building code requirements
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | 1 to basin, 1 to shower
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | type, size and placement to be confirmed at project level and coordinated with selected toilet, grabrails, assistive equipment and nurse call buttons
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIRT-101 | GRAB RAIL: straight, horizontal | 1 | 1 |  | for use as a towel rail while ensuring adequate strength and fixings if used for support
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIRT-136 | GRAB RAIL: toilet, drop down | 1 | 1 |  | optional; provision dependent on patient cohort requirements; ensure adequate in-wall supports if provided
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FQGE-102 | CURTAIN: shower | 1 | 1 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | vertical rail may be combined with horizontal grab rail
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | HYBA-142 | BASIN: type C, handwashing, with integral single shelf | 1 | 1 |  | [HYBA-078] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 1 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 1 | 1 |  | may be combined with vertical shower rail
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | HYWC-031 | TOILET SUITE: patient | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | may be shared between multiple rooms and stored in central equipment store
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | 1 |  | optional, may be considered in ensuites on selected specialised units to suit patient cohort requirements in line with local jurisdictional policies
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside door
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | FFE | MGFP-041 | FLOWMETER: oxygen | 1 | 1 |  | optional; for oxygen outlet if provided; provision dependent on patient cohort requirements
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to toilet; placement to be coordinated with grabrails and toilet paper dispenser to ensure reach from seated position on toilet and from the floor in case of a fall
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1
ENS-IN-OU | Ensuite - Inboard / Outboard | Inpatient Accommodation | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature, tamper proof | 2 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-082 | DRAIN: clear out, round, tamper proof, anti-ligature, tamper proof | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | to toilet
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside room
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 1 | with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 6 | 1 | Floor Skirting | to be tiles if tiled floor provided
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 7 | 1 | Wall Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIBM-152 | MIRROR: fixed, safety glass, toughened and laminated, frameless, tamper proof, anti-ligature | 1 | 1 |  | material to be confirmed at project level to suit service requirements
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-283 | HOLDER: soap/shampoo, wall recessed, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-302 | DISPENSER: toilet paper, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-124 | GRAB RAIL: toilet, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-154 | GRAB RAIL: shower, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYBA-152 | BASIN: type C, handwashing, tamper proof, anti-ligature, with integral single shelf | 1 | 1 |  | location of thermostatic mixing valve to be determined based on need to restrict consumer access and ability to share with nearby fittings
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYSH-006 | SHOWER: fixed rose, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-069 | TAPWARE: basin, tap set, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-263 | TAPWARE: shower, tap set, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYWC-036.02 | TOILET SUITE: patient, tamper proof, anti-ligature, concealed cistern | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-257 | DISPENSER: soap, wall mounted, tamper proof, anti-ligature | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIHR-027 | HOOK: coat, collapsible, tamper proof, anti-ligature, wall mounted | 2 | 1 |  | optional; some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-066 | TRACK: curtain, shower, collapsible/load release, tamper proof, anti-ligature | 1 | 1 |  | optional
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQGE-104 | CURTAIN: shower, with load release runners | 1 | 3 |  | optional
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-004 | FLUSH BUTTON: toilet suite, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 1 | with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIBM-152 | MIRROR: fixed, safety glass, toughened and laminated, frameless, tamper proof, anti-ligature | 1 | 1 |  | material to be confirmed at project level to suit service requirements
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIDI-283 | HOLDER: soap/shampoo, wall recessed, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIDI-302 | DISPENSER: toilet paper, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIRT-124 | GRAB RAIL: toilet, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIRT-154 | GRAB RAIL: shower, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYBA-152 | BASIN: type C, handwashing, tamper proof, anti-ligature, with integral single shelf | 1 | 1 |  | location of thermostatic mixing valve to be determined based on need to restrict consumer access; typically provided behind a lockable panel in external corridor
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYSH-006 | SHOWER: fixed rose, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYTP-069 | TAPWARE: basin, tap set, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYTP-263 | TAPWARE: shower, tap set, tamper proof, anti-ligature | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYWC-036.02 | TOILET SUITE: patient, tamper proof, anti-ligature, concealed cistern | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIDI-257 | DISPENSER: soap, wall mounted, tamper proof, anti-ligature | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIHR-027 | HOOK: coat, collapsible, tamper proof, anti-ligature, wall mounted | 2 | 1 |  | optional; some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FIRT-066 | TRACK: curtain, shower, collapsible/load release, tamper proof, anti-ligature | 1 | 1 |  | optional
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature, tamper proof | 2 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYDR-082 | DRAIN: clear out, round, tamper proof, anti-ligature, tamper proof | 1 | 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | to toilet
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside room
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 5 | 1 | Floor Skirting | to be tiles if tiled floor provided
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | FQGE-104 | CURTAIN: shower, with load release runners | 1 | 3 |  | optional
ENS-MH-NE | Ensuite - Mental Health, Nested | Mental Health | FFE | HYTP-004 | FLUSH BUTTON: toilet suite, tamper proof, anti-ligature | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
ENS-NE | Ensuite - Nested | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | lock with occupancy indicator and emergency release hardware required; outward swing recommended, emergency release is required hardware to allow for outward opening if an inward swing is provided
ENS-NE | Ensuite - Nested | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | tiles are also acceptable
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | tiles are also acceptable
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | 1 to basin, 1 to shower
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | type, size and placement to be confirmed at project level and coordinated with selected toilet, grabrails, assistive equipment and nurse call buttons
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIRT-101 | GRAB RAIL: straight, horizontal | 1 | 1 |  | for use as a towel rail while ensuring adequate strength and fixings if used for support
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIRT-136 | GRAB RAIL: toilet, drop down | 1 | 1 |  | optional; provision dependent on patient cohort requirements; ensure adequate in-wall supports if provided
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FQGE-102 | CURTAIN: shower | 1 | 1 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | HYBA-142 | BASIN: type C, handwashing, with integral single shelf | 1 | 1 |  | [HYBA-078] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 1 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 1 | 1 |  | may be combined with vertical shower rail
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | HYWC-031 | TOILET SUITE: patient | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | vertical rail may be combined with horizontal grab rail
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | may be shared between multiple rooms and stored in central equipment store
ENS-NE | Ensuite - Nested | Inpatient Accommodation | FFE | MGFP-041 | FLOWMETER: oxygen | 1 | 1 |  | optional; for oxygen outlet if provided; provision dependent on patient cohort requirements
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | 1 to basin, 1 to shower
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | HYTP-433 | OUTLET: water, warm | 2 | 1 |  | 1 to basin, 1 to shower
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] optional, to support grooming (i.e. shaving, hair drying, etc.); inclusion to be informed by local policies on the provision and maintenance of electrical outlets in wet areas
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | floor slope/fall to comply with relevant building code requirements
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | 1 |  | optional, may be considered in ensuites on selected specialised units to suit patient cohort requirements in line with local jurisdictional policies
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside door
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to toilet; placement to be coordinated with grabrails and toilet paper dispenser to ensure reach from seated position on toilet and from the floor in case of a fall
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1
ENS-NE | Ensuite - Nested | Inpatient Accommodation | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1
EXIT | Exit Bay | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
EXIT | Exit Bay | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
EXIT | Exit Bay | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
EXIT | Exit Bay | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
EXIT | Exit Bay | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1
EXIT | Exit Bay | Operating | FIN | WLPR-006.07 | WALL PROTECTION: corner guards, full height | 1 | 1 | Wall Finish 2
EXIT | Exit Bay | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to operating room (see OR-GEN), cover required to vision panel if laser is to be used
EXIT | Exit Bay | Operating | D+W | DOHI-001.01 | DOOR: hinged, 1 leaf, 800 clear opening, solid | 1 | 1 | Internal - Door 2 | to ICT/AV cupboard
EXIT | Exit Bay | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides of door
EXIT | Exit Bay | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
EXIT | Exit Bay | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2
EXIT | Exit Bay | Operating | FFE | FIHR-171 | BRACKET: gas cylinder, single, wall mounted | 1 | 1 |  | clear space above the bracket for loading/unloading of the cylinder
EXIT | Exit Bay | Operating | FFE | MGGE-011.01 | CYLINDER: medical gas, C size, oxygen | 1 | 1
EXIT | Exit Bay | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
EXIT | Exit Bay | Operating | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1
EXIT | Exit Bay | Operating | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1
EXIT | Exit Bay | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1
EXIT | Exit Bay | Operating | SER | MGFP-011 | VALVE BOX: medical gases | 1 | 1
EXIT | Exit Bay | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
EXIT | Exit Bay | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
FLUO | Fluoroscopy Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
FLUO | Fluoroscopy Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
FLUO | Fluoroscopy Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
FLUO | Fluoroscopy Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
FLUO | Fluoroscopy Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to bench
FLUO | Fluoroscopy Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
FLUO | Fluoroscopy Room | Medical Imaging | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 2 | to control room (see FLUO-CTRL)
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | to support bed movement, delayed action closing
FLUO | Fluoroscopy Room | Medical Imaging | D+W | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 | Internal - Door 1 | to support bed movement
FLUO | Fluoroscopy Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | from corridor
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to imaging room side
FLUO | Fluoroscopy Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room (see FLUO-CTRL)
FLUO | Fluoroscopy Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to accessible ensuite if provided
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to ensuite side
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
FLUO | Fluoroscopy Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 3 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 1 | optional - provide if UPS required
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-176 | GPO: single, UPS, on services panel | 1 | 1 | Panel 1 | optional - extent of UPS to be confirmed to suit service and equipment requirements
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to sink tapware
FLUO | Fluoroscopy Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to sink tapware
FLUO | Fluoroscopy Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to sink
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above medical services panel
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | 1 to bench, 1 to workstation on wheels, 1 under control room window
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control room entry
FLUO | Fluoroscopy Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | outside all room entries, to automatically turn on when modality is in use
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | 1 to bench, 1 to workstation on wheels
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to clock
FLUO | Fluoroscopy Room | Medical Imaging | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | optional - to accessible ensuite if provided
FLUO | Fluoroscopy Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to patient monitor
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYTP-182 | TAPWARE: sink, tap set, wall mounted, lever handles | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 2 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | for storage of positioning aids
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIDI-136 | HOLDER: PPE, lead goggles, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | to bench
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-001 | IMAGING DEVICE: general x-ray, tube head, ceiling suspended | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-005 | IMAGING DEVICE: general x-ray, wall bucky, fixed | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-001 | IMAGING DEVICE: fluoroscopy/screening, with patient table | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-025 | GENERATOR: general x-ray, floor standing | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-026 | GENERATOR: general x-ray, wall mounted | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIXR-023 | BOARD: electrical distribution (EDB), general x-ray | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-025 | GENERATOR: fluoroscopy/screening | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | LIPO-021 | LIGHT: examination, articulated, mobile | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIGE-051 | INJECTOR: contrast, pedestal, mobile | 1 | 1 |  | optional
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-012 | CONTROL CONSOLE: fluoroscopy/screening, single display screen, control unit, mobile | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | wall mounted, may be on mobile stand
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | optional - for patient access to fluoroscopy table, provision dependent on adjustable height range of table
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | FQWS-237 | BIN: clinical waste, 120L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MMTR-063 | TROLLEY: dressing, 750W x 490D x 900H nom | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MIGE-005 | SHIELD: radiation, on pendant arm | 1 | 1 | Pendant 2 - Arm 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MIFL-061 | DISPLAY SCREEN: fluoroscopy/screening | 2 | 1 | Pendant 1 - Arm 1 | quantity dependent on equipment set up
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-051 | RACK: fluoroscopy/screening, table mounted shields, mobile | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FFE | MIFL-023 | BOARD: electrical distribution (EDB), fluoroscopy/screening | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 2 | inset section of contrasting colour to fluoroscopy machine area, indicates clear zone as mobile items may be crushed when the table is tilted
FLUO | Fluoroscopy Room | Medical Imaging | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-113 | PENDANT: single arm, on ceiling track | 1 | 1 | Pendant 1 | reach of arm to ensure screen positioning is possible to both sides of the table
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 2
FLUO | Fluoroscopy Room | Medical Imaging | MSP | MMSP-301 | TRACK: pendant, ceiling mounted | 1 | 1 | Pendant 1
FLUO | Fluoroscopy Room | Medical Imaging | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 1 - Arm 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to imaging room side
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to control room side
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | DOHI-013.05 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass | 1 | 1 | Internal - Door 1 | to imaging room
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | optional - staff entry from corridor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | over desk for portable devices
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to each door, 1 optional - to staff entry if provided
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | to imaging room entry, to automatically turn on when modality is in use
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to contrast warmer
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | to control console, extent of UPS to be confirmed to suit service and equipment requirements
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | bench height to be confirmed; adjustable height desks may be considered depending on WHS policies and coordination with services and observation window
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | display/processing workstation, on dual arm bracket
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-211 | BENCH SUPPORT: bracket | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | leg support is also acceptable
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MIFL-011 | CONTROL CONSOLE: fluoroscopy/screening, dual display screens, keyboard and mouse, control unit, desktop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MIFL-016 | COMPUTER: fluoroscopy/screening, central processing unit (CPU) | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 1 | 1 |  | for communication with patient, may be integral to control unit provided by MME vendor
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to display/processing workstation
FLUO-CTRL | Fluoroscopy Control Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | DOHI-106 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-027] optional, to equipment store
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | DOHI-145.01 | DOOR: hinged, 1 1/2 leaves, 1500 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-041]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIGE-041 | STEEL MESH: framed, ceiling mounted | 1 | 3 |  | [FIRT-017] optional, to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | FLVY-122 | FLOOR FINISH: vinyl, seamless, inset, distance markings | 1 | 1 | Floor Finish 2 | [FLVY-010]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1 |  | [FQBS-030] to arm ergometer
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQDW-134.02 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1200W | 2 | 1 |  | [FQDW-028] for arm ergometer
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 1 | 1 |  | [FQSN-007] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | [ITCL-008] 1 x to plinth, 1 x at entry door
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | [ITCL-004] 1 x to plinth, 1 x at entry door
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 3 |  | [ITCL-028] optional, to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | JOSP-151 | JOINERY UNIT: bespoke, gymnasium, tall, equipment storage, open shelves | 1 | 1 |  | [FIJO-225]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | JOSP-152 | JOINERY UNIT: bespoke, gymnasium, tall, equipment storage, enclosed | 1 | 1 |  | [FIJO-227]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-051 | EXERCISE MACHINE: stationary bicycle | 2 | 1 |  | [MMAH-002]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-052 | EXERCISE MACHINE: stationary bicycle, recumbent | 1 | 1 |  | [MMAH-003]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-061 | EXERCISE MACHINE: rowing | 1 | 1 |  | [MMAH-019]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-066 | EXERCISE MACHINE: stepping | 1 | 1 |  | [MMAH-020]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-071 | EXERCISE MACHINE: treadmill | 2 | 1 |  | [MMAH-027]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-076 | EXERCISE MACHINE: ergometer, upper body | 2 | 1 |  | [MMAH-016]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-146 | WEIGHTS: dumbbell set, with rack, floor standing | 1 | 1 |  | [FIHR-061]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-171 | PLINTH: treatment, electric | 1 | 1 |  | [MMAH-035]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 2 | 1 | Wall Finish 2 | [WLWA-020]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] quantity to suit equipment requirements
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | D+W | DOHI-106 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-027] optional, to equipment store
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | D+W | DOHI-145.01 | DOOR: hinged, 1 1/2 leaves, 1500 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-041]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-010]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 4 | 1 |  | [FIDI-001]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FIGE-041 | STEEL MESH: framed, ceiling mounted | 3 | 3 |  | [FIRT-017] optional, to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FIHR-029 | HOOK: equipment, wall mounted | 6 | 1 |  | [FIHR-029] to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 3 | 1 |  | [FIHR-033] to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FIN | FLVY-122 | FLOOR FINISH: vinyl, seamless, inset, distance markings | 1 | 1 | Floor Finish 2 | [FLVY-010]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FQGE-101 | CURTAIN: privacy screen | 3 | 1 |  | [FQGE-010] to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | [FQSN-007] to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 4 | 1 |  | [ITCL-008] 3 x to plinth, 1 x at entry door
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 4 | 1 |  | [ITCL-004] 3 x to plinth, 1 x at entry door
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 3 | 3 |  | [ITCL-028] optional, to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026] to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 3 | 1 |  | [ITNE-008+MMGE-164]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | JOSP-152 | JOINERY UNIT: bespoke, gymnasium, tall, equipment storage, enclosed | 1 | 1 |  | [FIJO-227]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | MMAH-051 | EXERCISE MACHINE: stationary bicycle | 1 | 1 |  | [MMAH-002]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | MMAH-071 | EXERCISE MACHINE: treadmill | 1 | 1 |  | [MMAH-027]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | MMAH-101 | PARALLEL BARS: height adjustable, manual | 1 | 1 |  | [MMAH-001] bariatric capacity to be determine based on service requirements
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | MMAH-116 | STEPS: rehabilitation, corner | 1 | 1 |  | [MMAH-044]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | MMAH-146 | WEIGHTS: dumbbell set, with rack, floor standing | 1 | 1 |  | [FIHR-061]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | MMAH-171 | PLINTH: treatment, electric | 2 | 1 |  | [MMAH-035]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | MMAH-176 | PLINTH: treatment, electric, wide | 1 | 1 |  | [MMAH-033]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 2 | 1 | Wall Finish 1 | [WLWA-004]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | FFE | FIRT-051 | TRACK: curtain, privacy | 3 | 1 |  | [FIRT-032]
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] quantity to suit equipment requirements
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 3 | 1 |  | [ELGP-109] to plinths
GYAH-ID | Gymnasium, Individual Treatment | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 9 | 1 |  | [ELGP-208] to plinths
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to female change room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-165.01 | DOOR: hinged, 1 1/2 leaves, 1500 clear opening, fully glazed, framed | 1 | 1 | Internal - Door 1 | [DWGL-040] to lobby/ waiting; lockable, restricted access
HYDP | Hydrotherapy Pool | Allied Health | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 1 | 3 |  | [ELGP-106] optional, for motorised pool blanket
HYDP | Hydrotherapy Pool | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
HYDP | Hydrotherapy Pool | Allied Health | FIN | FLSK-073 | SKIRTING: tiles, to match floor tiles, coved | 12 | 1 | Floor Skirting | [FLSK-004]
HYDP | Hydrotherapy Pool | Allied Health | FIN | FLTI-005 | FLOOR FINISH: tiles, ceramic, non-slip, wet area, barefoot | 2 | 1 | Floor Finish 2 | [FLGE-010]
HYDP | Hydrotherapy Pool | Allied Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
HYDP | Hydrotherapy Pool | Allied Health | SER | HYDR-021 | DRAIN: floor waste, round | 16 | 1 |  | [HYDR-004] every 3-4 metres on concourse
HYDP | Hydrotherapy Pool | Allied Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] for washing down concourse
HYDP | Hydrotherapy Pool | Allied Health | SER | ITBU-131 | HEAD END: public address system | 1 | 1 |  | [ITBU-020]
HYDP | Hydrotherapy Pool | Allied Health | SER | ITBU-132 | CONTROL PANEL: public address system | 1 | 1 |  | [ITBU-009] for announcements and music
HYDP | Hydrotherapy Pool | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 4 | 1 |  | [ITCL-004] 1 each side of pool
HYDP | Hydrotherapy Pool | Allied Health | FFE | MMAH-302 | POOL COVER: hydrotherapy, powered, on roller, fixed | 1 | 3 |  | [MMAH-032] optional, power requirements dependent on selected model
HYDP | Hydrotherapy Pool | Allied Health | FFE | MMBE-301 | LIFTER: patient hoist, seated pool transfer, hydrotherapy, fixed, floor mounted | 1 | 1 |  | [MMAH-017] weight limit requirement to be confirmed dependent on service requirements
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 1 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | FIN | WLFI-021 | WALL FINISH: tiles, ceramic | 3 | 1 | Wall Finish 1 | [WLWA-011] to pool and all walls
HYDP | Hydrotherapy Pool | Allied Health | SER | ELGP-104 | GPO: single, wall mounted, waterproof, power available indicator | 4 | 1 |  | [ELGP-113]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 2 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 3 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 4 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-157.01 | WINDOW: fixed, external, double glazed, sill at 900H | 1 | 1 | External - Window 2 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-157.01 | WINDOW: fixed, external, double glazed, sill at 900H | 1 | 1 | External - Window 1 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-163.01 | WINDOW: fixed, external, double glazed, sill at 1800H | 1 | 1 | External - Window 3 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-163.01 | WINDOW: fixed, external, double glazed, sill at 1800H | 1 | 1 | External - Window 4 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-165.01 | DOOR: hinged, 1 1/2 leaves, 1500 clear opening, fully glazed, framed | 1 | 1 | External - Door 1 | [DWGL-040] external emergency exit
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 3 | [DWSC-003] to male change room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 4 | [DWSC-003] to cleaner's room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 5 | [DWSC-003] to pool equipment room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 6 | [DWSC-003] to pool plant room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | External - Door 2 | [DWSC-003] optional, for alternate external emergency exit; may be required by building code
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 4 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 5 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 6 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | External - Door 2 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to change room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to change room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 4 | [DWPR-005] to cleaner's room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 5 | [DWPR-005] to equipment room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | External - Door 2 | [DWPR-001] to external side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 6 | [DWPR-001] to plant room side
HYDP | Hydrotherapy Pool | Allied Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-002]
HYDP | Hydrotherapy Pool | Allied Health | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 2
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV | Interview Room | Ambulatory Care | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
INTV | Interview Room | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
INTV | Interview Room | Ambulatory Care | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
INTV | Interview Room | Ambulatory Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
INTV | Interview Room | Ambulatory Care | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
INTV | Interview Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
INTV | Interview Room | Ambulatory Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
INTV | Interview Room | Ambulatory Care | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
INTV | Interview Room | Ambulatory Care | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 6 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
INTV | Interview Room | Ambulatory Care | FFE | FQBS-251 | ARMCHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-010]
INTV | Interview Room | Ambulatory Care | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 3 |  | [FQGE-002] optional
INTV | Interview Room | Ambulatory Care | FFE | FQTA-202 | TABLE: square, 450H, 600L | 2 | 1 |  | [FQTA-075]
INTV | Interview Room | Ambulatory Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 3 |  | [ITCL-008] optional, + indicator button & light
INTV | Interview Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional, + indicator button & light
INTV | Interview Room | Ambulatory Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
INTV | Interview Room | Ambulatory Care | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-050]
INTV | Interview Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
INTV | Interview Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
INTV | Interview Room | Ambulatory Care | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 2 | [ITSE-038] optional to second egress door
INTV | Interview Room | Ambulatory Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-005] optional, for staff egress
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-001] to room side
INTV | Interview Room | Ambulatory Care | D+W | WIFX-057.01 | WINDOW: fixed, internal, double glazed, sill at 900H | 1 | 1 | External - Window 1 | [DWWH-005]
INTV | Interview Room | Ambulatory Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 4 | 1 |  | [FQBS-058]
INTV | Interview Room | Ambulatory Care | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1 |  | [FQBS-041]
INTV | Interview Room | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 6 | 1 | Floor Skirting
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side as required
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 3
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 3 | External - Window 1 | optional; natural light and external outlook is desirable; consider placement and room orientation for patient privacy; requirements for glazing to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 3 | External - Window 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FIBM-020 | WHITEBOARD: fixed, magnetic, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FIBM-057 | NOTICE BOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQDW-104.02 | WORKSTATION: straight, fixed height, 720H, 750D x 1200W | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to corridor side as required
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | secondary egress
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | if tamper proof and anti-ligature finish required flush set ceiling to be provided
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to room side
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2 | optional; provision to suit security and egress requirements
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDFI-026 | DOOR GLAZING FINISH: vision panel, privacy film | 1 | 1 | Internal - Door 1 | optional; as required to suit privacy requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; provision to suit security and egress requirements
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 10 | 1 | Floor Skirting
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 8 | 1 | Wall Finish 2
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
LAUN-MH | Laundry - Mental Health | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to both sides
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 3 | Internal - Door 2 | optional; secondary egress; provision dependent on local WHS policies; requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | 1 to washing machine; 1 to dryer
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature, tamper proof | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | to washing machine
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-432 | OUTLET: water, hot | 1 | 1 |  | to washing machine
LAUN-MH | Laundry - Mental Health | Mental Health | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | D+W | WIFX-009.01 | WINDOW: fixed, internal, single glazed, sill at 1200H | 1 | 1 | Internal - Window 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-101 | WASHING MACHINE: laundry, domestic, front loading | 1 | 1 |  | quantity to suit service requirements
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-111 | DRYER: laundry, domestic | 1 | 1 |  | quantity to suit service requirements
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-121 | PLINTH: washing machine, domestic | 1 | 1 |  | for improved reaching height to machine opening; as required to suit configuration and machines selected; washing machine may alternatively be floor standing
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQCL-141 | STACKING KIT: washing machine and dryer, domestic | 1 | 1 |  | as required to suit configuration and machines selected; dryer may alternatively be on a plinth or floor standing
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on service requirements, operational models for waste management and local IPC policies
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | HYBA-411 | SINK: laundry, single bowl | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby fixtures
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | HYTP-184 | TAPWARE: sink, tap set, wall mounted, tamper proof, anti-ligature | 1 | 1 |  | selection of sink and tapware should be coordinated to ensure compatibility
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | lockable
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | lockable
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | FFE | JOSH-105 | SHELF UNIT: wall mounted, pigeonholes | 1 | 1
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink tapware
LAUN-MH | Laundry - Mental Health | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | ELSW-001 | SWITCH: light | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | ELGP-202 | GPO: double, wall mounted, power available indicator | 2 | 1 |  | to washing machine and dryer
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | to washing machine, requirements to be confirmed to suit selected appliance
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | HYTP-432 | OUTLET: water, hot | 1 | 1 |  | to washing machine, requirements to be confirmed to suit selected appliance
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | MEEX-021 | GRILLE: exhaust, ceiling mounted | 1 | 1 |  | exhaust requirements are to be confirmed to suit the selected appliances.
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | FQCL-101 | WASHING MACHINE: laundry, domestic, front loading | 1 | 1 |  | commercial appliances may be considered to suit service requirements
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | FQCL-111 | DRYER: laundry, domestic | 1 | 1 |  | commercial appliance may be considered to suit service requirements
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | FQCL-121 | PLINTH: washing machine, domestic | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | FQCL-131 | PLINTH: dryer, domestic | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | HYBA-411 | SINK: laundry, single bowl | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | may be lockable for storage of detergents/chemicals depending on operational requirements
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | 1 to tall cupboard, 1 to wall mounted cupboards
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | ELGP-202 | GPO: double, wall mounted, power available indicator | 1 | 3 |  | optional, for ironing facilities if provided depending on service requirements
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 2
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to laundry sink tapware
LAUN-PT | Laundry - Patient / Visitor | Neonatal Care | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to laundry sink
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLFI-003 | CEILING FINISH: paint, sterile areas | 1 | 1 | Ceiling Finish 2 | [CLFS-005]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-005]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 3 | [CLTI-002] inset area above machine as requried
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | D+W | DOSP-202 | GATE: hinged, 1 leaf, 900 clear opening | 1 | 1 | Internal - Door 1 | [DWGE-013]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-122]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 4 | 1 |  | [ELBO-001]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-131 | BUTTON: last person out | 1 | 1 |  | [ELBO-019]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | [FIDI-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 2 | 1 |  | [FIHR-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-322 | BRACKET: keyboard and mouse, fixed height, wall mounted | 1 | 1 |  | [FIHR-093]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | FLVY-103 | FLOOR FINISH: vinyl, seamless, standard slip resistance, static dissipative | 1 | 1 | Floor Finish 1 | [FLVY-001] floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQCL-251 | TROLLEY: clean linen, small | 1 | 1 |  | [MMGE-110]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITAV-141 | MICROPHONE: AV system, ceiling mounted | 2 | 1 |  | [ITAV-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 2 | 1 |  | [ITAV-057] for patient's own music, individual to each bunker from control room, hearing loop required to speakers
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 1 |  | [ITNE-073] wall mounted
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 6 | 1 |  | [ITCL-012 + FIHR-077] 1 x optional, for total body irradiation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 11 | 3 |  | [ITIN-011] 1 x optional, to additional patient observation camera if provided
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] workstation on wheels is also acceptable
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITNE-121 | COMPUTER: single display screen, all-in-one | 1 | 1 |  | [ITNE-066]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] to wall mounted computer, may be wireless
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOBE-031 | BENCH: 600D, laminate | 3 | 1 |  | [FIJO-058]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-140]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-135]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-031 | JOINERY UNIT: bespoke, radiotherapy, tall, applicator storage | 1 | 1 |  | [FIJO-165] custom joinery is required for vendor specific electron cones, including sliding rails, shelving to be reinforced for electron shields
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-032 | JOINERY UNIT: bespoke, radiotherapy, tall, horizontal patient device storage | 3 | 1 |  | [FIJO-166] wide span shelving to be reinforced
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-033 | JOINERY UNIT: bespoke, radiotherapy, tall, vertical patient device storage | 2 | 1 |  | [FIJO-167]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-041 | JOINERY UNIT: bespoke, radiotherapy, wall mounted, laser enclosure | 3 | 1 |  | [FIJO-231]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | LIFX-214 | LIGHT: illuminated sign, beam on/off | 1 | 1 |  | [LIFX-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-001 | RADIOTHERAPY DEVICE: treatment, linear accelerator | 1 | 1 |  | [MMRA-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-031 | SENSOR: entry detection, light curtain, radiotherapy bunker, | 1 | 1 |  | [MMRA-012]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-041 | LASER: patient positioning, radiotherapy, overhead | 1 | 1 |  | [MMRA-015]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-044 | LASER: patient positioning, radiotherapy, lateral, MRI compatible | 2 | 1 |  | [MMRA-016]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-046 | LASER: patient positioning, radiotherapy, sagittal, MRI compatible | 1 | 1 |  | [MMRA-017]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-071 | DEVICE: surface guided radiation therapy system, ceiling mounted | 3 | 1 |  | [MMRA-008 + FIHR-089] as required for respiratory gating / motion management / surface guidance systems, to suit service requirements
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-106 | DEVICE: tester, radiotherapy, daily QA | 1 | 1 |  | [MMRA-011]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-191 | ACCESS PANEL: penetration, medical physics port | 1 | 1 |  | [MMRA-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLFI-001 | WALL FINISH: paint | 14 | 1 | Wall Finish 1 | [WLWA-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 16 | 1 | Wall Finish 2 | [WLWA-022]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 9 | 1 | Wall Protection | [WLPR-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 1 |  | [MMRA-013] radiotherapy information, ceiling mounted
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 5 | 1 |  | [ELGP-220.1] to wall mounted lasers
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-123]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 12 | 1 |  | [ELGP-125] 1 x to ceiling mounted laser, 1 x optional, to additional patient observation camera if provided
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | [ELGP-223]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 1 | [DWPR-001] to room side
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | Internal - Door 1 | [DWSC-003] optional
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 1 | 1 |  | [ELGP-106] to linear accelerator computer cabinet
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | [ELBO-001] may be integral to linear accelerator control console
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 2 | 1 |  | [FIHR-067] to patient observation monitors
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FQBS-171 | CHAIR: office, ergonomic | 5 | 1 |  | [FQBS-018]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 1 | 1 |  | [ITAV-014]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1 |  | [ITAV-057] may be bench mounted, or integrated with microphone
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITCL-381 | DISPLAY SCREEN: patient observation | 2 | 1 |  | [ITNE-074]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 8 | 1 |  | [ITIN-036] quantity to suit computer and display screen requirements
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITIN-056 | OUTLET: data, USB, wall mounted | 1 | 1 |  | [ITIN-055] connection for music to bunker
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-071] for access to local network including patient records and images for planning and reporting
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] for patient observation cameras to control pan, tilt and zoom; may be custom control depending on camera system
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | [FIJO-031]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-211 | BENCH SUPPORT: bracket | 5 | 1 |  | [FIHR-080] legs are also acceptable, quantity to be confirmed to achieve required support, ensure location does not impact leg clearance at workstations
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-221 | BENCH SUPPORT: end panel | 2 | 1 |  | [FIJO-213]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-251 | CAP: cable access | 8 | 1 |  | [FIJO-099]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 5 | 1 |  | [FIJO-145]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-011 | CONTROL CONSOLE: linear accelerator, dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1 |  | [MMRA-010]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-016 | COMPUTER: linear accelerator, central processing unit (CPU) | 6 | 1 |  | [MMRA-009] quantity to be confirmed based on vendor and equipment requirements; current provision allows for 1 x linear accelerator control system, 1 x record and verify system, and 2-4 x imaging and patient set up systems (e.g. gating and patient positioning).
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-021 | SYSTEM CABINET: linear accelerator | 1 | 1 |  | [MMRA-007] size, configuration and location to be confirmed by vendor
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-191 | ACCESS PANEL: penetration, medical physics port | 1 | 1 |  | [MMRA-006]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 14 | 1 |  | [ELGP-223] quantity to suit computer and display screen requirements
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELGP-201 | GPO: double, wall mounted | 10 | 1 |  | [ELGP-208]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-002]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminum skirting acceptable if carpet tiles are provided
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1 |  | [FQBS-043] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FQGE-002 | ARTWORK: wall mounted | 2 | 1 |  | [FQGE-002]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FQTA-202 | TABLE: square, 450H, 600L | 2 | 1 |  | [FQTA-075] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 3 |  | [ITCL-006] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 3 |  | [ITCL-028] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to television, MATV outlet may also be provided depending on local ICT policies
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | MMGE-019 | CHAIR: patient | 2 | 1 |  | [MMGE-019] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] natural light and external outlook is essential
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] 1 to television, 2 to room
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-011]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry door
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | D+W | DOHI-244.01 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-061]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] 1 to television, 2 to room
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | FIHR-046 | RACK: magazine/pamphlet, wall mounted | 1 | 3 |  | [FIHR-045] optional
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminum skirting acceptable if carpet tiles are provided
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | FQBS-351 | LOUNGE: 1 seat | 2 | 1 |  | [FQBS-039] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | FQBS-352 | LOUNGE: 2 seat | 2 | 1 |  | [FQBS-043] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | FQGE-002 | ARTWORK: wall mounted | 2 | 1 |  | [FQGE-002]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | FQTA-202 | TABLE: square, 450H, 600L | 2 | 1 |  | [FQTA-075] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 3 |  | [ITCL-006] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 3 |  | [ITCL-028] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to television, MATV outlet may also be provided depending on local ICT policies
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | MMGE-019 | CHAIR: patient | 2 | 1 |  | [MMGE-019] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-011]
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] natural light and external outlook is essential
LNGE-20 | Lounge - Patient / Visitor, 20m2 | Clinical Support Set 2 | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry door
MAMMO | Mammography Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
MAMMO | Mammography Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
MAMMO | Mammography Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MAMMO | Mammography Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
MAMMO | Mammography Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
MAMMO | Mammography Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
MAMMO | Mammography Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
MAMMO | Mammography Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
MAMMO | Mammography Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
MAMMO | Mammography Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 1
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
MAMMO | Mammography Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
MAMMO | Mammography Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
MAMMO | Mammography Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above services panel
MAMMO | Mammography Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to imaging equipment and control console
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1 |  | to workstation
MAMMO | Mammography Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies
MAMMO | Mammography Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to workstation
MAMMO | Mammography Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
MAMMO | Mammography Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lighting
MAMMO | Mammography Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | outside all room entries, to automatically turn on when modality is in use
MAMMO | Mammography Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | to imaging equipment and control console
MAMMO | Mammography Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
MAMMO | Mammography Room | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
MAMMO | Mammography Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
MAMMO | Mammography Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | to workstation
MAMMO | Mammography Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MIMM-046 | RACK: mammography paddles, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MIMM-001 | IMAGING DEVICE: mammography | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
MAMMO | Mammography Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | MIMM-011 | CONTROL CONSOLE: mammography, single display screen, keyboard and mouse, control unit | 1 | 1
MAMMO | Mammography Room | Medical Imaging | FFE | FQSM-057 | PEDESTAL: mobile, 840H nominal, 4 equal wire basket drawers | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
MAMMO | Mammography Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
MAMMO | Mammography Room | Medical Imaging | D+W | DOHI-104.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, shielded | 1 | 1 | Internal - Door 1
MAMMO | Mammography Room | Medical Imaging | FFE | MMGE-019 | CHAIR: patient | 1 | 1
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-003]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FIDI-072 | DISPENSER: sticker roll, wall mounted | 1 | 3 |  | [FIDI-052] optional
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FQSM-152 | STORAGE SOLUTION: modular system, mobile, 400D x 600W x 2100H nominal | 3 | 1 |  | [FQSM-046] type and quantity of storage options to be determined based on service requirements
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FQSM-202 | SHELVING UNIT: mobile, adjustable shelves, 400D x 600W x 2100H nominal | 2 | 1 |  | [FQSM-048] type and quantity of storage options to be determined based on service requirements
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | FQWS-271 | BIN: pharmaceutical waste, 20L | 1 | 1 |  | [FQCW-061]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to drug fridge, for temperature monitoring
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 3 |  | [ITIN-026] optional, for future provision of automated dispensing cabinets
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 3 |  | [ITSE-012] optional, provision and placement dependent on local policies
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 1 | 1 |  | [FIJO-157]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 5 | 1 |  | [FIJO-108]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008] under wall mounted joinery
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | MMPH-002 | SAFE: dangerous drugs, wall mounted, medium | 1 | 1 |  | [MMGE-087] size and quantity to be based on service requirements
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FFE | MMPH-024 | FRIDGE: medication/vaccine, 1000L nom, double door | 1 | 1 |  | [MMGE-034] size and quantity to be based on service requirements
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 3 | [WLWA-020] extent dependent on type and height storage solution
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023] extent dependent on type and height storage solution
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 3 |  | [ELGP-223] optional, for future provision of automated dispensing cabinets
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to drug fridge
MED-14 | Medication Room, 14m2 | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
MEET-15 | Meeting Room, 15m2 | Administration | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
MEET-15 | Meeting Room, 15m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to AV system control panel if provided
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-046 | OUTLET: data, quadruple RJ45, wall mounted | 1 | 3 |  | [ITIN-046] optional, to AV/videoconferencing equipment if provided; AV outlet type and quantity to be confirmed to suit equipment selection and service requirements
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 3 |  | [ITIN-143] optional; services may be wall mounted depending on furniture layout and anticipated room use informed by service requirements
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 1 | 3 |  | [ITIN-145] optional; softwired for connection to floor box or wall mounted services
MEET-15 | Meeting Room, 15m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to corridor side, extent dependent on equipment movement in adjacent area
MEET-15 | Meeting Room, 15m2 | Administration | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] may be lockable
MEET-15 | Meeting Room, 15m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
MEET-15 | Meeting Room, 15m2 | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
MEET-15 | Meeting Room, 15m2 | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
MEET-15 | Meeting Room, 15m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MEET-15 | Meeting Room, 15m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MEET-15 | Meeting Room, 15m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
MEET-15 | Meeting Room, 15m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MEET-15 | Meeting Room, 15m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
MEET-15 | Meeting Room, 15m2 | Administration | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | [FIHR-006] optional, provision to suit service requirements and local ICT policies
MEET-15 | Meeting Room, 15m2 | Administration | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 3 |  | [ITAV-006] optional; provision to suit service requirements and local ICT policies; where provided, item may be wall mounted, table mounted or portable
MEET-15 | Meeting Room, 15m2 | Administration | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 3 |  | [ITAV-063] optional, provision to suit service requirements and local ICT policies
MEET-15 | Meeting Room, 15m2 | Administration | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 3 |  | [ITAV-051] optional, provision to suit service requirements and local ICT policies
MEET-15 | Meeting Room, 15m2 | Administration | FFE | ITAV-160 | SOUNDBAR: AV system, camera, speaker and microphone, wall mounted | 1 | 3 |  | [ITAV-090] optional, provision to suit service requirements and local ICT policies; AV equipment configurations may vary and camera, speaker and microphone functions may be provided by individual items
MEET-15 | Meeting Room, 15m2 | Administration | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | [ITAV-062] optional, provision to suit service requirements and local ICT policies
MEET-15 | Meeting Room, 15m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MEET-15 | Meeting Room, 15m2 | Administration | FFE | FQBS-142 | CHAIR: meeting room, stackable | 8 | 1 |  | [FQBS-059]
MEET-15 | Meeting Room, 15m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MEET-15 | Meeting Room, 15m2 | Administration | FFE | FQTA-124.04 | TABLE: rectangular, 750H, 1200L x 900W, folding, on casters | 2 | 1 |  | [FQTA-086] 1 with services box if floor box provided
MEET-15 | Meeting Room, 15m2 | Administration | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 1 |  | [FIJO-194]
MEET-15 | Meeting Room, 15m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
MEET-15 | Meeting Room, 15m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 3 | 3 |  | [ELGP-208] optional, to AV/videoconferencing equipment if provided; quantity to be confirmed to suit equipment selection and service requirements
MEET-15 | Meeting Room, 15m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 2 | 3 |  | [ELGP-103] optional; services may be wall mounted depending on furniture layout and anticipated room use informed by service requirements
MEET-15 | Meeting Room, 15m2 | Administration | SER | ELGP-128 | GPO: single, in desk box | 4 | 3 |  | optional; softwired for connection to floor box or wall mounted services
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to room booking control panel if provided
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-019 | OUTLET: data, single RJ45, in desk box | 1 | 3 |  | optional; softwired for connection to floor box or wall mounted services
MEET-15 | Meeting Room, 15m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1 |  | [ITIN-022] optional; services may be wall mounted depending on furniture layout and anticipated room use informed by service requirements
MEET-20 | Meeting Room, 20m2 | Administration | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
MEET-20 | Meeting Room, 20m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to room booking control panel if provided
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | [ITIN-021] to microphone array
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] to AV/videoconferencing equipment; AV outlet type and quantity to be confirmed to suit equipment selection and service requirements
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 3 |  | [ITIN-143] optional; services may be wall mounted depending on furniture layout and anticipated room use informed by service requirements
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 1 | 3 |  | [ITIN-145] optional; softwired for connection to floor box or wall mounted services
MEET-20 | Meeting Room, 20m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MEET-20 | Meeting Room, 20m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MEET-20 | Meeting Room, 20m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
MEET-20 | Meeting Room, 20m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MEET-20 | Meeting Room, 20m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
MEET-20 | Meeting Room, 20m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to corridor side, extent dependent on equipment movement in adjacent area
MEET-20 | Meeting Room, 20m2 | Administration | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] may be lockable
MEET-20 | Meeting Room, 20m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
MEET-20 | Meeting Room, 20m2 | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
MEET-20 | Meeting Room, 20m2 | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
MEET-20 | Meeting Room, 20m2 | Administration | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1 |  | [ITAV-063] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-20 | Meeting Room, 20m2 | Administration | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITAV-051] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-20 | Meeting Room, 20m2 | Administration | FFE | ITAV-160 | SOUNDBAR: AV system, camera, speaker and microphone, wall mounted | 1 | 1 |  | [ITAV-090] configuration of ICT/AV equipment to suit service requirements and local ICT policies, camera, speaker and microphone functions may be provided by individual items
MEET-20 | Meeting Room, 20m2 | Administration | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | [ITAV-062] optional, provision to suit service requirements and local ICT policies
MEET-20 | Meeting Room, 20m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MEET-20 | Meeting Room, 20m2 | Administration | FFE | FQBS-142 | CHAIR: meeting room, stackable | 12 | 1 |  | [FQBS-059]
MEET-20 | Meeting Room, 20m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MEET-20 | Meeting Room, 20m2 | Administration | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 1 |  | [FIJO-194]
MEET-20 | Meeting Room, 20m2 | Administration | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-20 | Meeting Room, 20m2 | Administration | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | [ITAV-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies; item may be wall mounted, table mounted or portable
MEET-20 | Meeting Room, 20m2 | Administration | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 3 |  | [FQGE-005] optional
MEET-20 | Meeting Room, 20m2 | Administration | FFE | FQTA-126.04 | TABLE: rectangular, 750H, 1500L x 900W, folding, on casters | 2 | 1 |  | [FQTA-086] 1 with services box if floor box provided
MEET-20 | Meeting Room, 20m2 | Administration | FFE | ITAV-142 | MICROPHONE: AV system, ceiling mounted, array | 1 | 1 |  | [ITAV-071] optional, may be provided to support microphone in soundbar as required; may be recessed in ceiling
MEET-20 | Meeting Room, 20m2 | Administration | FFE | ITAV-132 | CAMERA: AV system, video conferencing, wall mounted | 1 | 1 |  | [ITNE-004] optional, multidirectional, may be provided to support camera in soundbar as required
MEET-20 | Meeting Room, 20m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] to AV/videoconferencing equipment; quantity to be confirmed to suit equipment selection and service requirements
MEET-20 | Meeting Room, 20m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
MEET-20 | Meeting Room, 20m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 2 | 3 |  | [ELGP-103] optional; services may be wall mounted depending on furniture layout and anticipated room use informed by service requirements
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 3 |  | [ITIN-022] optional; services may be wall mounted depending on furniture layout and anticipated room use informed by service requirements
MEET-20 | Meeting Room, 20m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to AV system control panel
MEET-30 | Meeting Room, 30m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQBS-142 | CHAIR: meeting room, stackable | 18 | 1 |  | [FQBS-059]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | [ITAV-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies; item may be wall mounted, table mounted or portable
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1 |  | [ITAV-063] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITAV-051] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-132 | CAMERA: AV system, video conferencing, wall mounted | 1 | 1 |  | [ITNE-004] multidirectional, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-142 | MICROPHONE: AV system, ceiling mounted, array | 1 | 1 |  | [ITAV-071] may be recessed in ceiling, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 4 | 1 |  | [ITAV-057] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | [ITAV-062] optional, provision to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to AV system control panel
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | [ITIN-021] to microphone array
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 2 | 1 |  | [ITIN-022]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] to AV/videoconferencing equipment; AV outlet type and quantity to be confirmed to suit equipment selection and service requirements
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 2 | 1 |  | [ITIN-143]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 2 | 1 |  | [ITIN-145] softwired for connection to floor box or wall mounted services
MEET-30 | Meeting Room, 30m2 | Administration | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1 |  | [FIJO-011]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | [FIHR-065]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 2 | [WLWA-004]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 12 | 3 | Wall Finish 1 | [WLWA-001] optional; to suit acoustic requirements
MEET-30 | Meeting Room, 30m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to corridor side, extent dependent on equipment movement in adjacent area
MEET-30 | Meeting Room, 30m2 | Administration | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] may be lockable
MEET-30 | Meeting Room, 30m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
MEET-30 | Meeting Room, 30m2 | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
MEET-30 | Meeting Room, 30m2 | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQTA-126.04 | TABLE: rectangular, 750H, 1500L x 900W, folding, on casters | 3 | 1 |  | [FQTA-086] 2 with services boxes to connect to floor boxes
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 4 | 1 |  | [ELGP-103]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] to AV/videoconferencing equipment; quantity to be confirmed to suit equipment selection and service requirements
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to room booking control panel if provided
MEET-55 | Meeting Room, 55m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 2 | 1 | Internal - Door 1 | [DWPR-001] to room side
MEET-55 | Meeting Room, 55m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MEET-55 | Meeting Room, 55m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
MEET-55 | Meeting Room, 55m2 | Administration | D+W | DOHI-212.01 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-052] may be lockable
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MEET-55 | Meeting Room, 55m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQBS-142 | CHAIR: meeting room, stackable | 42 | 1 |  | [FQBS-059]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQTA-124.04 | TABLE: rectangular, 750H, 1200L x 900W, folding, on casters | 4 | 1 |  | [FQTA-086] quantity, type and size to be confirmed to suit service requirements
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | [ITAV-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies; item may be wall mounted or portable
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1 |  | [ITAV-063] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITAV-051] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-131 | CAMERA: AV system, video conferencing, ceiling mounted | 1 | 3 |  | [ITAV-064] optional, multidirectional, to rear of room for view of speaker, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-132 | CAMERA: AV system, video conferencing, wall mounted | 1 | 1 |  | [ITNE-004]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-142 | MICROPHONE: AV system, ceiling mounted, array | 2 | 1 |  | [ITAV-071] may be recessed in ceiling, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 6 | 1 |  | [ITAV-057]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-191 | LECTERN: mobile, with microphone | 1 | 1 |  | [FQDW-006 and ITAV-014]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | [ITAV-062] optional, provision to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 3 |  | [ITIN-011] optional, to speaker camera at rear of room if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to room booking control panel if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 2 | 1 |  | [ITIN-021] to microphone array
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 2 | 3 |  | [ITIN-022] optional, 1 to each floor box if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] to AV/videoconferencing equipment; AV outlet type and quantity to be confirmed to suit equipment selection and service requirements
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 2 | 3 |  | [ITIN-143] optional, to support flexible layout, location to be confirmed to suit service requirements
MEET-55 | Meeting Room, 55m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 2 | [WLWA-004]
MEET-55 | Meeting Room, 55m2 | Administration | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 12 | 3 | Wall Finish 1 | [WLWA-001] optional; to suit acoustic requirements
MEET-55 | Meeting Room, 55m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to corridor side, extent dependent on equipment movement in adjacent area
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1 |  | [ITIN-143] to lectern
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] to AV/videoconferencing equipment; quantity to be confirmed to suit equipment selection and service requirements
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 4 | 1 |  | [ELGP-103] to floor box for lectern
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 8 | 3 |  | [ELGP-103] optional, 4 to each floor box if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to AV system control panel
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1 |  | [ITIN-022] to floor box for lectern
MEET-9 | Meeting Room, 9m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
MEET-9 | Meeting Room, 9m2 | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
MEET-9 | Meeting Room, 9m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MEET-9 | Meeting Room, 9m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
MEET-9 | Meeting Room, 9m2 | Administration | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] may be lockable
MEET-9 | Meeting Room, 9m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MEET-9 | Meeting Room, 9m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MEET-9 | Meeting Room, 9m2 | Administration | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | [FIHR-006] optional, provision to suit service requirements and local ICT policies
MEET-9 | Meeting Room, 9m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MEET-9 | Meeting Room, 9m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MEET-9 | Meeting Room, 9m2 | Administration | FFE | FQBS-142 | CHAIR: meeting room, stackable | 4 | 1 |  | [FQBS-059]
MEET-9 | Meeting Room, 9m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MEET-9 | Meeting Room, 9m2 | Administration | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 3 |  | [ITAV-006] optional; provision to suit service requirements and local ICT policies; where provided, item may be wall mounted, table mounted or portable
MEET-9 | Meeting Room, 9m2 | Administration | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 3 |  | [ITAV-063] optional, provision to suit service requirements and local ICT policies
MEET-9 | Meeting Room, 9m2 | Administration | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 3 |  | [ITAV-051] optional, provision to suit service requirements and local ICT policies
MEET-9 | Meeting Room, 9m2 | Administration | FFE | ITAV-160 | SOUNDBAR: AV system, camera, speaker and microphone, wall mounted | 1 | 3 |  | [ITAV-090] optional, provision to suit service requirements and local ICT policies; AV equipment configurations may vary and camera, speaker and microphone functions may be provided by individual items
MEET-9 | Meeting Room, 9m2 | Administration | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | [ITAV-062] optional, provision to suit service requirements and local ICT policies
MEET-9 | Meeting Room, 9m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to AV system control panel if provided
MEET-9 | Meeting Room, 9m2 | Administration | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
MEET-9 | Meeting Room, 9m2 | Administration | SER | ITIN-046 | OUTLET: data, quadruple RJ45, wall mounted | 1 | 3 |  | [ITIN-046] optional, to AV/videoconferencing equipment if provided; AV outlet type and quantity to be confirmed to suit equipment selection and service requirements
MEET-9 | Meeting Room, 9m2 | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
MEET-9 | Meeting Room, 9m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
MEET-9 | Meeting Room, 9m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to corridor side, extent dependent on equipment movement in adjacent area
MEET-9 | Meeting Room, 9m2 | Administration | FFE | FQTA-126.01 | TABLE: rectangular, 750H, 1500L x 900W | 1 | 1 |  | [FQTA-023]
MEET-9 | Meeting Room, 9m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
MEET-9 | Meeting Room, 9m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 3 | 3 |  | [ELGP-208] optional, to AV/videoconferencing equipment if provided; quantity to be confirmed to suit equipment selection and service requirements
MEET-9 | Meeting Room, 9m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to room booking control panel if provided
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | [DWGL-005] to anteroom; door seals required
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] to corridor; door seals required
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 2 | 1 |  | [ELGP-106] power to evisceration and dissection tables (if not part of table configuration). Required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 8 | 1 |  | [ELGP-106] 4x outlets on evisceration and dissection tables, dependent on service requirements and vendor specifications. Required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1x general room lights, 1x task light over dissection bench. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 2 | 1 |  | [FIDI-031] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIHR-029 | HOOK: equipment, wall mounted | 1 | 3 |  | [FIHR-029] optional, for lifter straps/slings
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 2 | 1 |  | [FIHR-016]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIRT-101 | GRAB RAIL: straight, horizontal | 2 | 1 |  | [FIRT-005] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIRT-116 | GRAB RAIL: U-shaped, floor mounted | 1 | 1 |  | [FIRT-046] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004] junction with evisceration table to be considered to prevent water ingress
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 3 |  | [FQBS-051] optional, dependent on project requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-057 | BIN: general waste, 120L | 1 | 1 |  | [FQCW-015]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-237 | BIN: clinical waste, 120L | 1 | 1 |  | [FQCW-004]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-055]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYDR-025 | DRAIN: floor waste, linear | 2 | 1 |  | [HYDR-003]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYGE-031 | TROUGH: boot wash, floor recessed | 1 | 1 |  | [HYGE-026]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYGE-151 | HOSE REEL: retractable | 1 | 1 |  | [HYTP-003]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYSH-111 | STATION: emergency, safety, shower and eye wash, wall mounted | 1 | 1 |  | [HYTP-023]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 2 | 1 |  | [HYTP-038]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-176 | TAPWARE: sink, tap set, fixture mounted, laboratory | 1 | 1 |  | [HYTP-034] to dissection table
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-421 | TAPWARE: hosecock, wall mounted | 1 | 1 |  | [HYTP-012] to hose reel
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016] IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | ITNE-121 | COMPUTER: single display screen, all-in-one | 1 | 1 |  | [ITNE-066] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge and integral sink
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | LIFX-101 | LIGHT: task, ceiling recessed | 1 | 1 |  | [LIFX-037] task lighting over dissection table, articulated task light is also acceptable dependent on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | LIFX-131 | LIGHT: procedure, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-014] hardwired, a second light may be provided dependent on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | MEEX-122 | DIRECT CONNECTION: exhaust, downdraft | 1 | 3 |  | [MEEX-017] optional, on evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMGE-201 | SCALES: digital, benchtop | 1 | 1 |  | [MMGE-185]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMMT-001 | TABLE: evisceration, autopsy, fixed, height adjustable | 1 | 3 |  | [MMLA-086] bariatric capacity to be determined based on service requirements, services on table to be considered: suction capabilities (built-in or provided), power to table, power outlets (if not on table), down draft (optional, built-in to table), water connection (built-in to table)
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMMT-006 | TABLE: dissection, fixed, height adjustable | 1 | 1 |  | [MMLA-087] with integral sink
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 2 | 1 |  | [MMGE-119]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 8 | 1 | Wall Finish 2 | [WLWA-023]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | WIFX-008.01 | WINDOW: fixed, internal, single glazed, sill at 1050H | 1 | 1 | Internal - Window 1 | [DWOB-005] to observation area if provided
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | MGAS-063 | OUTLET: suction, wall mounted | 2 | 1 |  | [MGAS-060] on evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-406 | TAPWARE: spout, wall mounted | 1 | 1 |  | [HYTP-028] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-416 | TAPWARE: tap, wall mounted | 1 | 1 |  | [HYTP-030] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | [MMBE-071] optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMBE-266 | SLING: patient lifter, supine | 1 | 3 |  | [MMBE-071] optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 3 |  | [MMBE-071] optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to computer. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | [HYTP-008] connection only, to evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 2 | 1 |  | [HYTP-013] connection only, to evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink, 1 to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYDR-211 | DIRECT CONNECTION: wastewater, evisceration/autopsy table | 2 | 1 |  | [HYDR-001] 1 to autopsy table, 1 to evisceration table; confirm requirements at project level
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | 1 to hosecock, 1 to boot trough tapware
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] IP rated to suit AS/NZS wet zone requirements
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 3 | 1 |  | [ELGP-106] 1 to each refrigerator; required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] IP rated to suit AS/NZS wet zone requirements
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | FIHR-029 | HOOK: equipment, wall mounted | 1 | 1 |  | [FIHR-029] for lifter straps/slings
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | HYGE-151 | HOSE REEL: retractable | 1 | 1 |  | [HYTP-003]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | HYTP-421 | TAPWARE: hosecock, wall mounted | 1 | 1 |  | [HYTP-012]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | ITBU-401 | ALARM: equipment monitoring, temperature | 1 | 1 |  | [ITBU-001] temperature monitoring, alarm and BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016] temperature monitoring, IP rated to suit AS/NZS wet zone requirements, 1 to each refrigerator, BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | MMMT-026 | TROLLEY: mortuary, hydraulic stacking | 1 | 1 |  | [MMGE-133] bariatric capacity to be confirmed based on service requirements
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | MMMT-054 | FRIDGE: body holding, 3 tier | 3 | 1 |  | [MMGE-183] bariatric capacity to be confirmed based on service requirements; power and BMS requirements to be confirmed by project
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-025]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FIN | WLPR-046.03 | WALL PROTECTION: crash rail, to 900 AFFL | 2 | 1 | Wall Protection | [WLPR-021]
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | [MMBE-071] mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | MMBE-266 | SLING: patient lifter, supine | 1 | 1 |  | [MMBE-070] mobile lifter may be used, bariatric capacity to be confirmed based on service requirements; control may be suspended from motor or wall mounted depending on model
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | [MMBE-070] mobile lifter may be used, bariatric capacity to be confirmed based on service requirements; control may be suspended from motor or wall mounted depending on model
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to lifter
MOR-BH | Mortuary - Body Holding | Mortuary and Autopsy | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to hosecock
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] for task lighting
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-018]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 2 | 1 | Floor Skirting | [FLSK-010]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | FQDW-134.09 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 2400W | 1 | 1 |  | [FQDW-045] length to accommodate A3 landscape mortuary register
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026] 1 outlet for telephone
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] to underside of overhead cupboards
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | FIN | WLFI-001 | WALL FINISH: paint | 2 | 1 | Wall Finish 1 | [WLWA-004]
MOR-BR | Mortuary - Body Reception | Mortuary and Autopsy | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] emergency power may be provided depending on operational policies and service requirements
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-003] to viewing room side
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to waiting room
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | D+W | DOHI-212.01 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-052] to corridor
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010] heavy/domestic fabric is acceptable
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FFE | MMMT-021 | TROLLEY: mortuary, transport, concealment | 1 | 1 |  | [MMGE-186]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | D+W | WIFX-006.01 | WINDOW: fixed, internal, single glazed, sill at 750H | 1 | 1 | Internal - Window 1 | [DWOB-005]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-031]
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-003] to viewing room side
MOR-VR | Mortuary - Viewing Room | Mortuary and Autopsy | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-003] to waiting room side
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-003] to room side
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to viewing room; lockable
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] to corridor, lockable
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 6 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FFE | FQBS-116 | CHAIR: visitor, waiting areas | 3 | 1 |  | [FQBS-032]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1 |  | [FQBS-043]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1 |  | [FQGE-002]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FFE | FQTA-101 | TABLE: rectangular, 450H, 900L x 600W | 1 | 1 |  | [FQTA-034]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | WIFX-006.01 | WINDOW: fixed, internal, single glazed, sill at 750H | 1 | 1 | Internal - Window 1 | [DWOB-005]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-003] to corridor side
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-003] to room side
MOR-W | Mortuary - Waiting | Mortuary and Autopsy | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109]
MRI | MRI Room | Medical Imaging | FIN | CLFS-012 | CEILING: flush set, suspended, acoustic | 1 | 1 | Ceiling Finish 1 | ceiling tiles are also acceptable, grid must be MRI compatable
MRI | MRI Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
MRI | MRI Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MRI | MRI Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Finish 1 | [FLSK-010]
MRI | MRI Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Skirting
MRI | MRI Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
MRI | MRI Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2
MRI | MRI Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1 | 1 to emergency power circuit, 1 to UPS circuit
MRI | MRI Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | MRI compatible
MRI | MRI Room | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
MRI | MRI Room | Medical Imaging | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 1
MRI | MRI Room | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
MRI | MRI Room | Medical Imaging | MSP | ELGP-176 | GPO: single, UPS, on services panel | 2 | 1 | Panel 1 | extent of UPS to be confirmed to suit service and equipment requirements
MRI | MRI Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | above medical services panel
MRI | MRI Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
MRI | MRI Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lighting
MRI | MRI Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
MRI | MRI Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | to patient observation cameras
MRI | MRI Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | optional - 1 to slave patient monitor, 1 to FMRI monitor
MRI | MRI Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to clock
MRI | MRI Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 2 | 1 |  | to patient observation cameras
MRI | MRI Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
MRI | MRI Room | Medical Imaging | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | optional - to laser positioning light if provided
MRI | MRI Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 2 | 1 |  | optional - 1 to slave patient monitor, 1 to FMRI monitor
MRI | MRI Room | Medical Imaging | FIN | MIMR-112 | ACCESS PANEL: penetration, waveguide port, MRI | 1 | 1 | Wall Finish 3 | 2 to control room, 2 to anaesthetic preparation area
MRI | MRI Room | Medical Imaging | SER | MEGE-061 | SENSOR: oxygen depletion | 1 | 1 |  | connection to BMS to be confirmed by project
MRI | MRI Room | Medical Imaging | FFE | MIMR-001 | IMAGING DEVICE: MRI, gantry | 1 | 1 |  | refer to manufacturer's requirements for quench pipes and other associated equipment
MRI | MRI Room | Medical Imaging | FFE | MIMR-006 | TABLE: patient, MRI | 1 | 1 |  | mobile table with electronic docking capability, detachable table also acceptable, use of detachable table may negate need for additional MRI compatible patient transport trolley
MRI | MRI Room | Medical Imaging | FFE | MIMR-036 | PIPE: quench, MRI | 1 | 1 |  | installed to manufacturer's specifications with minimal bends
MRI | MRI Room | Medical Imaging | FFE | MIMR-041 | TROLLEY: patient, transport, MRI compatible | 1 | 1
MRI | MRI Room | Medical Imaging | FFE | MIMR-046 | MACHINE: anaesthetic, MRI compatible | 1 | 1
MRI | MRI Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FIN | MIMR-101 | CABIN: radio frequency shielding, faraday cage, MRI | 1 | 1 | Wall Finish 4
MRI | MRI Room | Medical Imaging | FFE | JOCU-021 | CUPBOARD: tall, double door | 5 | 1 |  | all materials and hardware to be MRI compatible
MRI | MRI Room | Medical Imaging | FFE | ITAV-151 | SPEAKER: AV system, ceiling mounted | 1 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | MMRA-042 | LASER: patient positioning, radiotherapy, overhead, MRI compatible | 1 | 1 |  | optional - as required for radiotherapy planning
MRI | MRI Room | Medical Imaging | FFE | MIGE-052 | INJECTOR: contrast, MRI compatible, pedestal, mobile | 1 | 1
MRI | MRI Room | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | MRI compatible
MRI | MRI Room | Medical Imaging | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | optional - to slave patient monitor if provided, MRI compatible
MRI | MRI Room | Medical Imaging | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 1 |  | optional - for functional MRI, MRI compatible
MRI | MRI Room | Medical Imaging | FFE | ITCL-437 | CAMERA: patient observation, MRI compatible, wall mounted | 2 | 1
MRI | MRI Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1
MRI | MRI Room | Medical Imaging | FFE | FIHR-341 | BRACKET: display screen, single, articulated, wall mounted | 1 | 1 |  | optional - to functional MRI display screen if provided, MRI compatible
MRI | MRI Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1 |  | optional - depending on service requirements, MRI compatible
MRI | MRI Room | Medical Imaging | D+W | DOSP-141 | DOOR: hinged, 1 leaf, 1200 clear opening, radio frequency shielding, MRI imaging room | 1 | 1 | Internal - Door 1
MRI | MRI Room | Medical Imaging | D+W | WIFX-008.04 | WINDOW: fixed, internal, single glazed, sill at 1050H, radio frequency shielding | 1 | 1 | Internal - Window 1 | for observation from control room (see MRI-CTRL)
MRI | MRI Room | Medical Imaging | D+W | WIFX-008.04 | WINDOW: fixed, internal, single glazed, sill at 1050H, radio frequency shielding | 1 | 1 | Internal - Window 2 | for observation from anaesthetic preparation area
MRI | MRI Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | MRI compatible, to both sides of door
MRI | MRI Room | Medical Imaging | D+W | MIMR-121 | BARRIER: MRI, retractable belt, wall mounted | 1 | 1 | Internal - Door 1
MRI | MRI Room | Medical Imaging | FFE | ITBU-443 | CLOCK: analogue display, electric, MRI compatible, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to slave patient monitor
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 6 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to printer
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to each door
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 3 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | to slave patient monitor
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | to control console, extent of UPS to be confirmed to suit service and equipment requirements
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to CCTV display screen if provided
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | optional - for anaesthetic assist
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional - to CCTV display screen if provided
MRI-CTRL | MRI Control Room | Medical Imaging | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | MEGE-081 | ALARM: oxygen depletion | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-341 | BRACKET: display screen, single, articulated, wall mounted | 1 | 1 |  | optional - to CCTV display screen if provided
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to display/processing workstation
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITCL-381 | DISPLAY SCREEN: patient observation | 1 | 1 |  | optional - for physiological monitoring
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | leg support is also acceptable
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 3 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | to slave patient monitor
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to MRI control CPU, 1 to PACS CPU
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | display/processing workstation, on dual arm bracket
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 3 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITNE-311 | PRINTER: desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | bench height to be confirmed; adjustable height desks may be considered depending on WHS policies and coordination with services and observation window
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | leg support is also acceptable
MRI-CTRL | MRI Control Room | Medical Imaging | FIN | MIMR-112 | ACCESS PANEL: penetration, waveguide port, MRI | 1 | 1 | Wall Finish 2
MRI-CTRL | MRI Control Room | Medical Imaging | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIMR-032 | BUTTON: quench, MRI | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FQSN-341 | LOCKER: floor standing, 4 door | 2 | 1 |  | optional
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | optional
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | optional
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIMR-011 | CONTROL CONSOLE: MRI, dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | MIMR-016 | COMPUTER: MRI, central processing unit (CPU) | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | vendor supplied sound system
MRI-CTRL | MRI Control Room | Medical Imaging | SER | HYGE-351 | CONTROL PANEL: water pump, cooling | 1 | 1
MRI-CTRL | MRI Control Room | Medical Imaging | D+W | WIFX-008.04 | WINDOW: fixed, internal, single glazed, sill at 1050H, radio frequency shielding | 1 | 1 | Internal - Window 1 | for observation of patient from control room
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] lockable
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional; where only one hook is provided ensure lower height is nominated for accessibility
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 2 | 1 | Floor Finish 1 | [FLCP-006]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FQBS-106 | CHAIR: visitor, office areas | 3 | 1 |  | [FQBS-029]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FQDW-134.04 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1600W | 1 | 1 |  | [FQDW-054]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007] lockable
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FQSN-285 | CABINET: floor standing, 1200H nominal, tambour unit | 1 | 1 |  | [FQSN-135] lockable, size to suit service requirements
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] to workstation
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-050]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] two display screens may be provided depending on service requirements
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] inclusion dependent on location of room, may not be required if located in staff only area, provision to suit local WHS policies
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | D+W | WIFX-002.01 | WINDOW: fixed, internal, single glazed, sill at skirting level | 1 | 1 | Internal - Window 1 | [DWOB-002] sidelight to door, extent of glazing to suit requirements for privacy and borrowed light
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | D+W | AFWFI-021 | WINDOW FINISH: privacy film | 1 | 1 | Internal - Window 1
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | FFE | FQTA-425.01 | TABLE: round, 750H, 900 diameter | 1 | 1 |  | [FQTA-055]
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] over workstation, for charging portable devices
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] to workstation
OFF-1P-12 | Office - 1 Person, 12m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] to meeting table
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] lockable
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | D+W | AFWFI-021 | WINDOW FINISH: privacy film | 1 | 1 | Internal - Window 1
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | D+W | WIFX-002.01 | WINDOW: fixed, internal, single glazed, sill at skirting level | 1 | 1 | Internal - Window 1 | [DWOB-002] sidelight to door, extent of glazing to suit requirements for privacy and borrowed light
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional; where only one hook is provided ensure lower height is nominated for accessibility
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FQBS-106 | CHAIR: visitor, office areas | 2 | 1 |  | [FQBS-029]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FQDW-134.04 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1600W | 1 | 1 |  | [FQDW-054]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007] lockable
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FQSN-285 | CABINET: floor standing, 1200H nominal, tambour unit | 1 | 1 |  | [FQSN-135] lockable, size to suit service requirements
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-050]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] two display screens may be provided depending on service requirements
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] to workstation
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] over workstation, for charging portable devices
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] to workstation
OFF-1P-9 | Office - 1 Person, 9m2 | Administration | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] inclusion dependent on location of room, may not be required if located in staff only area, provision to suit local WHS policies
OFF-2P | Office - 2 Person | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
OFF-2P | Office - 2 Person | Administration | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] lockable
OFF-2P | Office - 2 Person | Administration | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
OFF-2P | Office - 2 Person | Administration | D+W | AFWFI-021 | WINDOW FINISH: privacy film | 1 | 1 | Internal - Window 1
OFF-2P | Office - 2 Person | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
OFF-2P | Office - 2 Person | Administration | D+W | WIFX-002.01 | WINDOW: fixed, internal, single glazed, sill at skirting level | 1 | 1 | Internal - Window 1 | [DWOB-002] sidelight to door, extent of glazing to suit requirements for privacy and borrowed light
OFF-2P | Office - 2 Person | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
OFF-2P | Office - 2 Person | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OFF-2P | Office - 2 Person | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OFF-2P | Office - 2 Person | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 2 | 1 | Floor Finish 1 | [FLCP-006]
OFF-2P | Office - 2 Person | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
OFF-2P | Office - 2 Person | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
OFF-2P | Office - 2 Person | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 3 |  | [FIBM-019] optional
OFF-2P | Office - 2 Person | Administration | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional; where only one hook is provided ensure lower height is nominated for accessibility
OFF-2P | Office - 2 Person | Administration | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018]
OFF-2P | Office - 2 Person | Administration | FFE | FQDW-134.04 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1600W | 2 | 1 |  | [FQDW-054]
OFF-2P | Office - 2 Person | Administration | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 2 | 1 |  | [FQSM-007] lockable
OFF-2P | Office - 2 Person | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OFF-2P | Office - 2 Person | Administration | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-050]
OFF-2P | Office - 2 Person | Administration | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007] two display screens may be provided depending on service requirements
OFF-2P | Office - 2 Person | Administration | FFE | FQBS-106 | CHAIR: visitor, office areas | 2 | 1 |  | [FQBS-029]
OFF-2P | Office - 2 Person | Administration | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | [ELGP-208] 2 to each workstation
OFF-2P | Office - 2 Person | Administration | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] 1 over each workstation, for charging portable devices
OFF-2P | Office - 2 Person | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
OFF-2P | Office - 2 Person | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] 2 to each workstation
OFF-2P | Office - 2 Person | Administration | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] inclusion dependent on location of room, may not be required if located in staff only area, provision to suit local WHS policies
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | [ELGP-130] to printer; UPS to be provided if downtime computer required
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | [ELGP-235] UPS to be provided if downtime computer required. location of outlets to meet local operational/WHS requirements
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional, above bench
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIHR-322 | BRACKET: keyboard and mouse, fixed height, wall mounted | 1 | 1 |  | [FIHR-093] to patient flow monitor
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] to patient flow monitor
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FQBS-171 | CHAIR: office, ergonomic | 4 | 1 |  | [FQBS-018]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 1 |  | [ITBU-013]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016] 1 x to patient flow monitor, 1 x to printer
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | 1 |  | [ITIN-036] location of outlets to meet local operational/WHS requirements
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-071 | TELEPHONE: handset, desktop | 4 | 1 |  | [ITNE-049]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 4 | 1 |  | [ITNE-007]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] to patient flow monitor
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] below desk, wall mounted is also acceptable
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITSE-071 | CHARGER: security, duress, wireless devices, wall mounted | 2 | 3 |  | [ITCL-037] optional
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-031]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOBE-211 | BENCH SUPPORT: bracket | 3 | 1 |  | [FIHR-080] legs are also acceptable, quantity to be confirmed to achieve required support, ensure location does not impact leg clearance at workstations
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOBE-251 | CAP: cable access | 4 | 1 |  | [FIJO-099]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 6 | 1 |  | [FIJO-152] overhead joinery may be configured to include pigeon holes for record storage as required
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | LIFX-108 | LIGHT: task, integral to joinery | 6 | 1 |  | [LIFX-008] under wall mounted joinery
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 1 | 3 |  | [ELGP-208] optional, for duress charging station if provided
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] for BYO devices, to be located above desk for easy access
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 7 | 1 |  | [ELGP-208] location of outlets to meet local operational/WHS requirements
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 3 | Internal - Window 1 | [DWOB-002] optional
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | [CLGE-001] Between above bench joinery and ceiling
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 4 | 1 |  | [ELGP-208] 2 per workspace
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] Pelmet lighting
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019] Between bench and overbench joinery
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018] For standing height bench, use ergonomic high chair for standring height
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 1 |  | [ITCL-001] Located in corridor adjacent, number to suit design
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026] Number of outlets per faceplate as per ICT policy. 1 per workspace
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-049]
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007] Consider location of harddrive, if below bench add bracket
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-020] standing or seating height, refer RLS or project specific requirements
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 4 | 1 |  | [FIJO-152] Above bench, number to suit layout. Refer to RLS or project specific requirements
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] For above bench joinery
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
OFF-WI-5 | Office - Write-up, 5m2 | Clinical Support Set 2 | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | [WLPR-010] Align heights of corner guards with other corridor elements
OFF-WS | Office - Workstation | Administration | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 1 | 1 |  | [ITIN-145]
OFF-WS | Office - Workstation | Administration | SER | ITIN-181 | CABLE TRAY: power and data outlets, softwired, under bench/desk | 1 | 1 |  | [FQDW-075] configuration for separation of power and data cables may be required depending on local ICT policies
OFF-WS | Office - Workstation | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OFF-WS | Office - Workstation | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OFF-WS | Office - Workstation | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
OFF-WS | Office - Workstation | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
OFF-WS | Office - Workstation | Administration | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
OFF-WS | Office - Workstation | Administration | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
OFF-WS | Office - Workstation | Administration | FFE | FQDW-134.04 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1600W | 1 | 1 |  | [FQDW-054]
OFF-WS | Office - Workstation | Administration | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007] lockable
OFF-WS | Office - Workstation | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 3 |  | [FQCW-016] optional, quantity to be rationalised between multiple workstations
OFF-WS | Office - Workstation | Administration | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | [ITNE-050] optional
OFF-WS | Office - Workstation | Administration | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] two display screens may be provided depending on service requirements
OFF-WS | Office - Workstation | Administration | FFE | FQDW-082 | WORKSTATION SYSTEM: partition, acoustic | 1 | 1 |  | [FQDW-043] a modesty panel may also be required depending on overall room layout, this may be an extension of the acoustic panel or a separate additional panel depending on selected workstation system
OFF-WS | Office - Workstation | Administration | SER | ELGP-128 | GPO: single, in desk box | 2 | 1 |  | for charging portable devices
OFF-WS | Office - Workstation | Administration | SER | ELGP-129 | GPO: single, in cable tray | 4 | 1
OFF-WS | Office - Workstation | Administration | SER | ITIN-017 | OUTLET: data, single RJ45, in cable tray | 2 | 1
OPG | OPG Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
OPG | OPG Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
OPG | OPG Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
OPG | OPG Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
OPG | OPG Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
OPG | OPG Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
OPG | OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
OPG | OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | to imaging area
OPG | OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | to control workstation area
OPG | OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to both sides
OPG | OPG Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
OPG | OPG Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
OPG | OPG Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
OPG | OPG Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
OPG | OPG Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
OPG | OPG Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | 1 close to imaging device, 1 to control workstation area
OPG | OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to imaging equipment
OPG | OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation
OPG | OPG Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
OPG | OPG Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lighting
OPG | OPG Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | outside all room entries, to automatically turn on when modality is in use
OPG | OPG Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | to imaging device
OPG | OPG Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
OPG | OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to imaging device
OPG | OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation
OPG | OPG Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | as required for imaging device connection to remote activation panel
OPG | OPG Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | MMTR-001.02 | TROLLEY: stainless steel, 490W x 490D x 900H nom, 2 tier | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
OPG | OPG Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
OPG | OPG Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | MIOC-001 | IMAGING DEVICE: orthopantomogram (OPG) | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | MIOC-011 | CONTROL PANEL: orthopantomogram (OPG), remote activation | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | ITNE-341 | SCANNER: desktop, document, flatbed, desktop | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | located close to medical services panel
OPG | OPG Room | Medical Imaging | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 1 | 1
OPG | OPG Room | Medical Imaging | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
OPG | OPG Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
OPG | OPG Room | Medical Imaging | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | optional - for storage of consumables and PPE items to meet service requirements
OPG | OPG Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 2 | 1
OR-GEN | Operating Room - General | Operating | FIN | CLFI-003 | CEILING FINISH: paint, sterile areas | 1 | 1 | Ceiling Finish 2
OR-GEN | Operating Room - General | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
OR-GEN | Operating Room - General | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 2 | inset section of contrasting colour to sterile zone
OR-GEN | Operating Room - General | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
OR-GEN | Operating Room - General | Operating | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | alternative impermeable seamless materials may also be acceptable, confirm material selection to suit infection prevention and control requirements
OR-GEN | Operating Room - General | Operating | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to anaesthetic preparation room (see ANAES), cover required to vision panel if laser is to be used
OR-GEN | Operating Room - General | Operating | D+W | DOHI-213.03 | DOOR: hinged, 2 leaves, 1700 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | to exit bay (see EXIT), cover required to vision panel if laser is to be used
OR-GEN | Operating Room - General | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 1 | delayed action closing
OR-GEN | Operating Room - General | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 2 | delayed action closing
OR-GEN | Operating Room - General | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
OR-GEN | Operating Room - General | Operating | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 2 | to allow for opening either one or both leaves of the door
OR-GEN | Operating Room - General | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
OR-GEN | Operating Room - General | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 2 | to both sides
OR-GEN | Operating Room - General | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 3 | to store - sterile stock, access provided for stock delivery where sterile stock is not directly adjacent to operating room
OR-GEN | Operating Room - General | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 3 | to both sides
OR-GEN | Operating Room - General | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 3
OR-GEN | Operating Room - General | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 3
OR-GEN | Operating Room - General | Operating | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | optional, to store - sterile stock
OR-GEN | Operating Room - General | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | optional - provided for theatres where obstetric procedures are undertaken or services are otherwise required separately to those in the medical services pendants
OR-GEN | Operating Room - General | Operating | SER | ELSW-042 | SWITCH: light, laser in use | 1 | 1 |  | optional - to be provided if laser to be used, may be integrated on lighting control panel
OR-GEN | Operating Room - General | Operating | SER | ELSW-043 | SWITCH: light, x-ray in use | 1 | 1 |  | optional - to be provided if x-ray to be used, may be integrated on lighting control panel
OR-GEN | Operating Room - General | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 3 | 1 |  | located outside doors, optional - to be provided if laser to be used
OR-GEN | Operating Room - General | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | located outside doors, optional - to be provided if x-ray to be used
OR-GEN | Operating Room - General | Operating | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ITCL-211 | BUTTON: nurse call, orderly/porter, with cancel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ELSW-051 | CONTROL PANEL: lighting | 2 | 1
OR-GEN | Operating Room - General | Operating | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | to UPS power outlets on medical services pendants
OR-GEN | Operating Room - General | Operating | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1
OR-GEN | Operating Room - General | Operating | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
OR-GEN | Operating Room - General | Operating | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 4 | 1 |  | for removal of anaesthetic gases, rectilinear or triangular ducts are also acceptable
OR-GEN | Operating Room - General | Operating | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1
OR-GEN | Operating Room - General | Operating | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 2
OR-GEN | Operating Room - General | Operating | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ELGP-176 | GPO: single, UPS, on services panel | 4 | 1 | Panel 2 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | MGAS-022 | OUTLET: medical air, on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1 | optional
OR-GEN | Operating Room - General | Operating | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 3 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 2 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2
OR-GEN | Operating Room - General | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1
OR-GEN | Operating Room - General | Operating | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | for recharging equipment
OR-GEN | Operating Room - General | Operating | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-213 | BUTTON: nurse call, orderly/porter, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on pendant services head | 1 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITCL-213 | BUTTON: nurse call, orderly/porter, with cancel, on pendant services head | 1 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-071 | OUTLET: tool air, with integral control panel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | optional - depending on medical equipment to be used, may also be wall mounted
OR-GEN | Operating Room - General | Operating | MSP | MGAS-071 | OUTLET: tool air, with integral control panel, on pendant services head | 1 | 1 | Pendant 2 - Arm 1 | optional - depending on medical equipment to be used, may also be wall mounted
OR-GEN | Operating Room - General | Operating | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 12 | 1 | Pendant 1 - Arm 1 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 4 | 1 | Pendant 1 - Arm 1 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 12 | 1 | Pendant 2 - Arm 1 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 4 | 1 | Pendant 2 - Arm 1 | quantity and type of power outlets to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | ELGP-318 | ISOLATOR: three phase, with socket outlet, on pendant services head | 1 | 1 | Pendant 2 - Arm 1 | optional - depending on equipment requirements, may be wall mounted
OR-GEN | Operating Room - General | Operating | MSP | MGAS-001 | OUTLET: carbon dioxide (CO2), on pendant services head | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITIN-014 | OUTLET: data, single RJ45, on pendant services head | 4 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | optional; required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 3 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ELPR-034 | PANEL: UPS status indicator, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-001 | OUTLET: carbon dioxide (CO2), on pendant services head | 1 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 1 | Pendant 2 - Arm 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 1 | Pendant 2 - Arm 1 | optional; required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical service requirements and operational models
OR-GEN | Operating Room - General | Operating | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 3 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | ITIN-014 | OUTLET: data, single RJ45, on pendant services head | 4 | 1 | Pendant 2 - Arm 1
OR-GEN | Operating Room - General | Operating | FFE | JOBE-002 | BENCH: 450D, stainless steel | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | MSP | MMOP-303 | DISPLAY SCREEN: digital operating room (DOR) integration, on pendant arm | 1 | 1 | Pendant 3 - Arm 2
OR-GEN | Operating Room - General | Operating | MSP | MMOP-303 | DISPLAY SCREEN: digital operating room (DOR) integration, on pendant arm | 1 | 1 | Pendant 4 - Arm 2
OR-GEN | Operating Room - General | Operating | MSP | LIFX-149 | LIGHT HEAD: operating, on pendant arm | 1 | 1 | Pendant 3 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | LIFX-149 | LIGHT HEAD: operating, on pendant arm | 1 | 1 | Pendant 4 - Arm 1
OR-GEN | Operating Room - General | Operating | MSP | MMOP-316 | CAMERA: surgical field, digital operating room (DOR) integration, integral to operating light | 1 | 1 | Pendant 3 - Arm 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-311 | CAMERA: patient observation, digital operating room (DOR) integration, ceiling mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-106 | TABLE: operating, mobile, electric | 1 | 1 |  | type of operating table to suit service requirements
OR-GEN | Operating Room - General | Operating | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | to digital operating room (DOR) display screen
OR-GEN | Operating Room - General | Operating | FFE | FIHR-327 | BRACKET: keyboard and mouse, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | optional - to medical services panel if provided
OR-GEN | Operating Room - General | Operating | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-121 | STOOL: mobile, operating | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | workstation on wheels (WOW) may be provided depending on workflows
OR-GEN | Operating Room - General | Operating | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | workstation for digital operating room (DOR) computer
OR-GEN | Operating Room - General | Operating | FFE | MMOP-341 | CONTROL PANEL: digital operating room (DOR) integration, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | SER | MMOP-346 | CONTROL PANEL: operating lights, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMGE-045 | POLE: IV, mobile | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-302 | DISPLAY SCREEN: digital operating room (DOR) integration, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-211 | KICKBUCKET: with stand | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-166 | TROLLEY: anaesthetic | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-162 | MACHINE: anaesthetic, with patient monitor, high acuity | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-171 | MACHINE: electrosurgical, diathermy | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-351 | PATCH PANEL: digital room operating (DOR) integration, wall mounted | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MMOP-352 | PATCH PANEL: digital room operating (DOR) integration, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
OR-GEN | Operating Room - General | Operating | FFE | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMPH-002 | SAFE: dangerous drugs, wall mounted, medium | 1 | 1 |  | optional - drug safe may alternatively be located in the anaesthetic preparation room; with card reader, safe location and type of medication stored is dependent on the operational policies and medication management regulations in different jurisdictions
OR-GEN | Operating Room - General | Operating | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
OR-GEN | Operating Room - General | Operating | FFE | MMOP-201 | STAND: bowl, double | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-202 | STAND: bowl, single | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | optional - to medical services panel if provided
OR-GEN | Operating Room - General | Operating | FFE | MMOP-371 | SYSTEM CABINET: digital integration in operating rooms (DOR) | 1 | 1 |  | located in ICT/AV cupboard (see EXIT)
OR-GEN | Operating Room - General | Operating | FFE | MMTR-171 | TROLLEY: mayo table | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-123 | TROLLEY: gowns/scrubs, 1220W x 610D x 1830H nominal | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-108 | TROLLEY: set-up, table 1250W x 800D x 900H nom | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMTR-003.02 | TROLLEY: stainless steel, 750W x 490D x 900H nom, 2 tier | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FQWS-005 | BIN: sharps, clinical, extra large | 1 | 1 |  | on cart
OR-GEN | Operating Room - General | Operating | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FQWS-396 | TROLLEY: waste bag | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMGE-367 | DEVICE: patient warming, air blanket | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-331 | SPEAKER: digital operating room (DOR) integration, ceiling recessed | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-123 | STOOL: mobile, surgeon | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITNE-224 | INPUT DEVICE: bar code scanner, wireless, with charging dock, medical grade, washable | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 2 | 1
OR-GEN | Operating Room - General | Operating | FFE | MMOP-173 | MACHINE: smoke plume evacuation system | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MMOP-363 | OUTLET: digital operating room (DOR) integration, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | optional - for connection of image capture device to digital operating room (DOR) system
OR-GEN | Operating Room - General | Operating | MSP | MMOP-363 | OUTLET: digital operating room (DOR) integration, on pendant services head | 1 | 1 | Pendant 2 - Arm 1 | optional - for connection of image capture device to digital operating room (DOR) system
OR-GEN | Operating Room - General | Operating | SER | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 |  | to wall mounted display screen
OR-GEN | Operating Room - General | Operating | FIN | CLFS-012 | CEILING: flush set, suspended, acoustic | 1 | 1 | Ceiling Finish 1 | finish to be suitable for sterile environments, refer to local engineering services guidance for acoustic performance (i.e. reverberation time control, sound absorption class, etc.)
OR-GEN | Operating Room - General | Operating | SER | ITBU-436 | CONTROL PANEL: time and elapsed time, synchronised slave clock | 1 | 1
OR-GEN | Operating Room - General | Operating | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1
OR-GEN | Operating Room - General | Operating | MSP | MMSP-121 | PENDANT: double arm, ceiling mounted | 1 | 1 | Pendant 3
OR-GEN | Operating Room - General | Operating | MSP | MMSP-121 | PENDANT: double arm, ceiling mounted | 1 | 1 | Pendant 4
OR-GEN | Operating Room - General | Operating | MSP | MMSP-181 | MEDICAL SERVICES HEAD: horizontal, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | ergonomic control handles required; configuration (horizontal or vertical) to suit services requirements; services allocations are indicative - type and number of services on the pendant to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | MMSP-181 | MEDICAL SERVICES HEAD: horizontal, on pendant arm | 1 | 1 | Pendant 2 - Arm 1 | ergonomic control handles required; configuration (horizontal or vertical) to suit services requirements; services allocations are indicative - type and number of services on the pendant to suit service requirements
OR-GEN | Operating Room - General | Operating | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 3 - Arm 2
OR-GEN | Operating Room - General | Operating | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 4 - Arm 2
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 1 | [DWPR-001] optional
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] to corridor; lockable
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 to general room lighting, 1 to reading light
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 8 | 1 | Floor Skirting | [FLSK-009] aluminum or timber skirting is also acceptable
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 3 |  | [FQBS-018] optional, to desk if provided
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQCA-401 | FRIDGE: domestic, 120L nom, single door, under bench | 1 | 3 |  | [FQCA-030] optional, dependent on project requirements
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQDW-111.01 | WORKSTATION: straight, fixed height, 900H, 600D x 1000W | 1 | 3 |  | [FQDW-053] optional
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to bedside for phone
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049] may be wall mounted
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] to wardrobe; plasterboard bulkhead is also acceptable
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] essential
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 1 | [DWWD-004] blackout fabric
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | DOHI-003 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to ensuite; lockable
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-001] optional; to bedroom side
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-001] optional; to ensuite side
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | [ELGP-109] optional, to fridge if provided
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] 1 to bedside, 1 to desk
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] optional, to desk if provided
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQBS-061 | BED: domestic, single | 1 | 1 |  | [FQBS-004]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQBS-071 | MATTRESS: domestic, single | 1 | 1 |  | [FQBS-004]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | [FIJO-130]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQSN-103 | BEDSIDE TABLE: floor standing, domestic | 1 | 1 |  | [FQTA-001]
OVES | Overnight Stay - Ensuite | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] optional; to bedroom side
OVES | Overnight Stay - Ensuite | Staff Amenities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
OVES | Overnight Stay - Ensuite | Staff Amenities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
OVES | Overnight Stay - Ensuite | Staff Amenities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
OVES | Overnight Stay - Ensuite | Staff Amenities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, inward opening door to have emergency release
OVES | Overnight Stay - Ensuite | Staff Amenities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | [FIDI-030] 1 - to basin, 1 - to shower
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 3 |  | [FIDI-049] optional
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIRT-206 | RAIL: towel, wall mounted | 1 | 1 |  | [FIRT-016]
OVES | Overnight Stay - Ensuite | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
OVES | Overnight Stay - Ensuite | Staff Amenities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | HYSH-001 | SHOWER: fixed rose, wall mounted | 1 | 1 |  | [HYTP-018]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1 |  | [HYTP-039]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | HYWC-021 | TOILET SUITE: standard | 1 | 1 |  | [HYWC-008] with 100mm clearout access point
OVES | Overnight Stay - Ensuite | Staff Amenities | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable
OVES | Overnight Stay - Ensuite | Staff Amenities | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
OVES | Overnight Stay - Ensuite | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] optional; to ensuite side
OVES | Overnight Stay - Ensuite | Staff Amenities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-034] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
OVES | Overnight Stay - Ensuite | Staff Amenities | FFE | HYBA-143 | BASIN: type C, handwashing, with integral double shelf | 1 | 1 |  | [HYBA-002]
OVES | Overnight Stay - Ensuite | Staff Amenities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
OVES | Overnight Stay - Ensuite | Staff Amenities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
OVES | Overnight Stay - Ensuite | Staff Amenities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin, 1 to shower
OVES | Overnight Stay - Ensuite | Staff Amenities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin, 1 to shower
PAR | Parenting Room | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PAR | Parenting Room | Sanitary Facilities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PAR | Parenting Room | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
PAR | Parenting Room | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
PAR | Parenting Room | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
PAR | Parenting Room | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
PAR | Parenting Room | Sanitary Facilities | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | [FLVY-003] minimum slip rating R10/pendulum P3 or agreed equivalent; tiles are also acceptable
PAR | Parenting Room | Sanitary Facilities | FFE | FQGE-361 | CHANGE TABLE: baby, wall mounted | 1 | 1 |  | [FQBS-035]
PAR | Parenting Room | Sanitary Facilities | FFE | FQTA-401 | TABLE: round, 450H, 500 diameter | 1 | 1 |  | [FQTA-049]
PAR | Parenting Room | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
PAR | Parenting Room | Sanitary Facilities | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] for nappies, dedicated sanitary waste stream may be required depending on local waste management policies, size to suit operation policies regarding frequency of waste removal
PAR | Parenting Room | Sanitary Facilities | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
PAR | Parenting Room | Sanitary Facilities | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
PAR | Parenting Room | Sanitary Facilities | FFE | JOBE-041 | BENCH: 650D, laminate | 1 | 1 |  | [FIJO-232] solid surface material is also acceptable
PAR | Parenting Room | Sanitary Facilities | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213]
PAR | Parenting Room | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PAR | Parenting Room | Sanitary Facilities | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 2 | [WLWA-020]
PAR | Parenting Room | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to bench with sink
PAR | Parenting Room | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PAR | Parenting Room | Sanitary Facilities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with privacy latch, emergency release required if inward opening door
PAR | Parenting Room | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PAR | Parenting Room | Sanitary Facilities | FFE | FQBS-261 | ARMCHAIR: visitor, waiting areas | 1 | 1 |  | [FQBS-010] to be suitable for breastfeeding
PAR | Parenting Room | Sanitary Facilities | FFE | HYBA-302 | SINK: single bowl, accessible | 1 | 1 |  | [HYBA-051] depth to meet accessibility requirements when combined with joinery shroud; provision of an integrated solid surface sink in a solid surface bench is also acceptable
PAR | Parenting Room | Sanitary Facilities | FFE | JOGE-037 | SHROUD: under bench, removable, accessible | 1 | 1 |  | [FIJO-228] to bench to conceal plumbing for sink
PAR | Parenting Room | Sanitary Facilities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PAR | Parenting Room | Sanitary Facilities | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
PAR | Parenting Room | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
PAR | Parenting Room | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
PAR | Parenting Room | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink tapware
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to exam light
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional, prioritize lower hook for wheelchair users if only one hook provided
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016] on trolley
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIRT-051.01 | TRACK: curtain, privacy, straight | 1 | 1 |  | [FIRT-031]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 3 |  | [FQBS-028] optional
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 1 | 1 |  | [FQSN-007] extent and type of storage to be based on service requirements and local infection control policies
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044] on trolley; may be wall mounted or mobile
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] a desk may be provided depending on operational model
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 3 |  | [FQGE-056] optional, on WOW
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | MMTR-087 | TROLLEY: phlebotomy, 600W x 490D x 900H nom | 1 | 1 |  | [MMGE-189] with drop down shelf
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-020]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 3 |  | [ELGP-101] optional, to exam light
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to chair
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | MMBE-094 | CHAIR: patient, recliner, clinical, phlebotomy, electric | 1 | 1 |  | [MMBE-094] height adjustable and able to lie flat, electric examination couch may also be provided
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004] dependent on local infection control policies and service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | ELGP-216 | GPO: double, on services panel | 3 | 1 | Panel 1 | [ELGP-206]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] to exam light
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051] quantity to be rationalised across the unit to suit number of staff
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1 |  | [FQSN-051]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional, dependent on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011] hardwired
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 2 | [MGAS-022] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2 | [MGAS-042] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2 | [MGAS-062] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 2 | [MGFP-002] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2 | [MGFP-004] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | MGFP-061 | ADAPTER: suction | 1 | 1 |  | [MMGE-002] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | [MMGE-023] or bed
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | [MMSP-026] 1 panel for medical gases may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 2 | 1 | Wall Finish 1 | [WLWA-004]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection | [WLPR-002]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | D+W | WIFX-162.01 | WINDOW: fixed, external, double glazed, sill at 1650H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is required
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2 | [MMGE-002] may be shared between two bays depending on service requirements
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] + indicator button & light
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] + indicator button & light
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | ITCL-252 | HANDSET: nurse call, patient to staff call, with light control | 1 | 1 | Panel 1 | [ITCL-028] call button on the handset, reading light control
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low level, for bed/recliner
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to patient entertainment screen
PBTR-MD | Patient Bay - Medical Day Treatment | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | ELGP-246 | GPO: double, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-222]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to exam light if provided
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / pendulum P3 or agreed equivalent; a higher slip rating may be required depending on local WHS policies
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] in case of spills, to be consolidated between multiple bays
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | HYDR-181 | ACCESS PANEL: waterless trap | 1 | 1 |  | [HYDR-019]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | HYGE-081 | WALL BOX: renal dialysis, integral tundish, with 1 water supply connection and 1 drain connection | 1 | 1 |  | [MMGE-096]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | HYDR-104 | TUNDISH: in wall, with viewing panel | 1 | 1 |  | [MMGE-096]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | [MMGE-096]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | HYTP-458 | DIRECT CONNECTION: water, reverse osmosis (RO) | 1 | 1 |  | [MMGE-096]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment system, may be replaced with data outlet depending on ICT policy
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | [MMGE-023]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | MMGE-381 | MACHINE: dialysis | 1 | 1 |  | [MMGE-049]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 2 | 3 | Wall Finish 2 | [WLWA-020] optional, to side walls if provided
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 3 | Wall Protection | [WLPR-006] optional, to side walls if provided
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | D+W | WIFX-161.01 | WINDOW: fixed, external, double glazed, sill at 1500H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook essential
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] + indicator button & light
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] + indicator button & light
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Panel 1 | [ITCL-028]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to patient entertainment system
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] low level, to recliner
PBTR-RD-A | Patient Bay - Renal Dialysis, Chair | Renal Dialysis | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Panel 1 | [ITCL-028]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ELGP-246 | GPO: double, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-222]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 2 | 3 | Wall Finish 2 | [WLWA-020] optional, to side walls if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 3 | Wall Protection | [WLPR-006] optional, to side walls if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / pendulum P3 or agreed equivalent; a higher slip rating may be required depending on local WHS policies
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | D+W | WIFX-161.01 | WINDOW: fixed, external, double glazed, sill at 1500H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook essential
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to exam light if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to patient entertainment system
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] low level, to recliner
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] in case of spills, to be consolidated between multiple bays
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-181 | ACCESS PANEL: waterless trap | 1 | 1 |  | [HYDR-019]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment system, may be replaced with data outlet depending on ICT policy
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYGE-081 | WALL BOX: renal dialysis, integral tundish, with 1 water supply connection and 1 drain connection | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-104 | TUNDISH: in wall, with viewing panel | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYTP-458 | DIRECT CONNECTION: water, reverse osmosis (RO) | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | MMGE-381 | MACHINE: dialysis | 1 | 1 |  | [MMGE-049]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1 |  | [MMBE-009]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 2 | [DWPR-005] to room side
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 2 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-005] automated
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | [DWSC-034] automated
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | [ELGP-122] on service panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-226 | GPO: double, in floor box | 4 | 1 |  | [ELGP-203]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | [ELPR-007] on service panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012] number determined by number of doors
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014] near door
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | [FIHR-030]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-091 | HOOK: anchor point, for attaching patient self-assist positioning aid, wall mounted | 1 | 1 |  | [FIHR-092]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel + indicator button & light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] on services panel + indicator button & light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 2 | 1 |  | [ITCL-012 + FIHR-077]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 2 | 1 |  | [ITIN-011]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026] on wall near PET-CT unit
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 2 | 1 |  | [ITIN-143]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] handsfree to control room
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | [ITSE-025]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-136]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | [LIFX-002] to outside of all doors to room, auto on when modality is in use, vendor to provide signal wiring to light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 1 |  | [MEGE-007] alarm for temperature range
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional, on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional, on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MGFP-061 | ADAPTER: suction | 2 | 1 |  | [MMGE-002] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 3 |  | [MMMI-377] optional
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-053 | INJECTOR: contrast, ceiling mounted | 1 | 1 |  | [MMMI-107] also may be mobile or wall mounted
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-071 | INJECTOR: radioisotope, automatic, mobile | 1 | 1 |  | [MMMI-218]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIPT-001 | IMAGING DEVICE: PET-CT | 1 | 1 |  | [MMMI-207]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIPT-006 | TABLE: patient, PET-CT | 1 | 1 |  | [MMMI-217]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIPT-041 | PHANTOM: PET-CT | 1 | 1 |  | [MMMI-209] stored within shielded custom joinery
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | [MMBE-042]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1 |  | [MMGE-045] may be ceiling mounted
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-251 | DEVICE: sphygmomanometer, portable | 1 | 1 |  | [MMGE-091]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026] patient services
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-025]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 6 | 1 | Wall Finish 3 | [WLWA-020]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [MMGE-142]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | [ITCL-012 + FIHR-078]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-218] reinforced shelving
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] 1 to clock
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-106 | GPO: single, ceiling mounted | 3 | 1 |  | [ELGP-101] 1 to laser positioning light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123.1]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] to walls
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PHA-CO | Pharmacy - Counter | Pharmacy | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PHA-CO | Pharmacy - Counter | Pharmacy | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PHA-CO | Pharmacy - Counter | Pharmacy | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
PHA-CO | Pharmacy - Counter | Pharmacy | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006] vinyl is also acceptable
PHA-CO | Pharmacy - Counter | Pharmacy | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 12 | 1 | Floor Skirting | [FLSK-009] seamless coved vinyl skirting if vinyl flooring provided
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] quantity and type of bins to be based on local waste management policies
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | FQWS-212 | BIN: confidential document, secure, 30L | 1 | 1 |  | [FQCW-064] quantity and type of bins to be based on local waste management policies
PHA-CO | Pharmacy - Counter | Pharmacy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-049]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
PHA-CO | Pharmacy - Counter | Pharmacy | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] shared, below desk
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1 |  | [FIJO-051]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-058]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | [FIJO-099]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-135]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JODW-021 | DRAWER UNIT: under bench, 2 drawers, equal | 1 | 1 |  | [FIJO-114]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | [FIJO-229]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 2 | 1 |  | [WLPT-015]
PHA-CO | Pharmacy - Counter | Pharmacy | FFE | JOSP-081 | JOINERY UNIT: bespoke, pharmacy, under bench, pass through drawer | 1 | 1 |  | [FQSN-028] lockable, under bench, for transfer of large items
PHA-CO | Pharmacy - Counter | Pharmacy | FIN | WLFI-001 | WALL FINISH: paint | 7 | 1 | Wall Finish 1 | [WLWA-004]
PHA-CO | Pharmacy - Counter | Pharmacy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] extent of emergency power to be determined based on service requirements
PHA-CO | Pharmacy - Counter | Pharmacy | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | FQDW-134.05 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1800W | 1 | 1 |  | [FQDW-002]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] may be on wall or desk mounted bracket, an additional screen may be provided depending on project ICT requirements
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 1 |  | [ITNE-003]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | ITNE-231 | INPUT DEVICE: portable data entry, with charging dock | 1 | 1 |  | [ITNE-072] may be shared between multiple workstations
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-069]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 1 | 1 |  | [FIJO-108]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PHA-DB | Pharmacy - Distribution Workstation | Pharmacy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] extent of emergency power to be determined based on service requirements
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] quantity and type of bins to be based on local waste management policies
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | FQWS-212 | BIN: confidential document, secure, 30L | 1 | 1 |  | [FQCW-064] quantity and type of bins to be based on local waste management policies
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] may be on desk mounted bracket
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-171 | DISPLAY SCREEN: computer | 1 | 3 |  | [ITNE-063] optional, depending on project ICT requirements; may be on desk mounted bracket
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 1 |  | [ITNE-003]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-093]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | MMPH-081 | WORKSTATION SYSTEM: pharmacy, shelving, with integral power and data, softwired | 1 | 1 |  | [FQDW-048 + FQDW-047] services spine may be shared between multiple workstations
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | MMPH-174.01 | WORKSTATION: pharmacy, straight, adjustable height, 900H nom, 750D x 1800W | 1 | 1 |  | [FQDW-046]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] extent of emergency power to be determined based on service requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 2 x task lights
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-273 | BIN: pharmaceutical waste, 50L | 1 | 1 |  | [FQCW-065] quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYBA-303 | SINK: single bowl, with drainer | 1 | 1 |  | [HYBA-069]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-020] may be height adjustable item depending on service requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-059]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-103 | CUPBOARD: wall mounted, single door, glazed | 1 | 1 |  | [FIJO-159]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-123 | CUPBOARD: wall mounted, double door, glazed | 3 | 1 |  | [FIJO-148]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-136]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] under wall mounted joinery
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | MMGE-201 | SCALES: digital, benchtop | 2 | 1 |  | [MMGE-185]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | MMLA-172 | CABINET: fume hood, mobile | 1 | 1 |  | [MEEX-013]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 3 |  | [FQSM-016] optional
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 6 | 1 | Wall Finish 2 | [WLWA-020]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | WLFI-101 | SPLASHBACK: vinyl | 4 | 1 | Wall Finish 3 | [WLWA-010]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-003]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | [ELGP-208] provision of emergency power to be determined based on service requirements
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FFE | FQDW-134.05 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1800W | 1 | 1 |  | [FQDW-002]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FFE | FQSM-211 | SHELVING UNIT: mobile, adjustable shelves, 600D x 400W x 2100H nominal | 2 | 1 |  | [FQSM-045]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] may be on wall or desk mounted bracket, an additional screen may be provided depending on project ICT requirements
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 1 |  | [ITNE-003]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PHA-RE | Pharmacy - Returns Workstation | Pharmacy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] extent of emergency power to be determined based on service requirements
PLAY | Play Area - Paediatric | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PLAY | Play Area - Paediatric | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PLAY | Play Area - Paediatric | Public Areas | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001] quantity and location to suit local IPC policies
PLAY | Play Area - Paediatric | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010]
PLAY | Play Area - Paediatric | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PLAY | Play Area - Paediatric | Public Areas | FFE | FQBS-116 | CHAIR: visitor, waiting areas | 2 | 1 |  | [FQBS-032]
PLAY | Play Area - Paediatric | Public Areas | FFE | FQBS-161 | CHAIR: play areas, child | 2 | 1 |  | [FQBS-012]
PLAY | Play Area - Paediatric | Public Areas | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1 |  | [FQGE-002]
PLAY | Play Area - Paediatric | Public Areas | FFE | FQTA-096 | TABLE: play areas, child | 1 | 1 |  | [FQTA-003]
PLAY | Play Area - Paediatric | Public Areas | FFE | FQTA-202 | TABLE: square, 450H, 600L | 1 | 1 |  | [FQTA-075]
PLAY | Play Area - Paediatric | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
PLAY | Play Area - Paediatric | Public Areas | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
PLAY | Play Area - Paediatric | Public Areas | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook is desirable
PLAY | Play Area - Paediatric | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | DOHI-106 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-027] lockable
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | DOHI-106 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-027] optional secondary access door, lockable
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELGP-131.01 | GPO: single, emergency power, wall mounted, horizontal | 1 | 3 |  | [ELGP-123] optional, dependent on equipment
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELGP-231.01 | GPO: double, emergency power, wall mounted, horizontal | 8 | 1 |  | [ELGP-223] for water treatment equipment, high level (power tools to be on a separate circuit)
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-010] optional
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | FLGE-003 | FLOOR FINISH: concrete, trowel finished, sealed | 1 | 1 | Floor Finish 2 | [FLGE-003]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | FLSK-081 | SKIRTING: concrete, sealed, coved | 6 | 1 | Floor Skirting | [FLSK-002]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 3 |  | [FQBS-051] optional
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FFE | FQDW-131.03 | WORKSTATION: straight, adjustable height, 720H nom, 600D x 1500W | 1 | 3 |  | [FQDW-051] optional
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FFE | FQGE-442 | PALLET: half size | 1 | 1 |  | [FQSN-138]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-037 | DRAIN: floor waste, sump, square | 1 | 1 |  | [HYDR-017] floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-101 | TUNDISH: fixture mounted | 2 | 1 |  | [HYDR-006]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-102 | TUNDISH: floor mounted | 1 | 1 |  | [HYDR-018] tundish must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-211 | PLANT: water treatment, softener tank | 1 | 1 |  | [HYGE-024] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-212 | PLANT: water treatment, brine tank | 1 | 1 |  | [HYGE-019] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-213 | PLANT: water treatment, multimedia tank | 1 | 1 |  | [HYGE-021] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-221 | PLANT: water treatment, carbon filter | 3 | 3 |  | [HYGE-020] 1 is optional; size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-222 | PLANT: water treatment, ultraviolet filter | 1 | 1 |  | [HYGE-027]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-231 | PLANT: water treatment, particle filter, 1 micron | 1 | 1 |  | [HYGE-022] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-232 | PLANT: water treatment, particle filter, 5 micron | 1 | 1 |  | [HYGE-023] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-251 | PLANT: dialysis, water treatment, reverse osmosis | 1 | 1 |  | [HYGE-012] details according to manufacturer's specifications
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-301 | PUMP: pressure booster | 2 | 1 |  | [HYGE-016] to suit water pressure drop through pre-filtration train where building water pressure and flow is inadequate
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ITBU-376 | ALARM: chlorine detector | 1 | 3 |  | [ITBU-024] optional, dependent on local operational policies
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ITBU-402 | ALARM: equipment monitoring, water treatment malfunction | 1 | 1 |  | [ITBU-002] connected to BMS and staff station in unit
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | MEGE-201 | PLANT: heat exchanger, supplied by mechanical chilled water | 1 | 1 |  | [MEGE-010] as required; may be necessary to cool feed water where high temperatures are expected, refer to technical expert for required outlet temperature (generally <25°C)
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-051.03 | DOOR FRAME PROTECTION: corners, to 1200H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PLST | Plaster Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PLST | Plaster Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PLST | Plaster Room | Ambulatory Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PLST | Plaster Room | Ambulatory Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PLST | Plaster Room | Ambulatory Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PLST | Plaster Room | Ambulatory Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033]
PLST | Plaster Room | Ambulatory Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
PLST | Plaster Room | Ambulatory Care | MSP | ELGP-116 | GPO: single, on services panel | 3 | 1 | Panel 1 | [ELGP-105]
PLST | Plaster Room | Ambulatory Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-122]
PLST | Plaster Room | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
PLST | Plaster Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light, 1 x examination light
PLST | Plaster Room | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PLST | Plaster Room | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
PLST | Plaster Room | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PLST | Plaster Room | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
PLST | Plaster Room | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
PLST | Plaster Room | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019] quantity to suit number of suction outlets
PLST | Plaster Room | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PLST | Plaster Room | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PLST | Plaster Room | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PLST | Plaster Room | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PLST | Plaster Room | Ambulatory Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 3 |  | [FQCW-008] optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
PLST | Plaster Room | Ambulatory Care | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
PLST | Plaster Room | Ambulatory Care | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-053] hot water
PLST | Plaster Room | Ambulatory Care | SER | HYDR-151 | TRAP: plaster | 1 | 1 |  | [HYDR-008] to be easily accessible for cleaning and maintenance
PLST | Plaster Room | Ambulatory Care | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 1 | 1 |  | [HYTP-038] to sink
PLST | Plaster Room | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
PLST | Plaster Room | Ambulatory Care | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
PLST | Plaster Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
PLST | Plaster Room | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] call button on the handset
PLST | Plaster Room | Ambulatory Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
PLST | Plaster Room | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PLST | Plaster Room | Ambulatory Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
PLST | Plaster Room | Ambulatory Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
PLST | Plaster Room | Ambulatory Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PLST | Plaster Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
PLST | Plaster Room | Ambulatory Care | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-060] with sink and wet edge
PLST | Plaster Room | Ambulatory Care | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 3 | 1 |  | [FIJO-145]
PLST | Plaster Room | Ambulatory Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-136]
PLST | Plaster Room | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
PLST | Plaster Room | Ambulatory Care | SER | LIFX-108 | LIGHT: task, integral to joinery | 3 | 1 |  | [LIFX-008]
PLST | Plaster Room | Ambulatory Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
PLST | Plaster Room | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
PLST | Plaster Room | Ambulatory Care | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional
PLST | Plaster Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 3 | Panel 1 | [MGAS-042] 1 is optional, quantity dependent on service requirements
PLST | Plaster Room | Ambulatory Care | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | [MGAS-053]
PLST | Plaster Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 3 | Panel 1 | [MGAS-062] 1 is optional, quantity dependent on service requirements
PLST | Plaster Room | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
PLST | Plaster Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004] quantity to suit number of oxygen outlets
PLST | Plaster Room | Ambulatory Care | MSP | MGFP-082 | BLENDER: oxygen (O2) and nitrous oxide (N20) | 1 | 3 | Panel 1 | [MMMA-011] optional, may be mobile, on trolley or wall mounted
PLST | Plaster Room | Ambulatory Care | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | [MMBE-043] or plinth/examination couch
PLST | Plaster Room | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100] quantity to suit number of suction outlets
PLST | Plaster Room | Ambulatory Care | FFE | MMGE-233 | DIAGNOSTIC SET: otoscope and ophthalmoscope, wall mounted | 1 | 3 |  | [MMGE-031] optional, may be portable/mobile on stand
PLST | Plaster Room | Ambulatory Care | FFE | MMGE-326 | DEVICE: saw, plaster, with integral dust extraction | 1 | 1 |  | [MMAH-023 + MMAH-045] integral/localised dust extraction required or independent dust extraction system to be provided
PLST | Plaster Room | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PLST | Plaster Room | Ambulatory Care | FFE | MMTR-141 | TROLLEY: plaster | 1 | 1 |  | [MMAH-028]
PLST | Plaster Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PLST | Plaster Room | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020]
PLST | Plaster Room | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
PLST | Plaster Room | Ambulatory Care | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 3 | Panel 1 | [MMGE-001] optional
PLST | Plaster Room | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 2 | Panel 1 | [MMGE-002] quantity to suit number of suction outlets
PLST | Plaster Room | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-039]
PLST | Plaster Room | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to sink, 1 to basin
PLST | Plaster Room | Ambulatory Care | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
PLST | Plaster Room | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to basin tapware
PLST | Plaster Room | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PLST | Plaster Room | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low level, for patient trolley
PLST | Plaster Room | Ambulatory Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to exam light
PLST | Plaster Room | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | [ELGP-208]
PLST | Plaster Room | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry door
PLST | Plaster Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PLST | Plaster Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
PLST | Plaster Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
PLST | Plaster Room | Ambulatory Care | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] + indicator button & light
PLST | Plaster Room | Ambulatory Care | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] + indicator button & light
PLST | Plaster Room | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 3 | Panel 1 | [MMGE-002] optional; quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PROC | Procedure Room | Ambulatory Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PROC | Procedure Room | Ambulatory Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PROC | Procedure Room | Ambulatory Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
PROC | Procedure Room | Ambulatory Care | MSP | ELGP-116 | GPO: single, on services panel | 3 | 1 | Panel 1 | [ELGP-105]
PROC | Procedure Room | Ambulatory Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-122]
PROC | Procedure Room | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
PROC | Procedure Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light, 1 x examination light
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019] quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 3 |  | [FIHR-011] optional, for cardiac/vital signs monitor
PROC | Procedure Room | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
PROC | Procedure Room | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PROC | Procedure Room | Ambulatory Care | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1 |  | [FQBS-052]
PROC | Procedure Room | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PROC | Procedure Room | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
PROC | Procedure Room | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 3 |  | [FQCW-008] optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
PROC | Procedure Room | Ambulatory Care | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
PROC | Procedure Room | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
PROC | Procedure Room | Ambulatory Care | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
PROC | Procedure Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
PROC | Procedure Room | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] call button on the handset
PROC | Procedure Room | Ambulatory Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 3 |  | [ITIN-016] 1 to telephone, 1 - optional, for cardiac/vital signs monitor
PROC | Procedure Room | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PROC | Procedure Room | Ambulatory Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
PROC | Procedure Room | Ambulatory Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
PROC | Procedure Room | Ambulatory Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PROC | Procedure Room | Ambulatory Care | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
PROC | Procedure Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
PROC | Procedure Room | Ambulatory Care | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
PROC | Procedure Room | Ambulatory Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
PROC | Procedure Room | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
PROC | Procedure Room | Ambulatory Care | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
PROC | Procedure Room | Ambulatory Care | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008]
PROC | Procedure Room | Ambulatory Care | FFE | LIFX-121 | LIGHT: procedure, minor, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-013]
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional, dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042] quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional, dependent on service requirements, provide if nitrous oxide required
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062] quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004] quantity to suit number of oxygen outlets
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-082 | BLENDER: oxygen (O2) and nitrous oxide (N20) | 1 | 3 | Panel 1 | [MMMA-011] optional, may be mobile, on trolley or wall mounted
PROC | Procedure Room | Ambulatory Care | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | [MMBE-043]
PROC | Procedure Room | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100] quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | FFE | MMGE-233 | DIAGNOSTIC SET: otoscope and ophthalmoscope, wall mounted | 1 | 3 |  | [MMGE-031] optional, may be portable/mobile on stand
PROC | Procedure Room | Ambulatory Care | FFE | MMPM-021 | MONITOR: patient, high acuity | 1 | 3 |  | [MMHA-008] optional
PROC | Procedure Room | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PROC | Procedure Room | Ambulatory Care | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
PROC | Procedure Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PROC | Procedure Room | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 2 | [WLWA-020]
PROC | Procedure Room | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
PROC | Procedure Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PROC | Procedure Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PROC | Procedure Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PROC | Procedure Room | Ambulatory Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | DWGL-033]
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 3 | Panel 1 | [MMGE-002] 1 is optional, quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] + indicator button & light
PROC | Procedure Room | Ambulatory Care | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] + indicator button & light
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002] quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 3 | Panel 1 | [MGAS-062] 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 3 | Panel 1 | [MGAS-042] 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 3 | Panel 1 | [MGFP-004] 1 is optional, quantity to suit number of oxygen outlets
PROC | Procedure Room | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PROC | Procedure Room | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
PROC | Procedure Room | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PROC | Procedure Room | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
PROC | Procedure Room | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
PROC | Procedure Room | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low level, for patient trolley
PROC | Procedure Room | Ambulatory Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to procedure light
PROC | Procedure Room | Ambulatory Care | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | [ELGP-123] optional, for cardiac/vital signs monitor
PROC | Procedure Room | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with accessory storage and cable management items as required
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 3 |  | optional; to wall mounted computer if provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 3 |  | optional; to wall mounted computer if provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | shared between multiple patient bays, with quantity to be rationalised across the unit to suit clinical services requirements, operational models for EMR, local ICT policies and staffing models
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 3 |  | optional; may be provided in lieu of WOW; provision dependent on clinical services requirements, operational model for electronic medical records and local ICT policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to write up area, for workstation on wheels or wall mounted computer depending on solution provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use to charge portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to bedhead wall, low height for patient bed and mattress
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 3 | 1 | Wall Finish 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of bed; location to ensure visibility along paths of travel
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | provide if patient bay is configured with side walls
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 3 | 1 | Wall Finish 3 | provide if patient bay is configured with side walls; to be coordinated with adjacent wall protection
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 3 |  | optional; may be provided in PPE bay shared between multiple bays
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to write up area, for workstation on wheels or wall mounted computer depending on solution provided
PTB-E-ACU | Patient Bay - Emergency, Acute Treatment | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to write up area, for workstation on wheels or wall mounted computer depending on solution provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use to charge portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to bedhead wall, low height for patient bed and mattress
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | WIFX-057.04 | WINDOW: fixed, internal, double glazed, sill at 900H, with integral blind | 1 | 1 | Internal - Window 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation; provision of integral blinds or extension of the privacy curtain track over the window is to be determined to suit requirements for observation and patient privacy
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | DOHI-144.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 3 |  | optional; if room is designed for negative pressure isolation supply and exhaust air locations are to be confirmed in alignment with local engineering services guidance
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | Internal - Door 2 | optional, to ensuite if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 3 | Internal - Door 3 | optional, to anteroom if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to room side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | to ensuite side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 3 | to room side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 3 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; location to ensure visibility along paths of travel
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 7 | 1 | Wall Finish 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 3 | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 3 | to anteroom side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | to entry door, may extend over observation window
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with accessory storage and cable management items as required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 3 |  | optional; to wall mounted computer if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 3 |  | optional; may be provided in lieu of WOW; provision dependent on clinical services requirements, operational model for electronic medical records and local ICT policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door, may extend over observation window
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 3 |  | optional; to wall mounted computer if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | shared between multiple patient bays, with quantity to be rationalised across the unit to suit clinical services requirements, operational models for EMR, local ICT policies and staffing models
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | collocated with alcohol-based hand rub
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | with removable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to write up area, for workstation on wheels or wall mounted computer depending on solution provided
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | shared between multiple ambulance triage bays
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | shared between multiple ambulance triage bays; size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | shared between multiple ambulance triage bays; size to suit clinical services requirements, operational models for frequency of disposal and local IPC policies
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | optional, provision dependent on clinical services requirements and models of care
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 3 | Panel 1 | optional, to medical air outlet if provided
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of stretcher; location to ensure visibility along paths of travel
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for patient recliner
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use to charge portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided as wall mounted or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | selected item to be able to lay flat
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of recliner; location to ensure visibility along paths of travel
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | sharps bin may alternatively be wall mounted or on a clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 2 | 1 | Wall Protection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use to charge portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to bedhead wall, low height for patient bed and mattress
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1 |  | configuration of patient entertainment system will be dependent on operational models and local ICT strategies and policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | optional; required if patient monitor is provided; with cable and accessory management items as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration of patient entertainment system will be dependent on operational models and local ICT strategies and policies
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements; may alternatively be provided on a mobile stand to be shared across the unit and brought to the patient bay as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | optional; provision and configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | with control to patient handset
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of bed; location to ensure visibility along paths of travel
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | optional; may be provided in PPE bay shared between multiple bays
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 3 | 1 | Wall Finish 1
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | provide if patient bay is configured with side walls
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-NAC | Patient Bay - Emergency, Non-Acute Treatment | Emergency | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 2 | 1 | Wall Finish 3 | provide if patient bay is configured with side walls; to be coordinated with adjacent wall protection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 5 | 1 | Wall Finish 2
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLPR-046.03 | WALL PROTECTION: crash rail, to 900 AFFL | 2 | 1 | Wall Protection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 4 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELPR-034 | PANEL: UPS status indicator, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | wall mounted item is also acceptable
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | wall mounted item is also acceptable
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-135 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 | Pendant 1 - Arm 1 | with holder and cable management items as required
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-034 | OUTLET: data, triple RJ45, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | optional, provision of reticulated nitrous oxide to be confirmed to suit clinical services requirements and operational models
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | optional, required if reticulated nitrous oxide provided; provision of reticulated nitrous oxide to be confirmed to suit clinical services requirements and operational models
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 3 | Pendant 1 - Arm 1 | optional, to scavenge outlet if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-235 | DIAGNOSTIC SET: otoscope and ophthalmoscope, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMHA-051 | DEVICE: ventilator, adult | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 | Pendant 1 - Arm 1 | configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required; connection required for output to ceiling mounted slave monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-414 | BRACKET: patient monitor, articulated, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-296 | DEVICE: pump, syringe | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMGE-191 | CANNISTER: suction bottle | 3 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-403 | BRACKET: patient monitor, fixed, ceiling mounted | 1 | 1 |  | to slave display screen for patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1 |  | on ceiling mounted bracket, display feed from patient monitor on services pendant head
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 2 | 3 |  | optional, for education and/or to enable remote assistance in small services; provision, quantity and placement is dependent on clinical services requirements and local ICT strategies and policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | WLPR-006.06 | WALL PROTECTION: corner guards, to 2100 AFFL | 2 | 1 | Wall Protection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | LIFX-131 | LIGHT: procedure, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | to be coordinated with ceiling mounted IV track and medical services pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMGE-039 | HANGER: IV, for ceiling track | 1 | 3 |  | optional, to ceiling track if provided, may alternatively be provided as services pendant head mounted or mobile poles
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPH-021 | FRIDGE: medication/vaccine, 150L nom, single door, under bench | 1 | 3 |  | optional, may be provided in a shared area between resuscitation bays; provision in bay will be dependent on operational models for medication management
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 3 |  | optional, may be provided in a shared area between resuscitation bays; provision in bay will be dependent on operational models for medication management
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | to write-up workstation; provision of articulated wall or bench mounted brackets may be considered for ergonomics and to support flexible positioning of workstation for visibility of patient.
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-211 | BENCH SUPPORT: bracket | 3 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 2 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 8 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 3 |  | optional, to display screen for decision support tool if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | to electrical services on pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | for general room lights; to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to display screen for patient information and diagnostic imaging if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional, to medication fridge if provided; for temperature monitoring BMS connection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-053 | TROLLEY: airway/intubation, 750W x 490D x 900H nom | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-032 | TROLLEY: resuscitation, paediatric | 1 | 3 |  | optional, may alternatively be provided in a shared area between resuscitation bays or in a dedicated resuscitation bay
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-092 | TROLLEY: procedure, 600W x 490D x 900H nom | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1 |  | as required to suit portable equipment positioning
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | to resuscitation trolley
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-115 | BRACKET: sharps bin, trolley mounted | 1 | 1 |  | to resuscitation trolley
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | to resuscitation trolley; size to suit clinical services requirements and operational models for frequency of disposal
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 3 |  | optional, for decision support tool display; provision and placement dependent on clinical services requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | provided in addition to PPE bays shared between resuscitation bays
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | provided in addition to PPE bays shared between resuscitation bays
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | with removable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITBU-436 | CONTROL PANEL: time and elapsed time, synchronised slave clock | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | optional, to display screen for patient information and diagnostic imaging if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 3 |  | optional, for patient information and diagnostic imaging display; provision and placement dependent on clinical service requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | FIRT-091 | TRACK: IV, ceiling mounted | 1 | 3 |  | optional, may alternatively be provided as services pendant head mounted or mobile poles; to be coordinated with procedure light and medical services pendant
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to display screen for decision support tool if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to slave display screen for patient monitor; services to be confirmed to suit selected equipment, may be replaced with alternate AV outlet depending on system requirements
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to slave display screen for patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 4 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to display screen for patient information and diagnostic imaging if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to display screen for decision support tool if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to write-up workstation
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 6 | 1 |  | 2 over bench, 4 distributed across the room for medical equipment
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to medication fridge if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-014 | OUTLET: data, single RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | FIHR-423 | BRACKET: ventilator, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 |  | optional, to drug safe if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional, to card reader for drug safe if provided
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | FFE | MMTR-016.02 | TROLLEY: stainless steel, wire mesh drawers, 490W x 600D x 900H nom, 4 drawers | 4 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to diagnostic set
PTB-E-RES | Patient Bay - Emergency, Resuscitation | Emergency | MSP | ITIN-064 | OUTLET: data, HDMI, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | to patient monitor; services to be confirmed to suit selected equipment, may be replaced with alternate AV outlet depending on system requirements
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | D+W | WIOP-256.02 | WINDOW: operable, jockey sash, external, double glazed, sill at 750H, with integral blind | 1 | 1 | External - Window 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | to adjacent room to support patient observation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 2 | to adjacent room to support patient observation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FIN | WLPR-006.02 | WALL PROTECTION: corner guards, to 1050 AFFL | 1 | 1 | Wall Protection | coordinated with adjacent wall protection
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to patient lifter track
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 3 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 2 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | to UPS outlets on medical services pendant
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | to night lights; to be coordinated with switch on medical services pendant
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights; to be coordinated with switch on medical services pendant
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | to patient entertainment system; may be replaced with a data outlet or alternate AV outlet depending on system requirements and local ICT policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | LIFX-151 | LIGHT: night, wall mounted | 2 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to patient entertainment system
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYGE-082 | WALL BOX: renal dialysis, integral tundish, with 1 water supply connection and 2 drain connections | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-104 | TUNDISH: in wall, with viewing panel | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | optional; provision will be dependent on clinical service requirements regarding the delivery of dialysis; project team to confirm all quick connect fitting and adapter requirements to ensure secure connections with dialysis equipment; water supply via backflow prevention
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | HYDR-157 | TRAP: cooling pit, with sealed lid | 1 | 1 |  | optional, required if dialysis wall box is provided; to support cooling of wastewater from heat disinfection of dialysis machines and portable RO machines
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 2 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to carer's area
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQBS-282 | RECLINER: visitor, clinical areas, fold out bed | 1 | 1 |  | selected item to suit clinical services requirements, operational models and local IPC policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-116 | BED: patient, electric, with mattress, intensive care | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMGE-019 | CHAIR: patient | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMHA-051 | DEVICE: ventilator, adult | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 6 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | ability for screen to duplicate patient monitoring information for added visibility in emergency situations to be considered
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | alternative arrangement on ceiling mounted articulated arm may be considered at project level to suit clinical requirements and operational models for write-up and observation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | ITBU-471 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | ability to turn off/dim display to be considered to respond to patient preferences/needs
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMGE-386 | PROCESSOR: water treatment, dialysis, reverse osmosis (RO), mobile | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIHR-353 | BRACKET: patient entertainment system, fixed, ceiling mounted | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMGE-381 | MACHINE: dialysis | 1 | 1 |  | optional; provision will be dependent on clinical service requirements and operational models regarding the delivery of dialysis
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 2 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | a privacy curtain is provided to the glazed door and panel and staff workstation at the front of the room; the use of integral blinds or switchable glass may be considered at project level based on assessment of maintenance, product lifecycle and downtime requirements
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | may be shared between multiple rooms and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMTR-002.02 | TROLLEY: stainless steel, 600W x 490D x 900H nom, 2 tier | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | FFE | MMTR-092 | TROLLEY: procedure, 600W x 490D x 900H nom | 1 | 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | FIHR-414 | BRACKET: patient monitor, articulated, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-195 | BUTTON: nurse call, emergency, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELSW-021 | SWITCH: light, dimmer | 1 | 1 | Pendant 1 - Arm 2 | to general room lights; to be coordinated with switch on wall
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-047 | POLE: IV, on pendant services head | 1 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMSP-121 | PENDANT: double arm, ceiling mounted | 1 | 1 | Pendant 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITCL-135 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on pendant services head | 1 | 1 | Pendant 1 - Arm 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 2
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Pendant 1 - Arm 2 | to night lights; to be coordinated with switch on wall
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | shown to patient's right (services head R); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-ICU | Patient Bay - Intensive Care | Intensive Care | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 2 | shown to patient's left (services head L); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | for storage of family member property, may be lockable
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | WLPR-006.03 | WALL PROTECTION: corner guards, to 1200 AFFL | 1 | 1 | Wall Protection
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMSP-121 | PENDANT: double arm, ceiling mounted | 1 | 1 | Pendant 1 | coordinate provision of access panel on ceiling adjacent to pendant for maintenance
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 6 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELPR-034 | PANEL: UPS status indicator, on pendant services head | 1 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ITCL-125 | BUTTON: nurse call, patient to staff call, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ITIN-014 | OUTLET: data, single RJ45, on pendant services head | 3 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 6 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELPR-034 | PANEL: UPS status indicator, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | FIHR-104 | BRACKET: suction bottle, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | FIHR-215 | BRACKET: computer display screen, single articulated, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | FIHR-428 | BRACKET: ventilator, continuous positive airway pressure (CPAP), on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ITCL-125 | BUTTON: nurse call, patient to staff call, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ITCL-185 | BUTTON: nurse call, staff assist, with cancel, on pendant services head | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | ITIN-014 | OUTLET: data, single RJ45, on pendant services head | 3 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MGFP-081 | BLENDER: oxygen (O2) and medical air (MA) | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMGE-191 | CANNISTER: suction bottle | 2 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMHA-064 | DEVICE: ventilator, neonatal, CPAP | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMHA-061 | DEVICE: ventilator, neonatal | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMPM-026 | MONITOR: patient, high acuity, neonatal | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to procedure light
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ELSW-001 | SWITCH: light | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | 1 to wall mounted telephone, 1 to milk fridge
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to write-up area
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | to family area
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FIHR-115 | BRACKET: sharps bin, trolley mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FIRT-051.03 | TRACK: curtain, privacy, U-shaped | 1 | 3 |  | optional, portable screens in lieu of ceiling mounted privacy curtains
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FQCA-211 | APPLIANCE: bottle warmer, benchtop, domestic | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | ITCL-464 | CAMERA: patient observation, neonatal, crib mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | LIFX-121 | LIGHT: procedure, minor, single articulated arm, 1 light head, ceiling mounted | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | MMGE-045 | POLE: IV, mobile | 2 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | MMGE-311 | DEVICE: pump, breast milk | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | MMGE-371 | DEVICE: patient, warming/cooling | 1 | 3 |  | optional
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | MMMA-016 | INCUBATOR: infant, closed cot, humidicrib | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | MMMA-131 | FRIDGE: milk, 15L nominal, single door, benchtop | 1 | 1 |  | provision to suit local jurisdictional policies for breast milk storage to be centralised or decentralised; temperature monitoring is required
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | MMTR-053 | TROLLEY: airway/intubation, 750W x 490D x 900H nom | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMGE-291 | DEVICE: pump, infusion, single | 2 | 1 | Pendant 1 - Arm 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 3 |  | optional, portable screens in lieu of ceiling mounted privacy curtains
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | FQBS-284 | RECLINER: visitor, clinical areas, lay flat, kangaroo care | 1 | 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FFE | MMGE-349 | DEVICE: amplitude-integrated electroencephalography (aEEG), with trolley | 1 | 3 |  | optional
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.)
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 1
PTB-NEO-IC | Patient Bay - Neonatal, Intensive Care / High Dependency | Neonatal Care | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 2
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | for storage of family member property, may be lockable
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | WLPR-006.03 | WALL PROTECTION: corner guards, to 1200 AFFL | 1 | 1 | Wall Protection
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to procedure light
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ELSW-001 | SWITCH: light | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | 1 to wall mounted telephone, 1 to milk fridge, 1 to patient monitor
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to write-up area
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | to family area
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | centre panel
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 4 | 1 | Panel 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 4 | 1 | Panel 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 2 | 1 | Panel 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Panel 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MGFP-041 | FLOWMETER: oxygen | 4 | 1 | Panel 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MGFP-061 | ADAPTER: suction | 4 | 1 | Panel 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | optional
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FIHR-115 | BRACKET: sharps bin, trolley mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FIRT-051.03 | TRACK: curtain, privacy, U-shaped | 1 | 3 |  | optional, optional, portable screens in lieu of ceiling mounted privacy curtains
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FQBS-284 | RECLINER: visitor, clinical areas, lay flat, kangaroo care | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FQCA-211 | APPLIANCE: bottle warmer, benchtop, domestic | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 3 |  | optional, portable screens in lieu of ceiling mounted privacy curtains
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | ITCL-464 | CAMERA: patient observation, neonatal, crib mounted | 1 | 3 |  | optional
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | LIFX-121 | LIGHT: procedure, minor, single articulated arm, 1 light head, ceiling mounted | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMGE-045 | POLE: IV, mobile | 2 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMGE-191 | CANNISTER: suction bottle | 4 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMGE-311 | DEVICE: pump, breast milk | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMHA-061 | DEVICE: ventilator, neonatal | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMMA-016 | INCUBATOR: infant, closed cot, humidicrib | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMMA-131 | FRIDGE: milk, 15L nominal, single door, benchtop | 1 | 1 |  | provision to suit local jurisdictional policies for breast milk storage to be centralised or decentralised; temperature monitoring is required
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMPM-026 | MONITOR: patient, high acuity, neonatal | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | MMTR-053 | TROLLEY: airway/intubation, 750W x 490D x 900H nom | 1 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 4 | 1
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.)
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | patient's right
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ELGP-176 | GPO: single, UPS, on services panel | 1 | 1 | Panel 2
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 2
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 3
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ELGP-176 | GPO: single, UPS, on services panel | 1 | 1 | Panel 3
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 3
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 3 | patient's left
PTB-NEO-SC | Patient Bay - Neonatal, Special Care | Neonatal Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 3
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] acoustic tiles are also acceptable
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 5 | 1 | Panel 1 | [ELGP-122] type and quantity to suit service requirements
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] on services panel
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to services panel, for examination downlight if provided
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033] type and extent of storage dependant on operational policies for stock centralisation/decanting and infection prevention and control policies
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 3 |  | [FQBS-030] optional
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 4 | 1 |  | [FQSN-006] type and size of bins dependant on items to be stored
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] on services panel, with indicator button and light
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel, with indicator button and light
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] on services panel
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1 | [ITIN-025] quantity to suit service requirements
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, for patient monitoring
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] shared between multiple bays
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 3 |  | [LIFX-032] optional, provision dependant on service requirements; articulated examination light is also acceptable
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | [MMBE-091]
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low, for patient recliner
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] for patient's own devices
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | [ELGP-223] optional, for patient monitoring
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain
PT-HOLD-A | Patient Bay - Holding, Chair | Perioperative | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] acoustic tiles are also acceptable
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] to services panel
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to services panel, for examination downlight if provided
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] on services panel, with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel, with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] on services panel
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, for patient monitoring
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 3 |  | [LIFX-032] optional, provision dependant on service requirements; articulated examination light is also acceptable
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | [MMBE-091]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 3 |  | [FQBS-030] optional
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033] type and extent of storage dependant on operational policies for stock centralisation/decanting and infection prevention and control policies
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 4 | 1 |  | [FQSN-006] type and size of bins dependant on items to be stored
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] shared between multiple bays
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | MMBE-121 | BED: patient, electric, with mattress, holding/recovery | 1 | 1 |  | [MMBE-007]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 5 | 1 | Panel 1 | [ELGP-122] type and quantity to suit service requirements
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1 | [ITIN-025] quantity to suit service requirements
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIDI-247 | HOLDER: alcohol-based hand rub, bed mounted | 1 | 1 |  | [FIHR-068]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] for patient's own devices
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low, for patient bed
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | [ELGP-223] optional, for patient monitoring
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 7 | 1 | Panel 1 | [ELGP-122] type and quantity to suit service requirements
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] on services panel
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] on services panel, for examination downlight
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FIDI-247 | HOLDER: alcohol-based hand rub, bed mounted | 1 | 1 |  | [FIHR-068] may be wall mounted depending on bedhead arrangment
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FIHR-029 | HOOK: equipment, wall mounted | 1 | 1 |  | [FIHR-029]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033] type and extent of storage dependant on operational policies for stock centralisation/decanting and infection prevention and control policies
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067] may be located on left or right side of bedhead depending on monitor functionality and staff workflows; appropriate wall support required
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 2 | 1 | Floor Skirting | [FLSK-010]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 4 | 1 |  | [FQSN-006] type and size of bins dependant on items to be stored
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142] shared between multiple bays
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1 | [ITIN-025] quantity to suit service requirements
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to patient monitor
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] shared between multiple bays
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | [LIFX-032] articulated examination light is also acceptable
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | MMBE-121 | BED: patient, electric, with mattress, holding/recovery | 1 | 1 |  | [MMBE-007]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1 |  | [MMGE-045] bed mounted IV pole or ceiling mounted IV track are also acceptable
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 |  | [MMHA-008] may be located on left or right side of bedhead depending on monitor functionality and staff workflows; appropriate wall support required for mounting bracket
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119] shared between multiple bays
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] with indicator button and light
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | ITCL-163 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] with indicator button and light
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | MSP | ITCL-252 | HANDSET: nurse call, patient to staff call, with light control | 1 | 1 | Panel 1 | [ITCL-028]
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-223] to patient monitor
PT-RS1 | Patient Bay - Recovery, Stage 1 | Perioperative | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] low, for patient bed and pressure mattress
PTRY | Pantry | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PTRY | Pantry | Logistics / Support Services | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PTRY | Pantry | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
PTRY | Pantry | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PTRY | Pantry | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 2 | 1 |  | [FIDI-025] 1 to basin, 1 to sink
PTRY | Pantry | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | [FIDI-030] 1 to basin, 1 to sink
PTRY | Pantry | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PTRY | Pantry | Logistics / Support Services | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | [FLVY-003] minimum slip rating R10 / pendulum P3 or agreed equivalent
PTRY | Pantry | Logistics / Support Services | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 1 | 1 |  | [FQCA-067]
PTRY | Pantry | Logistics / Support Services | FFE | FQCA-231 | ICE MACHINE: commercial, benchtop | 1 | 3 |  | [FQCA-015] optional; item to comply with infection control requirements
PTRY | Pantry | Logistics / Support Services | FFE | FQCA-422 | FRIDGE: commercial, 300L nom, single door | 1 | 1 |  | [FQCA-027] Clear area for fridge to allow for adequate ventilation and full opening of door. May be connected to BMS for temperature monitoring depending on service requirements,
PTRY | Pantry | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PTRY | Pantry | Logistics / Support Services | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] size, type and quantity of bins dependent on local waste management policies
PTRY | Pantry | Logistics / Support Services | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | [FQCW-062] size, type and quantity of bins dependent on local waste management policies
PTRY | Pantry | Logistics / Support Services | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
PTRY | Pantry | Logistics / Support Services | FFE | HYBA-303 | SINK: single bowl, with drainer | 1 | 1 |  | [HYBA-069]
PTRY | Pantry | Logistics / Support Services | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | [HYGE-003] + [HYTP-029] instant hot/cold water tap to sink; provide grille in joinery for ventilation
PTRY | Pantry | Logistics / Support Services | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
PTRY | Pantry | Logistics / Support Services | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] to boiling/ chilled water unit
PTRY | Pantry | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, to fridge, for temperature monitoring as required
PTRY | Pantry | Logistics / Support Services | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-069] minimum depth 600mm; where an ice machine is provided the depth may need to increase to accommodate appliance
PTRY | Pantry | Logistics / Support Services | FFE | JOCU-041 | CUPBOARD: tall, with 1 microwave shelf unit | 1 | 1 |  | [FIJO-163]
PTRY | Pantry | Logistics / Support Services | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 1 | 1 |  | [FIJO-156]
PTRY | Pantry | Logistics / Support Services | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-143]
PTRY | Pantry | Logistics / Support Services | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
PTRY | Pantry | Logistics / Support Services | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 1 | 1 |  | [FIJO-104]
PTRY | Pantry | Logistics / Support Services | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
PTRY | Pantry | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PTRY | Pantry | Logistics / Support Services | FIN | WLFI-101 | SPLASHBACK: vinyl | 4 | 1 | Wall Finish 2 | [WLWA-007] to bench with sink, to basin
PTRY | Pantry | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PTRY | Pantry | Logistics / Support Services | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] with hold open device to support trolley movement as required
PTRY | Pantry | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PTRY | Pantry | Logistics / Support Services | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional, dependent on security requirements and location of room
PTRY | Pantry | Logistics / Support Services | SER | ELGP-101 | GPO: single, wall mounted | 3 | 1 |  | [ELGP-109] 1 to fridge, 1 to microwave, 1 to boiling/ chilled water unit
PTRY | Pantry | Logistics / Support Services | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] over bench
RECP-10 | Reception, 10m2 | Public Areas | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
RECP-10 | Reception, 10m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 3 | 1 | Ceiling Finish 2 | [CLGE-001]
RECP-10 | Reception, 10m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
RECP-10 | Reception, 10m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
RECP-10 | Reception, 10m2 | Public Areas | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
RECP-10 | Reception, 10m2 | Public Areas | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
RECP-10 | Reception, 10m2 | Public Areas | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, for lighting control across unit/adjacent areas
RECP-10 | Reception, 10m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
RECP-10 | Reception, 10m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
RECP-10 | Reception, 10m2 | Public Areas | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
RECP-10 | Reception, 10m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
RECP-10 | Reception, 10m2 | Public Areas | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to printer
RECP-10 | Reception, 10m2 | Public Areas | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] below desk for computer workstation; location of outlets to meet local WHS requirements
RECP-10 | Reception, 10m2 | Public Areas | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
RECP-10 | Reception, 10m2 | Public Areas | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] dual screens may be provided to suit service requirements
RECP-10 | Reception, 10m2 | Public Areas | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
RECP-10 | Reception, 10m2 | Public Areas | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1 |  | [FIJO-051]
RECP-10 | Reception, 10m2 | Public Areas | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
RECP-10 | Reception, 10m2 | Public Areas | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
RECP-10 | Reception, 10m2 | Public Areas | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106]
RECP-10 | Reception, 10m2 | Public Areas | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | [FIJO-182]
RECP-10 | Reception, 10m2 | Public Areas | FFE | JORS-051 | SECURITY GLAZING: to reception | 3 | 3 |  | [WLPT-014] optional
RECP-10 | Reception, 10m2 | Public Areas | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 2 | 3 |  | [WLPT-015] optional
RECP-10 | Reception, 10m2 | Public Areas | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, for temperature control across unit/adjacent areas
RECP-10 | Reception, 10m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
RECP-10 | Reception, 10m2 | Public Areas | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
RECP-10 | Reception, 10m2 | Public Areas | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
RECP-10 | Reception, 10m2 | Public Areas | FFE | JORS-041 | WHITEBOARD: fixed, magnetic, integral to reception desk | 1 | 1 |  | [FIBM-019]
RECP-10 | Reception, 10m2 | Public Areas | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 1 | 1 |  | [FQSM-007]
RECP-10 | Reception, 10m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] for charging portable devices, to be located above desk for easy access; location of outlets to meet local WHS requirements
RECP-10 | Reception, 10m2 | Public Areas | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] below desk for computer workstation; extent of emergency power to be determined based on service requirements; location of outlets to meet local WHS requirements
RECP-10 | Reception, 10m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] to printer
RECP-10 | Reception, 10m2 | Public Areas | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 1 | 1 |  | [ITSE-006]
RECP-10 | Reception, 10m2 | Public Areas | SER | ITSE-298 | BUTTON: door release, remote activation, surface mounted | 1 | 3 |  | [ITSE-025] optional, to external entry and/or unit entry as required
RECP-15 | Reception, 15m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
RECP-15 | Reception, 15m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 3 | 1 | Ceiling Finish 2 | [CLGE-001]
RECP-15 | Reception, 15m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
RECP-15 | Reception, 15m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
RECP-15 | Reception, 15m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
RECP-15 | Reception, 15m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
RECP-15 | Reception, 15m2 | Public Areas | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
RECP-15 | Reception, 15m2 | Public Areas | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
RECP-15 | Reception, 15m2 | Public Areas | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
RECP-15 | Reception, 15m2 | Public Areas | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
RECP-15 | Reception, 15m2 | Public Areas | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, for lighting control across unit/adjacent areas
RECP-15 | Reception, 15m2 | Public Areas | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, for temperature control across unit/adjacent areas
RECP-15 | Reception, 15m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] 1 to each workstation for charging portable devices, to be located above desk for easy access; location of outlets to meet local WHS requirements
RECP-15 | Reception, 15m2 | Public Areas | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | [ELGP-223] 2 to each workstation; extent of emergency power to be determined based on service requirements; location of outlets to meet local WHS requirements
RECP-15 | Reception, 15m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] to printer
RECP-15 | Reception, 15m2 | Public Areas | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] 1 to each workstation; location of outlets to meet local WHS requirements
RECP-15 | Reception, 15m2 | Public Areas | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 1 | 1 |  | [ITSE-006]
RECP-15 | Reception, 15m2 | Public Areas | SER | ITSE-298 | BUTTON: door release, remote activation, surface mounted | 1 | 3 |  | [ITSE-025] optional, to external entry and/or unit entry as required
RECP-15 | Reception, 15m2 | Public Areas | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
RECP-15 | Reception, 15m2 | Public Areas | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to printer
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 3 | 3 |  | [WLPT-015] optional
RECP-15 | Reception, 15m2 | Public Areas | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-051 | SECURITY GLAZING: to reception | 3 | 3 |  | [WLPT-014] optional
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-041 | WHITEBOARD: fixed, magnetic, integral to reception desk | 1 | 1 |  | [FIBM-019]
RECP-15 | Reception, 15m2 | Public Areas | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 2 | 1 |  | [FQSM-007] 1 to each workstation
RECP-15 | Reception, 15m2 | Public Areas | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1 |  | [FIJO-051]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | [FIJO-099]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-135]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 2 | 1 |  | [FIJO-106]
RECP-15 | Reception, 15m2 | Public Areas | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | [FIJO-182]
RECP-15 | Reception, 15m2 | Public Areas | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018] 1 to each workstation
RECP-15 | Reception, 15m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
RECP-15 | Reception, 15m2 | Public Areas | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007] dual screens may be provided to suit service requirements
RECP-15 | Reception, 15m2 | Public Areas | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-049] 1 to each workstation
RECP-20 | Reception, 20m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
RECP-20 | Reception, 20m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 3 | 1 | Ceiling Finish 2 | [CLGE-001]
RECP-20 | Reception, 20m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
RECP-20 | Reception, 20m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
RECP-20 | Reception, 20m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
RECP-20 | Reception, 20m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
RECP-20 | Reception, 20m2 | Public Areas | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
RECP-20 | Reception, 20m2 | Public Areas | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
RECP-20 | Reception, 20m2 | Public Areas | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
RECP-20 | Reception, 20m2 | Public Areas | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
RECP-20 | Reception, 20m2 | Public Areas | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, for lighting control across unit/adjacent areas
RECP-20 | Reception, 20m2 | Public Areas | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, for temperature control across unit/adjacent areas
RECP-20 | Reception, 20m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] 1 to each workstation for charging portable devices, to be located above desk for easy access; location of outlets to meet local WHS requirements
RECP-20 | Reception, 20m2 | Public Areas | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 6 | 1 |  | [ELGP-223] 2 to each workstation; extent of emergency power to be determined based on service requirements; location of outlets to meet local WHS requirements
RECP-20 | Reception, 20m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] to printer
RECP-20 | Reception, 20m2 | Public Areas | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 3 | 1 |  | [ITIN-036] 1 to each workstation; location of outlets to meet local WHS requirements
RECP-20 | Reception, 20m2 | Public Areas | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 1 | 1 |  | [ITSE-006]
RECP-20 | Reception, 20m2 | Public Areas | SER | ITSE-298 | BUTTON: door release, remote activation, surface mounted | 1 | 3 |  | [ITSE-025] optional, to external entry and/or unit entry as required
RECP-20 | Reception, 20m2 | Public Areas | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
RECP-20 | Reception, 20m2 | Public Areas | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to printer
RECP-20 | Reception, 20m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 3 |  | [ELGP-208] optional, to label printer if provided
RECP-20 | Reception, 20m2 | Public Areas | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-061] optional, to label printer if provided
RECP-20 | Reception, 20m2 | Public Areas | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
RECP-20 | Reception, 20m2 | Public Areas | FFE | JORS-051 | SECURITY GLAZING: to reception | 3 | 3 |  | [WLPT-014] optional
RECP-20 | Reception, 20m2 | Public Areas | FFE | JORS-041 | WHITEBOARD: fixed, magnetic, integral to reception desk | 1 | 1 |  | [FIBM-019]
RECP-20 | Reception, 20m2 | Public Areas | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1 |  | [FIJO-051]
RECP-20 | Reception, 20m2 | Public Areas | FFE | JOBE-251 | CAP: cable access | 3 | 1 |  | [FIJO-099]
RECP-20 | Reception, 20m2 | Public Areas | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-135]
RECP-20 | Reception, 20m2 | Public Areas | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 2 | 1 |  | [FIJO-106]
RECP-20 | Reception, 20m2 | Public Areas | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | [FIJO-182]
RECP-20 | Reception, 20m2 | Public Areas | FFE | FQBS-171 | CHAIR: office, ergonomic | 3 | 1 |  | [FQBS-018] 1 to each workstation
RECP-20 | Reception, 20m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
RECP-20 | Reception, 20m2 | Public Areas | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007] dual screens may be provided to suit service requirements
RECP-20 | Reception, 20m2 | Public Areas | FFE | ITNE-071 | TELEPHONE: handset, desktop | 3 | 1 |  | [ITNE-049] 1 to each workstation
RECP-20 | Reception, 20m2 | Public Areas | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 2 | 1 |  | [FQSM-007]
RECP-20 | Reception, 20m2 | Public Areas | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 4 | 3 |  | [WLPT-015] optional
RECP-20 | Reception, 20m2 | Public Areas | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-056] optional
RECP-E | Reception - Emergency | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | to waiting area; may be located to provide direct access to the waiting area or to a zone behind the main entry doors
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to waiting area side
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to treatment areas side
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
RECP-E | Reception - Emergency | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 2 | to department treatment areas
RECP-E | Reception - Emergency | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
RECP-E | Reception - Emergency | Emergency | SER | ITSE-186 | INTERCOM: audio-visual, slave, wall mounted | 1 | 1 |  | connected to intercom at external entry doors and security observation room
RECP-E | Reception - Emergency | Emergency | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional, provision dependent on clinical services requirements
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-316 | PRINTER: labels, small, desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | JORS-001 | JOINERY UNIT: reception desk | 2 | 1 |  | counters may be provided as standing height or seated height, or a mix of both; at least one counter to provide wheelchair access as per AS1428.1 / NZS 4121; joinery configuration may include privacy dividers between reception counters to support acoustic privacy with sensitive conversations, and materiality to be confirmed to balance privacy requirements with waiting room observation
RECP-E | Reception - Emergency | Emergency | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | FQGE-226 | DEVICE: electronic funds transfer at point of sale (EFTPOS) | 1 | 1 |  | optional; provision dependent on operational models
RECP-E | Reception - Emergency | Emergency | FFE | JOSH-001 | SHELF UNIT: tall, adjustable shelves | 1 | 1 |  | type, extent and configuration of storage for stationery and consumables will be dependent on operational models for EMR and local ICT strategies and policies
RECP-E | Reception - Emergency | Emergency | D+W | WIFX-008.01 | WINDOW: fixed, internal, single glazed, sill at 1050H | 1 | 3 | Internal - Window 1 | optional, may be provided to allow for visual access to ambulance entry, if collocated, to support efficient registration of patients; provision is dependent on overall department planning and operational models
RECP-E | Reception - Emergency | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to shelving unit
RECP-E | Reception - Emergency | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-311 | PRINTER: desktop | 4 | 1 |  | 1 to each reception workstation, 1 to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | for roaming clerk(s)
RECP-E | Reception - Emergency | Emergency | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 3 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to clerk workstation for printer
RECP-E | Reception - Emergency | Emergency | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | type and size of screen to be confirmed to suit security requirements
RECP-E | Reception - Emergency | Emergency | SER | ITSE-091 | BUTTON: security, perimeter lockdown, wall mounted | 1 | 1 |  | to activate lock down tof external entry doors and/or unit entry doors; requirements to be confirmed at project level based on security protocols and operational policies for unit lockdown
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to patient flow display screen if provided
RECP-E | Reception - Emergency | Emergency | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | to general room lighting, 1 to each door
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
RECP-E | Reception - Emergency | Emergency | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
RECP-E | Reception - Emergency | Emergency | SER | ITSE-298 | BUTTON: door release, remote activation, surface mounted | 3 | 1 |  | 1 to each reception workstation; to open external entry doors and/or unit entry doors
RECP-E | Reception - Emergency | Emergency | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 3 | 1 |  | configuration of communication slot and pass through aperture to be confirmed at project level to suit clinical services requirements and operational models
RECP-E | Reception - Emergency | Emergency | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 4 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 6 | 1 |  | 2 to each reception workstation
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to clerk workstation
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to patient flow display screen if provided
RECP-E | Reception - Emergency | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to workstation on wheels (WOW) for roaming clerk(s)
RECP-E | Reception - Emergency | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to clock; an additional power outlet may be required if power over ethernet (PoE) is not supported by the clock hardware
RECP-E | Reception - Emergency | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to clerk workstation for printer
RECP-E | Reception - Emergency | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | to security CCTV display screen
RECP-E | Reception - Emergency | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | optional, to patient flow display screen if provided
RECP-E | Reception - Emergency | Emergency | FFE | FQSM-081 | PEDESTAL: mobile, 660H nominal, 1 drawer and 1 printer shelf | 3 | 1 |  | 1 to each reception workstation
RECP-E | Reception - Emergency | Emergency | FFE | ITBU-470 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall mounted | 1 | 1 |  | type of clock and requirement for connection to the master clock system is to be confirmed at a project level based on clinical services requirements
RECP-E | Reception - Emergency | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 3 | 1 |  | 1 to each reception workstation for printers
RECP-E | Reception - Emergency | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
RECP-E | Reception - Emergency | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 3 | 1 | Wall Finish 1
RECP-E | Reception - Emergency | Emergency | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
RECP-E | Reception - Emergency | Emergency | FIN | CLBK-012 | BULKHEAD: flush set, acoustic | 1 | 1 | Ceiling Finish 2
RECP-E | Reception - Emergency | Emergency | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 3 | to bulkhead
RECP-E | Reception - Emergency | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
RECP-E | Reception - Emergency | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 12 | 1 | Floor Skirting
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
RECP-E | Reception - Emergency | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to room side
RECP-E | Reception - Emergency | Emergency | D+W | WIOP-008 | WINDOW: operable, sliding, internal, single glazed, sill at 1050H | 1 | 3 | Internal - Window 2 | optional, may be provided to triage assessment room, if collocated, to ensure staff are not isolated in the front of house area; provision is dependent on overall department planning, staffing models and WHS policies
RECP-E | Reception - Emergency | Emergency | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 3 | 1 |  | 1 to each reception workstation for printers
RECP-E | Reception - Emergency | Emergency | FFE | JORS-051 | SECURITY GLAZING: to reception | 1 | 1 |  | between reception counters to support acoustic privacy with sensitive conversations and materiality to be confirmed to balance privacy requirements with waiting room observation
RECP-E | Reception - Emergency | Emergency | FIN | WLPR-006.03 | WALL PROTECTION: corner guards, to 1200 AFFL | 3 | 1 | Wall Protection
REPR | Reporting Room | Medical Imaging | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
REPR | Reporting Room | Medical Imaging | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
REPR | Reporting Room | Medical Imaging | FIN | CLTI-022 | CEILING: drop-in tiles, acoustic, prefinished | 1 | 1 | Ceiling Finish 1
REPR | Reporting Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
REPR | Reporting Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
REPR | Reporting Room | Medical Imaging | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 1 | 1 | Wall Finish 2 | as required to reduce noise transfer between workstations
REPR | Reporting Room | Medical Imaging | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | cover to vision panel provided as required to reduce transfer of light from corridor
REPR | Reporting Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
REPR | Reporting Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor, coordinated with adjacent wall protection, to suit mobile equipment and patient trolley movement
REPR | Reporting Room | Medical Imaging | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 1
REPR | Reporting Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | optional - provision dependent on location of room in relation to public/patient areas and local WHS policies
REPR | Reporting Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | optional - to x-ray viewer if provided
REPR | Reporting Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
REPR | Reporting Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 2 | 1 |  | optional - 1 to each workstation to connect desktop computers to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | SER | ITIN-171 | DESK BOX: power and data outlets, softwired, surface mounted | 2 | 1 |  | 1 to each workstation, for charging/power to portable devices, number and type of power/AV outlets to be confirmed to suit ICT requirements
REPR | Reporting Room | Medical Imaging | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional - provision to ensure staff only access, requirement dependent on location of room in relation to public/patient areas
REPR | Reporting Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 3 | 1 |  | 1 to general room lighting, 1 to each workstation to indirect lighting
REPR | Reporting Room | Medical Imaging | SER | LIFX-079 | LIGHT: linear, indirect, wall mounted | 2 | 1 |  | dimmable, 1 to each workstation, to be coordinated with general room lighting to suit reporting task requirements
REPR | Reporting Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
REPR | Reporting Room | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1
REPR | Reporting Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 4 | 1 |  | 2 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | optional
REPR | Reporting Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | FIHR-231 | BRACKET: computer display screen, triple, articulated, bench/desk mounted | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | optional - to wall mounted display screen if provided
REPR | Reporting Room | Medical Imaging | FFE | FQSN-287 | CABINET: floor standing, 1800H nominal, tambour unit | 1 | 1 |  | optional - type and size of storage solutions to suit service requirements
REPR | Reporting Room | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | optional - one additional chair per workstation for consultation and training
REPR | Reporting Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | optional - large wall mounted display screen for collaborative image reviewing
REPR | Reporting Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | MMGE-151 | LIGHT BOX: x-ray viewer, wall mounted | 1 | 1 |  | optional
REPR | Reporting Room | Medical Imaging | FFE | ITNE-241 | RECORDER: dictation | 2 | 1 |  | 1 to each workstation
REPR | Reporting Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | optional
REPR | Reporting Room | Medical Imaging | FFE | FQDW-165.07 | WORKSTATION: straight, adjustable height, electric, 720H nom, 800D x 2200W | 2 | 1
REPR | Reporting Room | Medical Imaging | FFE | FQGE-109 | SCREEN: privacy, acoustic, floor standing | 1 | 1 |  | as required to reduce noise transfer between workstations
REPR | Reporting Room | Medical Imaging | FFE | ITNE-251 | CAMERA: webcam, display screen mounted | 2 | 1 |  | optional
REPW | Reporting Workstation | Medical Imaging | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
REPW | Reporting Workstation | Medical Imaging | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 1 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
REPW | Reporting Workstation | Medical Imaging | FIN | CLTI-022 | CEILING: drop-in tiles, acoustic, prefinished | 1 | 1 | Ceiling Finish 1
REPW | Reporting Workstation | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
REPW | Reporting Workstation | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
REPW | Reporting Workstation | Medical Imaging | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 1 | 1 | Wall Finish 2 | as required to reduce noise transfer between workstations
REPW | Reporting Workstation | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
REPW | Reporting Workstation | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
REPW | Reporting Workstation | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1
REPW | Reporting Workstation | Medical Imaging | SER | ITIN-066 | OUTLET: data, HDMI, wall mounted | 1 | 1 |  | optional - to connect desktop computers to wall mounted display screen (shared between multiple workstations) if provided
REPW | Reporting Workstation | Medical Imaging | SER | ITIN-171 | DESK BOX: power and data outlets, softwired, surface mounted | 1 | 1 |  | for charging/power to portable devices, number and type of power/AV outlets to be confirmed to suit ICT requirements
REPW | Reporting Workstation | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to indirect lighting
REPW | Reporting Workstation | Medical Imaging | SER | LIFX-079 | LIGHT: linear, indirect, wall mounted | 1 | 1 |  | dimmable, to be coordinated with general room lighting to suit reporting task requirements
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | optional - additional chair for consultation and training
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-241 | RECORDER: dictation | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FQDW-165.07 | WORKSTATION: straight, adjustable height, electric, 720H nom, 800D x 2200W | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FQGE-109 | SCREEN: privacy, acoustic, floor standing | 2 | 1 |  | as required to reduce noise transfer between workstations
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-251 | CAMERA: webcam, display screen mounted | 1 | 1 |  | optional
REPW | Reporting Workstation | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 2 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
REPW | Reporting Workstation | Medical Imaging | FFE | FIHR-231 | BRACKET: computer display screen, triple, articulated, bench/desk mounted | 1 | 1
SECL | Seclusion Room | Mental Health | FIN | FLVY-102 | FLOOR FINISH: vinyl, seamless, standard slip resistance, cushioned | 1 | 1 | Floor Finish 1
SECL | Seclusion Room | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 5 | 1 | Floor Skirting
SECL | Seclusion Room | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 3 | 1 | Wall Finish 1
SECL | Seclusion Room | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
SECL | Seclusion Room | Mental Health | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 3 | Internal - Door 1 | optional; to room side if provided; provision dependent on leaf material and finish
SECL | Seclusion Room | Mental Health | D+W | DOHI-019.12 | DOOR: hinged, 1 leaf, 1200 clear opening, solid, anti-ligature and anti-barricade, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1
SECL | Seclusion Room | Mental Health | D+W | WIFX-057.04 | WINDOW: fixed, internal, double glazed, sill at 900H, with integral blind | 1 | 1 | Internal - Window 1 | for observation from staff area; control for blinds external to room
SECL | Seclusion Room | Mental Health | FFE | FIBM-216 | MIRROR: fixed, convex, indoor, tamper proof, anti-ligature, quarter dome, wall and ceiling mounted | 1 | 1
SECL | Seclusion Room | Mental Health | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 2 | 3 |  | optional; connection requirements to be confirmed; music source to be controlled from device in staff observation area
SECL | Seclusion Room | Mental Health | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to staff observation area
SECL | Seclusion Room | Mental Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | to staff observation area
SECL | Seclusion Room | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to staff observation area
SECL | Seclusion Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | optional; to corridor side if provided; provision dependent on leaf material and finish
SECL | Seclusion Room | Mental Health | D+W | WIOP-262.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 1650H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 1 | blinds controlled from staff area
SECL | Seclusion Room | Mental Health | D+W | WIOP-262.03 | WINDOW: operable, jockey sash, external, double glazed, sill at 1650H, with integral blind, tamper proof, anti-ligature | 1 | 1 | External - Window 2 | blinds controlled from staff area
SECL | Seclusion Room | Mental Health | FIN | CLFS-014 | CEILING: flush set, suspended, impact resistant | 1 | 1 | Ceiling Finish 1 | consider plywood backing to ceiling finish
SECL | Seclusion Room | Mental Health | FFE | MMBE-184 | MATTRESS: patient, tamper proof, anti-ligature, with sealed seams | 1 | 1
SECL | Seclusion Room | Mental Health | SER | AHWHC-001 | CONTROL PANEL: integral blinds, remote operation, wall mounted | 1 | 1 |  | to staff observation area
SECL | Seclusion Room | Mental Health | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | to staff observation area
SECR | Security Observation Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
SECR | Security Observation Room | Logistics / Support Services | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 3 | External - Window 1 | [DWWD-004] optional, to external window if provided
SECR | Security Observation Room | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SECR | Security Observation Room | Logistics / Support Services | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
SECR | Security Observation Room | Logistics / Support Services | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] lockable, with secure staff-only access
SECR | Security Observation Room | Logistics / Support Services | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
SECR | Security Observation Room | Logistics / Support Services | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
SECR | Security Observation Room | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
SECR | Security Observation Room | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
SECR | Security Observation Room | Logistics / Support Services | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018]
SECR | Security Observation Room | Logistics / Support Services | FFE | FQSN-112 | CABINET: key management, electronic | 1 | 3 |  | [ITSE-010] optional
SECR | Security Observation Room | Logistics / Support Services | FFE | FQSN-124 | SAFE: medium, wall mounted | 1 | 1 |  | [FQSN-061] for securing lost items of value as required
SECR | Security Observation Room | Logistics / Support Services | FFE | FQSN-131 | SAFE: small, handgun, wall mounted | 1 | 3 |  | [FQSN-060] optional, for securing contraband and weapons, provision in alignment with operational policies and jurisdictional requirements; may be floor mounted.
SECR | Security Observation Room | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, to PC for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026] 1 to each workstation, 1 to bench with printers
SECR | Security Observation Room | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to CCTV display screen; quantity to meet security requirements
SECR | Security Observation Room | Logistics / Support Services | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-050] 1 to each computer workstation
SECR | Security Observation Room | Logistics / Support Services | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007]
SECR | Security Observation Room | Logistics / Support Services | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | [ITNE-007] optional, for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | Logistics / Support Services | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
SECR | Security Observation Room | Logistics / Support Services | FFE | ITNE-321 | PRINTER: identification/access control card, desktop | 1 | 3 |  | [ITNE-022] optional, for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | Logistics / Support Services | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] mounted under bench; may be wall mounted
SECR | Security Observation Room | Logistics / Support Services | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | [ITSE-048] type and quantity to meet security requirements for CCTV camera feed observation
SECR | Security Observation Room | Logistics / Support Services | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | [ITSE-038]
SECR | Security Observation Room | Logistics / Support Services | FFE | ITSE-296 | CAMERA: identification photo | 1 | 3 |  | [ITSE-019] optional, for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | Logistics / Support Services | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
SECR | Security Observation Room | Logistics / Support Services | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-031]
SECR | Security Observation Room | Logistics / Support Services | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | [FIHR-080]
SECR | Security Observation Room | Logistics / Support Services | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-117]
SECR | Security Observation Room | Logistics / Support Services | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-136]
SECR | Security Observation Room | Logistics / Support Services | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
SECR | Security Observation Room | Logistics / Support Services | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 1 | [DWOB-016]
SECR | Security Observation Room | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
SECR | Security Observation Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SECR | Security Observation Room | Logistics / Support Services | D+W | WIOP-008 | WINDOW: operable, sliding, internal, single glazed, sill at 1050H | 1 | 1 | Internal - Window 2 | [DWWH-002] sliding window for reception
SECR | Security Observation Room | Logistics / Support Services | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 3 | External - Window 1 | [DWWH-005] optional, provide as required for surveillance of external areas
SECR | Security Observation Room | Logistics / Support Services | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 6 | 1 |  | [ELGP-223] 2 to each workstation, 2 to bench with printers
SECR | Security Observation Room | Logistics / Support Services | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 3 |  | [ELGP-223] optional, to PC for provision of identification cards, access cards and visitor passes, this may occur at a central security unit reception
SECR | Security Observation Room | Logistics / Support Services | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | [ELGP-223] to CCTV display screen; quantity to meet security requirements
SECR | Security Observation Room | Logistics / Support Services | FFE | ITSE-078 | CHARGER: security, portable radios, desktop | 1 | 1 |  | [FQGE-003] for radios, cameras and other devices as required
SHAC | Shower - Accessible | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
SHAC | Shower - Accessible | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
SHAC | Shower - Accessible | Sanitary Facilities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1 |  | [FIDI-049] soap dispenser is also acceptable, to shower
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIRT-166 | GRAB RAIL: shower, T-shaped, vertical and horizontal | 1 | 1 |  | [FIRT-045] with bracket for hand held accessible shower mounted on vertical rail
SHAC | Shower - Accessible | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
SHAC | Shower - Accessible | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] to be suitable for bare feet; tiles are also acceptable
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SHAC | Shower - Accessible | Sanitary Facilities | FFE | HYSH-057 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail, accessible | 1 | 1 |  | [HYTP-045]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1 |  | [HYTP-039]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 1 |  | [FIJO-194]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | [MMGE-024] wall mounted fold-down bench seat is also acceptable
SHAC | Shower - Accessible | Sanitary Facilities | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable
SHAC | Shower - Accessible | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
SHAC | Shower - Accessible | Sanitary Facilities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional, may be provided if room is for staff use and located in a public / patient treatment area
SHAC | Shower - Accessible | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SHAC | Shower - Accessible | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, emergency release required if inward opening door
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 3 |  | outside door, placement to ensure visibility along paths of travel; optional, to be provided if room located in a patient treatment area for use by patients
SHAC | Shower - Accessible | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | 1 to shower head
SHAC | Shower - Accessible | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | 1 to shower head
SHAC | Shower - Accessible | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] IPX4 rating required
SHAC | Shower - Accessible | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
SHAC | Shower - Accessible | Sanitary Facilities | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 3 |  | [ITCL-006] IPX4 rating required; optional, to be provided if room located in a patient treatment area for use by patients
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 3 |  | [ITCL-008] IPX4 rating required; optional, to be provided if room located in a patient treatment area for use by patients
SHAC | Shower - Accessible | Sanitary Facilities | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 3 |  | [ITCL-004] IPX4 rating required; optional, to be provided if room located in a patient treatment area for use by patients
SHPT | Shower - Patient | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] IPX4 rating required
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1 |  | [FIDI-049] soap dispenser is also acceptable, to shower
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIRT-166 | GRAB RAIL: shower, T-shaped, vertical and horizontal | 1 | 1 |  | [FIRT-045] with bracket for hand held shower mounted on vertical rail
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIRT-206 | RAIL: towel, wall mounted | 1 | 1 |  | [FIRT-016] with grab rail strength/fixings
SHPT | Shower - Patient | Sanitary Facilities | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SHPT | Shower - Patient | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
SHPT | Shower - Patient | Sanitary Facilities | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
SHPT | Shower - Patient | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
SHPT | Shower - Patient | Sanitary Facilities | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | [HYTP-020]
SHPT | Shower - Patient | Sanitary Facilities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
SHPT | Shower - Patient | Sanitary Facilities | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1 |  | [HYTP-039]
SHPT | Shower - Patient | Sanitary Facilities | FFE | MMGE-024 | CHAIR: shower | 1 | 3 |  | [MMGE-024] or commode chair, optional
SHPT | Shower - Patient | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
SHPT | Shower - Patient | Sanitary Facilities | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
SHPT | Shower - Patient | Sanitary Facilities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
SHPT | Shower - Patient | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
SHPT | Shower - Patient | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
SHPT | Shower - Patient | Sanitary Facilities | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable
SHPT | Shower - Patient | Sanitary Facilities | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-008] IPX4 rating required
SHPT | Shower - Patient | Sanitary Facilities | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-006] IPX4 rating required
SHPT | Shower - Patient | Sanitary Facilities | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-004] IPX4 rating required
SHPT | Shower - Patient | Sanitary Facilities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 3 |  | [ELGP-208] optional, to support grooming (i.e. shaving, hair drying, etc.); inclusion to be informed by local policies on the provision and maintenance of electrical outlets in wet areas
SHPT | Shower - Patient | Sanitary Facilities | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SHPT | Shower - Patient | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
SHPT | Shower - Patient | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SHPT | Shower - Patient | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, emergency release required if inward opening door
SHPT | Shower - Patient | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to shower head
SHPT | Shower - Patient | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to shower head
SHPT | Shower - Patient | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
SHST | Shower - Staff | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
SHST | Shower - Staff | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
SHST | Shower - Staff | Sanitary Facilities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
SHST | Shower - Staff | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
SHST | Shower - Staff | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
SHST | Shower - Staff | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
SHST | Shower - Staff | Sanitary Facilities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 3 |  | [FIDI-049] optional
SHST | Shower - Staff | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 1 | 1 |  | [FIHR-026]
SHST | Shower - Staff | Sanitary Facilities | FFE | FIRT-206 | RAIL: towel, wall mounted | 1 | 1 |  | [FIRT-016]
SHST | Shower - Staff | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
SHST | Shower - Staff | Sanitary Facilities | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SHST | Shower - Staff | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
SHST | Shower - Staff | Sanitary Facilities | FFE | HYSH-001 | SHOWER: fixed rose, wall mounted | 1 | 1 |  | [HYTP-018]
SHST | Shower - Staff | Sanitary Facilities | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1 |  | [HYTP-039]
SHST | Shower - Staff | Sanitary Facilities | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable
SHST | Shower - Staff | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
SHST | Shower - Staff | Sanitary Facilities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with privacy latch, emergency release required if inward opening door
SHST | Shower - Staff | Sanitary Facilities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional, may be provided if room located in a public / patient treatment area
SHST | Shower - Staff | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SHST | Shower - Staff | Sanitary Facilities | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
SHST | Shower - Staff | Sanitary Facilities | FFE | FIGE-023 | BENCH SEAT: fixed, indoor, wet area, wall mounted | 1 | 1 |  | [FIGE-003]
SHST | Shower - Staff | Sanitary Facilities | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-033] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | [DWSC-005]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-034] to corridor
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGE-051 | POWER SUPPLY UNIT: uninterruptable power supply (UPS) | 1 | 3 |  | [ELGT-007] optional, dependent on vendor requirements
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | [ELGP-122]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | [ELPR-007]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006] on services panel
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012] number determined by number of doors
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014] near door
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | [FIHR-030]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-017 | BIN: sharps, clinical, radioactive, high energy, small | 1 | 1 |  | [FQCW-066]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel + indicator button & light
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] on services panel + indicator button & light
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 1 | 1 |  | [ITCL-012 + FIHR-077]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] on wall near SPECT/CT unit
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-117]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-136]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | [LIFX-002] auto on when modality is in use
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1 |  | [MMMI-377]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-051 | INJECTOR: contrast, pedestal, mobile | 1 | 3 |  | [MMMI-100] optional, floor or ceiling mounted to be confirmed
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-001 | IMAGING DEVICE: SPECT-CT | 1 | 1 |  | [MMMI-262]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-009 | CART: collimator, SPECT-CT | 4 | 1 |  | [MMMI-264] required quantity dependent on patient mix
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-021 | SYSTEM CABINET: SPECT-CT | 1 | 1 |  | [MMMI-263]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-023 | BOARD: electrical distribution (EDB), SPECT-CT | 1 | 1 |  | [MMMI-265]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-023 | BOARD: electrical distribution (EDB), SPECT-CT | 1 | 1 |  | [MMMI-272]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MISP-041 | PHANTOM: SPECT-CT | 1 | 1 |  | [MMMI-273]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | [MMBE-042]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-045 | POLE: IV, mobile | 1 | 3 |  | [MMGE-045] optional
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-337 | DEVICE: electrocardiography (ECG), with trolley | 1 | 1 |  | [MMGE-179] procured with SPECT/CT system vendor
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 |  | [MMHA-032]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026] patient services
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | [MMGE-139]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 7 | 1 | Wall Finish 2 | [WLWA-020]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 3 | [WLWA-007]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | [ITCL-012 + FIHR-078]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109] clock
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123.1]
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 5 | 1 |  | [ELGP-223] to walls
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 3 | Internal - Window 1 | [DWOB-009] optional, patient observation by camera may be considered, glazing to be AS1428 compliant safety glass
SPECT-CT | SPECT-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to control room side
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004] to observation window for patient privacy
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-005] to imaging room
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | [DWGL-005]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | [ELBO-012]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | [ELBO-001] mains power, consult manufacturer for safety and compatibility with equipment.
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | [FIHR-044]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | [FIHR-075]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | [FIHR-070]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FIHR-341 | BRACKET: display screen, single, articulated, wall mounted | 1 | 1 |  | [FIHR-066]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQDW-134.04 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1600W | 1 | 1 |  | [FQDW-054]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 1 | 1 |  | [ITAV-014] communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1 |  | [ITAV-057] communication with patient, on bench required if integrated intercom system not provided by equipment manufacturer
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016] 1 outlet for display screen, patient monitor slave; one outlet for telephone
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 4 | 1 |  | [ITIN-026]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | [ITNE-068]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | [ITNE-070]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-056]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | [FIJO-031]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | [LIFX-002] auto on when modality is in use
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 3 |  | [MMMI-369] optional
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MISP-011 | CONTROL CONSOLE: SPECT-CT, dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1 |  | [MMMI-274]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MISP-016 | COMPUTER: SPECT-CT, central processing unit (CPU) | 1 | 1 |  | [MMMI-269]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 3 |  | [MMGE-032] optional
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | FFE | ITNE-342 | SCANNER: desktop, document, upright, desktop | 1 | 1 |  | [FQGE-094]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-161 | GPO: single, UPS, wall mounted | 5 | 1 |  | [ELGP-135]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] to printer
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | [ELGP-223]
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to imaging room side
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to control room side
SPECT-CTCR | SPECT-CT Control Room | Nuclear Medicine / PET | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009]
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 4 | 1 |  | [ELGP-109]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 4 | 1 |  | [ELGP-208]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10/ pendulum P3 or agreed equivalent around sink
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQBS-151 | CHAIR: dining areas | 4 | 1 |  | [FQBS-015]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQBS-351 | LOUNGE: 1 seat | 2 | 1 |  | [FQBS-039]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1 |  | [FQBS-042]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 1 | 1 |  | [FQCA-067]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQCA-402 | FRIDGE: domestic, 300L nom, single door | 1 | 1 |  | [FQCA-032]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQTA-202 | TABLE: square, 450H, 600L | 1 | 1 |  | [FQTA-075]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQTA-425.01 | TABLE: round, 750H, 900 diameter | 1 | 1 |  | [FQTA-055]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] quantity and type of bins to be based on local waste management policies
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | FSSP-101 | FIRE EXTINGUISHER: blanket | 1 | 1 |  | [FSPV-005]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | FSSP-102 | FIRE EXTINGUISHER: dry chemical | 1 | 1 |  | [FSPV-004] type to be confirmed at project level
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | [HYBA-080]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | [HYGE-003] + [HYTP-029] instant hot/cold water tap to sink; provide grille in joinery for ventilation
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITBU-011]
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 3 |  | [ITCL-001] optional, as required in patient care areas, audible
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] 1 x to television, 1 x to telephone
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOCU-041 | CUPBOARD: tall, with 1 microwave shelf unit | 1 | 1 |  | [FIJO-163]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-143]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JODW-012 | DRAWER UNIT: under bench, single drawer, slide out 1 bin | 1 | 1 |  | [FIJO-226] inclusion will depend on waste management and local IPC policies
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] external outlook is desirable
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
SRM-15 | Staff Room, 15m2 | Staff Amenities | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-010]
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SRM-15 | Staff Room, 15m2 | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | [ITIN-070] to television, may be replaced with data outlet in accordance with ICT policy
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to boiling/chilled water unit
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
SRM-15 | Staff Room, 15m2 | Staff Amenities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
SRM-35 | Staff Room, 35m2 | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
SRM-35 | Staff Room, 35m2 | Staff Amenities | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
SRM-35 | Staff Room, 35m2 | Staff Amenities | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 5 | 1 |  | [ELGP-109]
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 6 | 1 |  | [ELGP-208]
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 13 | 1 | Floor Skirting | [FLSK-010]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10/ pendulum P3 or agreed equivalent around sink
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQBS-151 | CHAIR: dining areas | 16 | 1 |  | [FQBS-015]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQBS-351 | LOUNGE: 1 seat | 4 | 1 |  | [FQBS-039]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQBS-352 | LOUNGE: 2 seat | 2 | 1 |  | [FQBS-042]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 2 | 1 |  | [FQCA-067]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQCA-402 | FRIDGE: domestic, 300L nom, single door | 1 | 1 |  | [FQCA-032]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQTA-202 | TABLE: square, 450H, 600L | 3 | 1 |  | [FQTA-075]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQTA-425.01 | TABLE: round, 750H, 900 diameter | 4 | 1 |  | [FQTA-055]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] quantity and type of bins to be based on local waste management policies
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | [FQCW-062] quantity and type of bins to be based on local waste management policies
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | FSSP-101 | FIRE EXTINGUISHER: blanket | 1 | 1 |  | [FSPV-005]
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | FSSP-102 | FIRE EXTINGUISHER: dry chemical | 1 | 1 |  | [FSPV-004] type to be confirmed at project level
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | [HYBA-080]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | [HYGE-003] + [HYTP-029] instant hot/cold water tap to sink; provide grille in joinery for ventilation
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITBU-011]
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | ITCL-101 | ANNUNCIATOR: nurse call | 1 | 3 |  | [ITCL-001] optional, as required in patient care areas, audible
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] 1 x to television, 1 x to telephone
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-116]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOCU-042 | CUPBOARD: tall, with 2 microwave shelf units | 1 | 1 |  | [FIJO-164]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 1 | 1 |  | [FIJO-156]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | [FIJO-143]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JODW-012 | DRAWER UNIT: under bench, single drawer, slide out 1 bin | 2 | 1 |  | [FIJO-226] inclusion will depend on waste management and infection control policies
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 3 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
SRM-35 | Staff Room, 35m2 | Staff Amenities | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] external outlook is desirable
SRM-35 | Staff Room, 35m2 | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
SRM-35 | Staff Room, 35m2 | Staff Amenities | FIN | WLFI-101 | SPLASHBACK: vinyl | 3 | 1 | Wall Finish 2 | [WLWA-010]
SRM-35 | Staff Room, 35m2 | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
SRM-35 | Staff Room, 35m2 | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038] optional
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | [ITIN-070] to television, may be replaced with data outlet in accordance with ICT policy
SRM-35 | Staff Room, 35m2 | Staff Amenities | FFE | JOGE-037 | SHROUD: under bench, removable, accessible | 1 | 1 |  | [FIJO-228] to sink and associated plumbing
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | 1 to sink tapware, 1 to boiling/chilled water unit
SRM-35 | Staff Room, 35m2 | Staff Amenities | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] acoustic ceiling treatments are also acceptable, including bulkheads
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 3 |  | [ELPR-007] optional
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] to task lighting
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | FQBS-171 | CHAIR: office, ergonomic | 2 | 1 |  | [FQBS-018]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 1 |  | [ITNE-049]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-007]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] under bench
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | [FIJO-099]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | JORS-021 | JOINERY UNIT: staff station | 1 | 1 |  | [FIJO-178] depth of bench and counter top to be confirmed based on service requirements and must consider ergonomics, staff safety and security, WHS requirements and Australian Standards
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] under counter top
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 3 |  | [MGFP-001] optional, location dependent on project requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | FFE | JORS-042 | WHITEBOARD: fixed, magnetic, integral to staff station | 1 | 1 |  | [FIBM-019] under counter top
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1 |  | [ELGP-208] for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 2 | 1 |  | [ELGP-223] location of outlets to meet local operational/WHS requirements
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-171 | GPO: single, UPS, joinery mounted | 1 | 1 |  | [ELGP-130] to printer; UPS to be provided if downtime computer required
SSTN-10 | Staff Station, 10m2 | Clinical Support Set 2 | SER | ELGP-271 | GPO: double, UPS, joinery mounted | 1 | 1 |  | [ELGP-235] UPS to be provided if downtime computer required, location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] acoustic ceiling treatments are also acceptable, including bulkheads
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 3 |  | [ELPR-007] optional
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] to task lighting
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, location dependent on project requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | FQBS-171 | CHAIR: office, ergonomic | 3 | 1 |  | [FQBS-018]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 2 | 1 |  | [FQSM-007]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 3 |  | [ITIN-016] 1 x optional, to labels printer if provided
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 3 | 1 |  | [ITIN-036] location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | ITNE-071 | TELEPHONE: handset, desktop | 3 | 1 |  | [ITNE-049]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 3 | 1 |  | [ITNE-007]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 3 |  | [FQGE-056] optional, dependent on service requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] under bench
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | JOBE-251 | CAP: cable access | 3 | 1 |  | [FIJO-099]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | JORS-021 | JOINERY UNIT: staff station | 1 | 1 |  | [FIJO-178] depth of bench and counter top to be confirmed based on service requirements and must consider ergonomics, staff safety and security, WHS requirements and Australian Standards
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | LIFX-108 | LIGHT: task, integral to joinery | 3 | 1 |  | [LIFX-008] under counter top
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, location dependent on project requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 3 |  | [MGFP-001] optional, location dependent on project requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | FFE | JORS-042 | WHITEBOARD: fixed, magnetic, integral to staff station | 1 | 1 |  | [FIBM-019] under counter top
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELGP-171 | GPO: single, UPS, joinery mounted | 1 | 1 |  | [ELGP-130] to printer, UPS to be provided if downtime computer required
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELGP-211 | GPO: double, joinery mounted | 3 | 1 |  | [ELGP-208] for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELGP-271 | GPO: double, UPS, joinery mounted | 1 | 1 |  | [ELGP-235] UPS to be provided if downtime computer required, location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 1 | 1 |  | [ELGP-223] location of outlets to meet local operational/WHS requirements
SSTN-14 | Staff Station, 14m2 | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] acoustic ceiling treatments are also acceptable, including bulkheads
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELGP-261 | GPO: double, UPS, wall mounted | 1 | 1 |  | [ELGP-235] UPS to be provided if downtime computer required, location of outlets to meet local operational/WHS requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 3 |  | [ELPR-007] optional
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 4 | 1 |  | [ELBO-015] to task lighting
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 3 |  | [ELBO-003] optional, location dependent on project requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | FQBS-171 | CHAIR: office, ergonomic | 4 | 1 |  | [FQBS-018]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 2 | 1 |  | [FQSM-007]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 3 |  | [ITIN-016] 2 x optional, to central monitor and labels printer if provided
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | 1 |  | [ITIN-036] location of outlets to meet local operational/WHS requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | ITNE-071 | TELEPHONE: handset, desktop | 4 | 1 |  | [ITNE-049]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 4 | 1 |  | [ITNE-007]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 3 |  | [FQGE-056] optional, dependent on service requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] under bench
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | JOBE-251 | CAP: cable access | 5 | 3 |  | [FIJO-099] 1 x optional, to central monitor if provided
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | JORS-021 | JOINERY UNIT: staff station | 1 | 1 |  | [FIJO-178] depth of bench and counter top to be confirmed based on service requirements and must consider ergonomics, staff safety and security, WHS requirements and Australian Standards
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | LIFX-108 | LIGHT: task, integral to joinery | 4 | 1 |  | [LIFX-008] under counter top
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] optional, location dependent on project requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 3 |  | [MGFP-001] optional, location dependent on project requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | MMPM-091 | MONITOR: central patient monitoring station, single display screen | 1 | 3 |  | [MMGE-187] optional, dependent on service requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | FFE | JORS-042 | WHITEBOARD: fixed, magnetic, integral to staff station | 1 | 1 |  | [FIBM-019] under counter top
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELGP-171 | GPO: single, UPS, joinery mounted | 1 | 1 |  | [ELGP-130] to printer, UPS to be provided if downtime computer required
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELGP-211 | GPO: double, joinery mounted | 4 | 1 |  | [ELGP-208] for BYO devices, to be located above desk for easy access, location of outlets to meet local operational/WHS requirements
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 5 | 1 |  | [ELGP-223] 1 x optional, to central monitor if provided
SSTN-20 | Staff Station, 20m2 | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | [ELGP-208]
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 2 | 1 | Wall Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | JORS-021 | JOINERY UNIT: staff station | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 3 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 3 | 1 |  | 1 to each workstation
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 3 | 1 |  | 1 to each workstation
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | JOBE-251 | CAP: cable access | 4 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-316 | PRINTER: labels, small, desktop | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQSM-061 | PEDESTAL: mobile, 660H nominal, 2 equal drawers and 1 file drawer | 2 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-302 | MULTIFUNCTION DEVICE: printer/copier/scanner/fax, floor standing | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | ambulance phone
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITSE-063 | BUTTON: security, duress, fixed, under bench mounted | 2 | 1 |  | 1 shared between 2 workstations/central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | LIFX-108 | LIGHT: task, integral to joinery | 4 | 1 |  | 1 to each workstation, 1 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to multi-function device
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITSE-111 | DISPLAY SCREEN: security, CCTV monitoring | 1 | 1 |  | type and size of screen to be confirmed to suit security requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional, for ambulance arrivals information; provision dependent on operational models and clinical services requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 3 |  | optional, for patient flow information; provision dependent on operational models and clinical services requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to ambulance arrivals display screen if provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to clock; an additional power outlet may be required if power over ethernet (PoE) is not supported by the clock hardware
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to multi-function device
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELSW-011 | SWITCH PLATE: light, multi-gang | 1 | 3 |  | optional, may be provided for control of general lighting in nearby treatment areas; provision dependent on overall department layout
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | to task lighting
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | JORS-071 | SECURITY GLAZING: to staff station | 3 | 1 |  | optional, provision and extent to be determined at project level based on risk assessment; may include communication slots and pass through apertures, with final configuration to be confirmed at project level to suit clinical services requirements and operational models
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | optional, to ambulance arrivals display screen if provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | optional, to patient flow display screen if provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | JORS-041 | WHITEBOARD: fixed, magnetic, integral to reception desk | 1 | 1
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FIHR-333 | BRACKET: display screen, single, fixed, ceiling mounted | 1 | 1 |  | to security CCTV display screen
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | MMPM-092 | MONITOR: central patient monitoring station, dual display screens | 1 | 1 |  | quantity and size of display screens to suit patient monitoring requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | optional, to patient flow display screen if provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to ambulance arrivals display screen if provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to patient flow display screen if provided
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted ambulance phone
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 6 | 1 |  | 2 to each workstation (except downtime workstation), 2 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-271 | GPO: double, UPS, joinery mounted | 2 | 1 |  | to downtime computer workstation; downtime requirements to be confirmed at project level
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-211 | GPO: double, joinery mounted | 3 | 1 |  | 1 to each workstation; over bench for portable device charging
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1 |  | to label printers
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | ITBU-470 | CLOCK: digital display, electric, synchronised slave, wired internet protocol (IP), wall mounted | 1 | 1 |  | type of clock and requirement for connection to the master clock system is to be confirmed at a project level based on clinical services requirements
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FIN | WLPR-006.03 | WALL PROTECTION: corner guards, to 1200 AFFL | 2 | 1 | Wall Protection | to be coordinated with adjacent wall protection
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 4 | 1 |  | 1 to each workstation, 1 to central patient monitoring station
SSTN-E | Staff Station - Emergency, Control Hub | Emergency | FFE | FQWS-213 | BIN: confidential document, secure, 50L | 1 | 1
STAD | Store - Accountable Drugs | Pharmacy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
STAD | Store - Accountable Drugs | Pharmacy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
STAD | Store - Accountable Drugs | Pharmacy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
STAD | Store - Accountable Drugs | Pharmacy | D+W | DOSP-101 | DOOR: hinged, 1 leaf, 900 clear opening, solid, strong room | 1 | 1 | Internal - Door 3 | [DWGE-003] outer door; access and door release controls to be determined based on security strategy
STAD | Store - Accountable Drugs | Pharmacy | D+W | DOSP-121 | DOOR: hinged, 1 leaf, 900 clear opening, mesh grille, strong room | 1 | 1 | Internal - Door 2 | [DWGE-002] inner door; access and door release controls to be determined based on security strategy
STAD | Store - Accountable Drugs | Pharmacy | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] extent of emergency power to be determined based on service requirements
STAD | Store - Accountable Drugs | Pharmacy | SER | ELGP-231.01 | GPO: double, emergency power, wall mounted, horizontal | 1 | 3 |  | [ELGP-223] optional, for refrigerator if provided
STAD | Store - Accountable Drugs | Pharmacy | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light
STAD | Store - Accountable Drugs | Pharmacy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STAD | Store - Accountable Drugs | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQDW-131.03 | WORKSTATION: straight, adjustable height, 720H nom, 600D x 1500W | 1 | 1 |  | [FQDW-051]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQSM-063 | PEDESTAL: mobile, 660H nominal, 3 equal drawers | 1 | 1 |  | [FQSM-007]
STAD | Store - Accountable Drugs | Pharmacy | FFE | FQSM-202 | SHELVING UNIT: mobile, adjustable shelves, 400D x 600W x 2100H nominal | 3 | 1 |  | [FQSM-048] type and quantity of storage options to be determined based on service requirements
STAD | Store - Accountable Drugs | Pharmacy | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, temperature monitoring, for refrigerator if provided
STAD | Store - Accountable Drugs | Pharmacy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] may be on wall or desk mounted bracket, an additional screen may be provided depending on project ICT requirements
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 1 |  | [ITNE-003]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-093]
STAD | Store - Accountable Drugs | Pharmacy | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 1 |  | [ITSE-012+FIHR-002]
STAD | Store - Accountable Drugs | Pharmacy | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
STAD | Store - Accountable Drugs | Pharmacy | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
STAD | Store - Accountable Drugs | Pharmacy | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008] under wall mounted joinery
STAD | Store - Accountable Drugs | Pharmacy | SER | MEGE-015 | PORT: ventilation, secure room | 2 | 1 |  | [MEGE-015]
STAD | Store - Accountable Drugs | Pharmacy | FFE | MMPH-024 | FRIDGE: medication/vaccine, 1000L nom, double door | 1 | 3 |  | [MMGE-034] optional
STAD | Store - Accountable Drugs | Pharmacy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STAD | Store - Accountable Drugs | Pharmacy | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023] extent dependent on type and height storage solution
STAD | Store - Accountable Drugs | Pharmacy | SER | ITSE-216 | SENSOR: security, vibration detection, for alarm, wall mounted | 1 | 1 |  | [ITSE-003]
STAD | Store - Accountable Drugs | Pharmacy | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2 | [ITSE-038]
STBK | Store - Bulk | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STBK | Store - Bulk | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STBK | Store - Bulk | Logistics / Support Services | D+W | DOHI-214.01 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-062] lockable or secure staff access, hold open hardware may be required
STBK | Store - Bulk | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208]
STBK | Store - Bulk | Logistics / Support Services | SER | ELGP-231.01 | GPO: double, emergency power, wall mounted, horizontal | 1 | 3 |  | [ELGP-223] optional, to refrigerator if provided
STBK | Store - Bulk | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
STBK | Store - Bulk | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STBK | Store - Bulk | Logistics / Support Services | FFE | FQCA-424 | FRIDGE: commercial, 1000L nom, double door | 1 | 3 |  | [FQCA-026] optional
STBK | Store - Bulk | Logistics / Support Services | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 2 | 1 |  | [FQSN-086] type and extent of storage solutions will be dependent on service requirements
STBK | Store - Bulk | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, to refrigerator if provided and temperature monitoring is required
STBK | Store - Bulk | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
STBK | Store - Bulk | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
STBK | Store - Bulk | Logistics / Support Services | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020] height dependent on movement of trolleys and pallets, crash rails are also acceptable
STBK | Store - Bulk | Logistics / Support Services | D+W | AFDPR-007.01 | DOOR PROTECTION: plate, heavy duty, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STBK | Store - Bulk | Logistics / Support Services | D+W | AFDPR-007.01 | DOOR PROTECTION: plate, heavy duty, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STBK | Store - Bulk | Logistics / Support Services | D+W | AFDPR-057.04 | DOOR FRAME PROTECTION: full wrap, heavy duty, to 1500H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STBK | Store - Bulk | Logistics / Support Services | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
STBK | Store - Bulk | Logistics / Support Services | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 3 | 1 |  | [FQSM-032]
STCL | Store - Cleaner | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STCL | Store - Cleaner | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STCL | Store - Cleaner | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
STCL | Store - Cleaner | Logistics / Support Services | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029] type and extent of storage solutions will be dependent on service requirements
STCL | Store - Cleaner | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
STCL | Store - Cleaner | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STCL | Store - Cleaner | Logistics / Support Services | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 3 | 1 |  | [FQSN-086] type and extent of storage solutions will be dependent on service requirements
STCL | Store - Cleaner | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
STCL | Store - Cleaner | Logistics / Support Services | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020] height dependent on movement of trolleys and pallets, crash rails are also acceptable
STCL | Store - Cleaner | Logistics / Support Services | D+W | AFDPR-007.01 | DOOR PROTECTION: plate, heavy duty, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STCL | Store - Cleaner | Logistics / Support Services | D+W | AFDPR-007.01 | DOOR PROTECTION: plate, heavy duty, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STCL | Store - Cleaner | Logistics / Support Services | D+W | AFDPR-057.04 | DOOR FRAME PROTECTION: full wrap, heavy duty, to 1500H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STCL | Store - Cleaner | Logistics / Support Services | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
STCL | Store - Cleaner | Logistics / Support Services | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021] lockable or secure staff access; hold open hardware may be required; vision panel may be provided
STCL | Store - Cleaner | Logistics / Support Services | FFE | FQSN-258 | CABINET: floor standing, 2100H nominal, single door | 1 | 1 |  | [FQSN-012] lockable
STCL | Store - Cleaner | Logistics / Support Services | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 4 | 3 |  | [FIHR-030] optional, provision dependent on service requirements, to be rated for minimum 10kg per hook if provided
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FIRT-231 | RAIL: equipment charging, vertical, wall mounted | 2 | 3 |  | [FIRT-012] optional, provision dependent on service requirements
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 3 | 1 |  | [FQSN-082] adjustable shelving; type and quantity of storage options to be determined based on service requirements
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-020] height dependent on type and height of mobile equipment, crash rails are also acceptable
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STEQ-14 | Store - Equipment, 14m2 | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 13 | 1 |  | [ELGP-208] type, quantity and configuration of outlets dependent on operational and equipment requirements
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 4 | 3 |  | [FIHR-030] optional, provision dependent on service requirements, to be rated for minimum 10kg per hook if provided
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FFE | FIRT-231 | RAIL: equipment charging, vertical, wall mounted | 3 | 3 |  | [FIRT-012] optional, provision dependent on service requirements
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 3 | 1 |  | [FQSN-082] adjustable shelving; type and quantity of storage options to be determined based on service requirements
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-020] height dependent on type and height of mobile equipment, crash rails are also acceptable
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 16 | 1 |  | [ELGP-208] type, quantity and configuration of outlets dependent on operational and equipment requirements
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STEQ-20 | Store - Equipment, 20m2 | Clinical Support Set 1 | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
STFS-10 | Store - Files, 10m2 | Administration | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to both sides
STFS-10 | Store - Files, 10m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STFS-10 | Store - Files, 10m2 | Administration | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STFS-10 | Store - Files, 10m2 | Administration | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] lockable
STFS-10 | Store - Files, 10m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] motion sensor light activation is also acceptable
STFS-10 | Store - Files, 10m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
STFS-10 | Store - Files, 10m2 | Administration | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STFS-10 | Store - Files, 10m2 | Administration | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STFS-10 | Store - Files, 10m2 | Administration | FFE | FQGE-162 | STOOL: step, safety | 1 | 1 |  | [FQGE-095]
STFS-10 | Store - Files, 10m2 | Administration | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 9 | 1 |  | [FQSN-085] type, size and quantity of shelving / storage solution to be confirmed to suit service requirements
STFS-10 | Store - Files, 10m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STFS-10 | Store - Files, 10m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
STFS-10 | Store - Files, 10m2 | Administration | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
STFS-20 | Store - Files, 20m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
STFS-20 | Store - Files, 20m2 | Administration | FFE | FQGE-162 | STOOL: step, safety | 1 | 1 |  | [FQGE-095]
STFS-20 | Store - Files, 20m2 | Administration | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to both sides
STFS-20 | Store - Files, 20m2 | Administration | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
STFS-20 | Store - Files, 20m2 | Administration | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] lockable
STFS-20 | Store - Files, 20m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STFS-20 | Store - Files, 20m2 | Administration | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STFS-20 | Store - Files, 20m2 | Administration | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STFS-20 | Store - Files, 20m2 | Administration | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STFS-20 | Store - Files, 20m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STFS-20 | Store - Files, 20m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
STFS-20 | Store - Files, 20m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] motion sensor light activation is also acceptable
STFS-20 | Store - Files, 20m2 | Administration | FFE | FQSN-142 | COMPACTUS: floor mounted | 1 | 1 |  | [FQSN-063] 5 bays; static shelving is also acceptable
STFS-20 | Store - Files, 20m2 | Administration | FFE | FQSN-142 | COMPACTUS: floor mounted | 1 | 1 |  | [FQSN-063] 2 bays; static shelving is also acceptable
STGN | Store - General | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STGN | Store - General | Clinical Support Set 1 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
STGN | Store - General | Clinical Support Set 1 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
STGN | Store - General | Clinical Support Set 1 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
STGN | Store - General | Clinical Support Set 1 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208]
STGN | Store - General | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
STGN | Store - General | Clinical Support Set 1 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
STGN | Store - General | Clinical Support Set 1 | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 3 | 3 |  | [FIHR-033] optional
STGN | Store - General | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
STGN | Store - General | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
STGN | Store - General | Clinical Support Set 1 | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 15 | 3 |  | [FQSN-007] optional
STGN | Store - General | Clinical Support Set 1 | FFE | FQSN-204 | SHELVING UNIT: floor standing, adjustable shelves, 400D x 900W x 2100H nominal | 6 | 1 |  | [FQSN-082] adjustable shelving; type and quantity of storage options to be determined based on service requirements
STGN | Store - General | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
STGN | Store - General | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STPP | Store - Patient Property | Mental Health | FFE | FQSN-214 | SHELVING UNIT: floor standing, adjustable shelves, 600D x 900W x 2100H nominal | 5 | 1 |  | type, extent and configuration of storage to suit service requirements and operational policies for method of property separation and volume of property to be stored per person
STPP | Store - Patient Property | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
STPP | Store - Patient Property | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
STPP | Store - Patient Property | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STPP | Store - Patient Property | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STPP | Store - Patient Property | Mental Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1
STPP | Store - Patient Property | Mental Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
STPP | Store - Patient Property | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
STPP | Store - Patient Property | Mental Health | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
STPP | Store - Patient Property | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
STPP | Store - Patient Property | Mental Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting
STPP | Store - Patient Property | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
STPP | Store - Patient Property | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STRT | Stress Testing | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
STRT | Stress Testing | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
STRT | Stress Testing | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
STRT | Stress Testing | Cardiac Investigations | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-003] optional, to change room if provided
STRT | Stress Testing | Cardiac Investigations | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
STRT | Stress Testing | Cardiac Investigations | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | [ELGP-122]
STRT | Stress Testing | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006]
STRT | Stress Testing | Cardiac Investigations | SER | ELSW-001 | SWITCH: light | 2 | 3 |  | [ELBO-015] optional, to optional change room
STRT | Stress Testing | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
STRT | Stress Testing | Cardiac Investigations | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
STRT | Stress Testing | Cardiac Investigations | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-025]
STRT | Stress Testing | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
STRT | Stress Testing | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
STRT | Stress Testing | Cardiac Investigations | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-028]
STRT | Stress Testing | Cardiac Investigations | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
STRT | Stress Testing | Cardiac Investigations | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 2 | 1 |  | [FQBS-052]
STRT | Stress Testing | Cardiac Investigations | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
STRT | Stress Testing | Cardiac Investigations | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010] to entry door
STRT | Stress Testing | Cardiac Investigations | FFE | FQSM-056 | PEDESTAL: mobile, 840H nominal, 3 equal wire basket drawers | 2 | 1 |  | [FQSM-003]
STRT | Stress Testing | Cardiac Investigations | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
STRT | Stress Testing | Cardiac Investigations | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
STRT | Stress Testing | Cardiac Investigations | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010] refer to BHWS-B (similar)
STRT | Stress Testing | Cardiac Investigations | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
STRT | Stress Testing | Cardiac Investigations | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
STRT | Stress Testing | Cardiac Investigations | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel, + indicator button & light
STRT | Stress Testing | Cardiac Investigations | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
STRT | Stress Testing | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 5 | 1 |  | [ITIN-026] 1 outlet for telephone
STRT | Stress Testing | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
STRT | Stress Testing | Cardiac Investigations | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-071]
STRT | Stress Testing | Cardiac Investigations | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
STRT | Stress Testing | Cardiac Investigations | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-131]
STRT | Stress Testing | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
STRT | Stress Testing | Cardiac Investigations | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
STRT | Stress Testing | Cardiac Investigations | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | [MGAS-022] optional
STRT | Stress Testing | Cardiac Investigations | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
STRT | Stress Testing | Cardiac Investigations | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
STRT | Stress Testing | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 3 | Panel 1 | [MGFP-002] optional
STRT | Stress Testing | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
STRT | Stress Testing | Cardiac Investigations | FFE | MIUS-051 | IMAGING DEVICE: echocardiography | 1 | 1 |  | [MMMI-325]
STRT | Stress Testing | Cardiac Investigations | FFE | MMAH-071 | EXERCISE MACHINE: treadmill | 1 | 1 |  | [MMAH-027]
STRT | Stress Testing | Cardiac Investigations | FFE | MMBE-157 | TROLLEY: patient, examination, echocardiography | 1 | 1 |  | [MMBE-069]
STRT | Stress Testing | Cardiac Investigations | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
STRT | Stress Testing | Cardiac Investigations | FFE | MMGE-337 | DEVICE: electrocardiography (ECG), with trolley | 1 | 1 |  | [MMGE-179]
STRT | Stress Testing | Cardiac Investigations | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002]
STRT | Stress Testing | Cardiac Investigations | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1 |  | [MMHA-027]
STRT | Stress Testing | Cardiac Investigations | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 3 |  | [MMGE-088] optional, for pharmacological stress testing
STRT | Stress Testing | Cardiac Investigations | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
STRT | Stress Testing | Cardiac Investigations | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
STRT | Stress Testing | Cardiac Investigations | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-025]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208]
STRT | Stress Testing | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | [ELGP-223]
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-005] to change room side
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
STRT | Stress Testing | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
STRT | Stress Testing | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
STRT | Stress Testing | Cardiac Investigations | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
STSS | Store - Sterile Stock | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to computer workstation
STSS | Store - Sterile Stock | Operating | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to area for workstation on wheels
STSS | Store - Sterile Stock | Operating | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 1 | 1 |  | controlled from operating room
STSS | Store - Sterile Stock | Operating | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | controlled from operating room
STSS | Store - Sterile Stock | Operating | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to area for workstation on wheels
STSS | Store - Sterile Stock | Operating | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
STSS | Store - Sterile Stock | Operating | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | to general room lighting, controlled from 3 entry points
STSS | Store - Sterile Stock | Operating | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
STSS | Store - Sterile Stock | Operating | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
STSS | Store - Sterile Stock | Operating | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
STSS | Store - Sterile Stock | Operating | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
STSS | Store - Sterile Stock | Operating | FIN | WLFI-003 | WALL FINISH: paint, sterile areas | 1 | 1 | Wall Finish 1
STSS | Store - Sterile Stock | Operating | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 1
STSS | Store - Sterile Stock | Operating | D+W | DOHI-114.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel, with integral blind | 1 | 1 | Internal - Door 1 | to corridor, large leaf to open 170 degrees
STSS | Store - Sterile Stock | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to room side
STSS | Store - Sterile Stock | Operating | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | to operating room
STSS | Store - Sterile Stock | Operating | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 2 | to both sides
STSS | Store - Sterile Stock | Operating | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1
STSS | Store - Sterile Stock | Operating | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 3 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | FFE | FQSN-141 | COMPACTUS: rail mounted | 1 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | FFE | FQSM-211 | SHELVING UNIT: mobile, adjustable shelves, 600D x 400W x 2100H nominal | 7 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | ITNE-223 | INPUT DEVICE: bar code scanner, medical grade, washable | 2 | 1 |  | 1 for data for tray tracking, 1 for H tracking
STSS | Store - Sterile Stock | Operating | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | optional, to bench or wall mounted
STSS | Store - Sterile Stock | Operating | FFE | MMIC-491 | TROLLEY: transfer, instruments, clean | 1 | 1
STSS | Store - Sterile Stock | Operating | FFE | FQSM-205 | SHELVING UNIT: mobile, adjustable shelves, 400D x 1200W x 2100H nominal | 1 | 1 |  | type and configuration of storage solutions to suit project requirements
STSS | Store - Sterile Stock | Operating | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
STSS | Store - Sterile Stock | Operating | FFE | MMTR-104 | TROLLEY: set-up, 900W x 490D x 900H nom | 4 | 1
STSS | Store - Sterile Stock | Operating | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side, to be coordinated with corridor wall protection
STSS | Store - Sterile Stock | Operating | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 2
STSS | Store - Sterile Stock | Operating | D+W | AHDMO-002 | DOOR MOTORISATION: hinged, 2 leaf | 1 | 1 | Internal - Door 2
TRBNL | Tribunal Hearing Room | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 10 | 1 | Floor Skirting
TRBNL | Tribunal Hearing Room | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
TRBNL | Tribunal Hearing Room | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRBNL | Tribunal Hearing Room | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side as required
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRBNL | Tribunal Hearing Room | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 2
TRBNL | Tribunal Hearing Room | Mental Health | D+W | WIFX-056.04 | WINDOW: fixed, internal, double glazed, sill at 750H, with integral blind | 1 | 1 | Internal - Window 1 | to observation area as required
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-226 | GPO: double, in floor box | 2 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to each door
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | optional; to room booking system if provided
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 1 | 1 |  | integral to 1 folding table as required
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FQBS-142 | CHAIR: meeting room, stackable | 12 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FQTA-125.04 | TABLE: rectangular, 750H, 1500L x 750W, folding, on casters | 4 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-103 | CONTROL PANEL: AV system, joinery mounted | 1 | 1 |  | may alternatively be provided as a wall mounted or portable item
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-134 | CAMERA: AV system, video conferencing, surface mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-147 | MICROPHONE: AV system, portable | 1 | 1 |  | may alternatively be provided as ceiling recessed item
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | optional
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 2 | 1 |  | lockable
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-201 | CUPBOARD: under bench, single door | 2 | 1 |  | lockable
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-125 | CUPBOARD: wall mounted, double door, for audio-visual equipment | 1 | 1 |  | lockable; with ventilation as required to suit AV equipment
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOCU-225 | CUPBOARD: under bench, double door, for audio-visual equipment | 1 | 1 |  | lockable; with ventilation as required to suit AV equipment
TRBNL | Tribunal Hearing Room | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
TRBNL | Tribunal Hearing Room | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to room side
TRBNL | Tribunal Hearing Room | Mental Health | FFE | FIHR-332 | BRACKET: display screen, single, fixed, joinery mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | to suit security and egress requirements
TRBNL | Tribunal Hearing Room | Mental Health | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 1 | 1
TRBNL | Tribunal Hearing Room | Mental Health | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 1 | 1 |  | to AV display screen and CPU
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to AV display screen and CPU
TRBNL | Tribunal Hearing Room | Mental Health | SER | ELGP-211 | GPO: double, joinery mounted | 2 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | provision of adjustable desk mounted brackets for computer screens may be considered at project level
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JORS-001 | JOINERY UNIT: reception desk | 1 | 1 |  | counters may be provided as standing height or seated height, or a mix of both; at least one counter to provide wheelchair access as per AS1428.1 / NZS 4121; joinery configuration may include privacy dividers between triage counters to support acoustic privacy with sensitive conversations, and materiality to be confirmed to balance privacy requirements with waiting room observation
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLBK-012 | BULKHEAD: flush set, acoustic | 1 | 1 | Ceiling Finish 2
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | FQSM-081 | PEDESTAL: mobile, 660H nominal, 1 drawer and 1 printer shelf | 1 | 1
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | on pedestal under bench
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITIN-038 | OUTLET: data, triple RJ45, surface mounted | 1 | 1 |  | to computer workstation
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 1 | 1 |  | to printers
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JOBE-251 | CAP: cable access | 2 | 1 |  | 1 to computer workstation; 1 to label printer
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ELGP-241 | GPO: double, emergency power, joinery mounted | 2 | 1 |  | to computer workstation
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITIN-028 | OUTLET: data, double RJ45, surface mounted | 1 | 1 |  | to printers
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | to main entry for emergency unit treatment areas
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | located discreetly
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JORS-053 | SECURITY GLAZING: to reception, with communication slot and pass through aperture | 1 | 1 |  | configuration of communication slot and pass through aperture to be confirmed at project level to suit clinical services requirements and operational models
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 3 | to bulkhead
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FFE | JORS-051 | SECURITY GLAZING: to reception | 2 | 1 |  | between triage counters to support acoustic privacy with sensitive conversations, and materiality to be confirmed to balance privacy requirements with waiting room observation
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | WLPR-006.03 | WALL PROTECTION: corner guards, to 1200 AFFL | 4 | 1 | Wall Protection
TRIAGE-CO | Triage - Emergency, Assessment Counter | Emergency | FIN | WLPT-031 | SCREEN: privacy divider | 2 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | to waiting area; extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with cable and accessory management items as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 1 |  | write-up function may be provided by a wall mounted computer workstation, a desk/bench with computer, or a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT strategies and policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | write-up function may be provided by a wall mounted computer workstation, a desk/bench with computer, or a wirelessly connected workstation on wheels (WOW). Final configuration is dependent on clinical service requirements, operational models for medical records and local ICT strategies and policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | collocated with alcohol-based hand rub
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | 1 to door from waiting area, 1 to back of room where unit treatment areas are accessed
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | selected item to be able to lay flat
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to wall mounted computer
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMTR-062 | TROLLEY: dressing, 600W x 490D x 900H nom | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of patient monitoring to be confirmed to suit clinical services requirements; with accessories (sensors, cuffs, cables, etc.) as required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to window facing waiting area; provision of integral blinds in lieu of a privacy curtain may be considered at project level to suit local IPC policies and requirements for observation and patient privac
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for waiting room observation; provision of integral blinds or provision of privacy curtain track is to be determined to suit requirements for waiting room observation and patient privacy
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1 |  | to wall mounted computer
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to wall mounted computer
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry from treatment areas; location to ensure visibility along paths of travel
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for patient recliner
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | optional; provision dependent on clinical service requirements; light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 3 | Panel 1 | optional, to ceiling recessed examination light if provided; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 3 | 1 |  | 1 to door from waiting area, 1 to back of room where unit treatment areas are accessed
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to window facing waiting area; provision of integral blinds in lieu of a privacy curtain may be considered at project level to suit local IPC policies and requirements for observation and patient privacy
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | with removable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 6 | 1 | Wall Finish 2
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 3 | to basin
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | FIN | WLPR-006.06 | WALL PROTECTION: corner guards, to 2100 AFFL | 3 | 1 | Wall Finish 4
TRIAGE-RM | Triage - Emergency, Assessment Room | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to waiting area side
TRMT | Treatment Room | Ambulatory Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
TRMT | Treatment Room | Ambulatory Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
TRMT | Treatment Room | Ambulatory Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] low level, for patient trolley
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-106.01 | GPO: single, ceiling mounted, horizontal | 1 | 1 |  | [ELGP-101] to exam light
TRMT | Treatment Room | Ambulatory Care | MSP | ELGP-116 | GPO: single, on services panel | 3 | 1 | Panel 1 | [ELGP-105]
TRMT | Treatment Room | Ambulatory Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1 | [ELGP-122]
TRMT | Treatment Room | Ambulatory Care | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
TRMT | Treatment Room | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
TRMT | Treatment Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light, 1 x examination light
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
TRMT | Treatment Room | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
TRMT | Treatment Room | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
TRMT | Treatment Room | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
TRMT | Treatment Room | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
TRMT | Treatment Room | Ambulatory Care | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1 |  | [FQBS-052]
TRMT | Treatment Room | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
TRMT | Treatment Room | Ambulatory Care | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
TRMT | Treatment Room | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
TRMT | Treatment Room | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 3 |  | [FQCW-008] optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT | Treatment Room | Ambulatory Care | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
TRMT | Treatment Room | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
TRMT | Treatment Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] indicator button and light
TRMT | Treatment Room | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] on services panel, call button on the handset
TRMT | Treatment Room | Ambulatory Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
TRMT | Treatment Room | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
TRMT | Treatment Room | Ambulatory Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
TRMT | Treatment Room | Ambulatory Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
TRMT | Treatment Room | Ambulatory Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
TRMT | Treatment Room | Ambulatory Care | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
TRMT | Treatment Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
TRMT | Treatment Room | Ambulatory Care | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
TRMT | Treatment Room | Ambulatory Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
TRMT | Treatment Room | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
TRMT | Treatment Room | Ambulatory Care | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
TRMT | Treatment Room | Ambulatory Care | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008] under wall mounted joinery
TRMT | Treatment Room | Ambulatory Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
TRMT | Treatment Room | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
TRMT | Treatment Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
TRMT | Treatment Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
TRMT | Treatment Room | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
TRMT | Treatment Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
TRMT | Treatment Room | Ambulatory Care | FFE | MGFP-061 | ADAPTER: suction | 1 | 1 |  | [MMGE-002]
TRMT | Treatment Room | Ambulatory Care | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | [MMBE-043]
TRMT | Treatment Room | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
TRMT | Treatment Room | Ambulatory Care | FFE | MMGE-233 | DIAGNOSTIC SET: otoscope and ophthalmoscope, wall mounted | 1 | 3 |  | [MMGE-031] optional, may be portable/mobile on stand
TRMT | Treatment Room | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
TRMT | Treatment Room | Ambulatory Care | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
TRMT | Treatment Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
TRMT | Treatment Room | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 5 | 1 | Wall Finish 2 | [WLWA-020]
TRMT | Treatment Room | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
TRMT | Treatment Room | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
TRMT | Treatment Room | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
TRMT | Treatment Room | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
TRMT | Treatment Room | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
TRMT | Treatment Room | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
TRMT | Treatment Room | Ambulatory Care | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] indicator button and light
TRMT | Treatment Room | Ambulatory Care | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] indicator button and light
TRMT | Treatment Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
TRMT | Treatment Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
TRMT | Treatment Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
TRMT | Treatment Room | Ambulatory Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | DWGL-033]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 3 | 1 | Internal - Door 1 | [DWPR-005] to room side
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-005] optional, second door for egress
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 2 x examination lights
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIDI-077 | DISPENSER: velcro roll, wall mounted | 1 | 1 |  | [FIDI-053]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 2 | 1 |  | [FIHR-067] to therapy tables, dependent on ICT strategy
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting | [FLSK-010]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 6 | 1 |  | [FQBS-030]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FQDW-131.02 | WORKSTATION: straight, adjustable height, 720H nom, 600D x 1200W | 2 | 1 |  | [FQDW-049]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FQGE-101 | CURTAIN: privacy screen | 3 | 1 |  | [FQGE-010]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FQGE-251 | DEVICE: sewing machine, domestic | 1 | 1 |  | [FQGE-043]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FQWS-235 | BIN: clinical waste, 80L | 1 | 1 |  | [FQCW-010] type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | HYBA-303 | SINK: single bowl, with drainer | 1 | 1 |  | [HYBA-069]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | HYDR-151 | TRAP: plaster | 1 | 3 |  | [HYDR-008] optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | ITNE-121 | COMPUTER: single display screen, all-in-one | 2 | 1 |  | [ITNE-066] to therapy tables, dependent on ICT strategy
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | [ITSE-006]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 3 | 1 |  | [FIJO-059]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-116]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | JOCU-201 | CUPBOARD: under bench, single door | 2 | 1 |  | [FIJO-140]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-135]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 1 | 1 |  | [FIJO-104] for thermaplastic storage, width to be confirmed to suit size of material
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 4 | 1 |  | [FIJO-152]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | LIFX-114 | LIGHT: examination, single articulated arm, 1 light head, wall mounted | 2 | 1 |  | [LIFX-026] to therapy tables, ceiling mounted is also acceptable
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | MMAH-012 | DEVICE: continuous passive motion (CPM), upper limb | 1 | 3 |  | [MMAH-012] optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | MMAH-261 | TABLE: hand therapy, adjustable height | 2 | 1 |  | [FQTA-084]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | MMAH-271 | DEVICE: hand therapy, pan, splint moulding, water bath | 1 | 1 |  | [MMAH-021]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | MMGE-151 | LIGHT BOX: x-ray viewer, wall mounted | 1 | 3 |  | [MMGE-150] optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | MMLA-014 | DEVICE: wax bath | 1 | 3 |  | [MMLA-014] optional
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-010] to bench
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 3 | [WLWA-007] to basin
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | FFE | FIRT-051 | TRACK: curtain, privacy | 2 | 1 |  | [FIRT-047]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 9 | 1 |  | [ELGP-208] extent of emergency power to be determined based on service requirements
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109]
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | [ELGP-109] optional, to x-ray viewing box
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
TRMT-HTS | Treatment Room - Hand Therapy / Splinting | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
TRMT-POD | Treatment Room - Podiatry | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
TRMT-POD | Treatment Room - Podiatry | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
TRMT-POD | Treatment Room - Podiatry | Allied Health | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
TRMT-POD | Treatment Room - Podiatry | Allied Health | MSP | ELGP-216 | GPO: double, on services panel | 2 | 1 | Panel 1 | [ELGP-205] extent of emergency power to be determined based on service requirements
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light, 1 x examination light
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIDI-151 | DISPENSER: PPE, combination, large, wall mounted | 1 | 1 |  | [FIDI-054]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1 |  | [FQBS-028]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 3 |  | [FQCW-008] optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
TRMT-POD | Treatment Room - Podiatry | Allied Health | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] computer may alternatively be on benchtop or wall mounted
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-117]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | LIFX-121 | LIGHT: procedure, minor, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-013]
TRMT-POD | Treatment Room - Podiatry | Allied Health | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
TRMT-POD | Treatment Room - Podiatry | Allied Health | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
TRMT-POD | Treatment Room - Podiatry | Allied Health | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
TRMT-POD | Treatment Room - Podiatry | Allied Health | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | [MMGE-139]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 2 | [WLWA-020]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 3 | [WLWA-007]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047]
TRMT-POD | Treatment Room - Podiatry | Allied Health | FFE | MMBE-176 | CHAIR: patient, examination, electric | 1 | 1 |  | [MMAH-010]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] extent of emergency power to be determined based on service requirements
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
TRMT-POD | Treatment Room - Podiatry | Allied Health | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101]
TRMT-POD | Treatment Room - Podiatry | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
TRMT-POD | Treatment Room - Podiatry | Allied Health | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
ULTR | Ultrasound Room | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-002] drop-in ceiling tiles are also acceptable
ULTR | Ultrasound Room | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ULTR | Ultrasound Room | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
ULTR | Ultrasound Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
ULTR | Ultrasound Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ULTR | Ultrasound Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ULTR | Ultrasound Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2
ULTR | Ultrasound Room | Medical Imaging | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Finish 3
ULTR | Ultrasound Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
ULTR | Ultrasound Room | Medical Imaging | FFE | FIHR-333 | BRACKET: display screen, single, fixed, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR | Ultrasound Room | Medical Imaging | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
ULTR | Ultrasound Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
ULTR | Ultrasound Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ULTR | Ultrasound Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ULTR | Ultrasound Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for examination trolley
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to workstation
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR | Ultrasound Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies
ULTR | Ultrasound Room | Medical Imaging | SER | ELSW-022 | SWITCH: light, dimmer, 2-gang | 1 | 1 |  | to general room lighting and indirect lighting
ULTR | Ultrasound Room | Medical Imaging | SER | ITIN-061 | OUTLET: data, HDMI, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR | Ultrasound Room | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to workstation
ULTR | Ultrasound Room | Medical Imaging | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1
ULTR | Ultrasound Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
ULTR | Ultrasound Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 8 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | ITIN-065 | OUTLET: data, HDMI, on services panel | 2 | 1 | Panel 1 | for connecting ultrasound machine to slave display screen on ceiling, type of AV outlet to be confirmed to suit equipment requirements
ULTR | Ultrasound Room | Medical Imaging | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
ULTR | Ultrasound Room | Medical Imaging | FFE | ITCL-362 | DISPLAY SCREEN: medical equipment, slave | 1 | 1 |  | for viewing ultrasound imaging by patient, may also be wall mounted
ULTR | Ultrasound Room | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
ULTR | Ultrasound Room | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
ULTR | Ultrasound Room | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
ULTR | Ultrasound Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MIUS-021 | DEVICE: warmer, ultrasound gel, benchtop | 1 | 1 |  | may be integral to ultrasound machine
ULTR | Ultrasound Room | Medical Imaging | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
ULTR | Ultrasound Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MIUS-011 | RACK: ultrasound probes, wall mounted | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | selection to suit service requirements, may require cut out section for cardiac scans
ULTR | Ultrasound Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQDW-164.02 | WORKSTATION: straight, adjustable height, electric, 720H nom, 750D x 1200W | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | optional - for patient access to examination trolley, provision dependent on adjustable height range of trolley
ULTR | Ultrasound Room | Medical Imaging | FFE | MMTR-001.02 | TROLLEY: stainless steel, 490W x 490D x 900H nom, 2 tier | 1 | 1
ULTR | Ultrasound Room | Medical Imaging | FFE | MIUS-036 | ERGONOMIC AID: ultrasound, arm/wrist support sling, on articulated arm, ceiling mounted | 1 | 1 |  | optional
ULTR | Ultrasound Room | Medical Imaging | FFE | MMBE-354 | HANDLE: fixed arm, patient self-assist transfer and positioning aid, bed/trolley mounted | 1 | 1 |  | optional
ULTR | Ultrasound Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Finish 3
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 8 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITIN-065 | OUTLET: data, HDMI, on services panel | 2 | 1 | Panel 1 | for connecting ultrasound machine to slave display screen on ceiling, type of AV outlet to be confirmed to suit equipment requirements
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for examination trolley
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | to workstation
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELSW-022 | SWITCH: light, dimmer, 2-gang | 1 | 1 |  | to general room lighting and indirect lighting
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITIN-061 | OUTLET: data, HDMI, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to workstation
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | type, size and quantity of bins to be determined based on service requirements and waste management policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-333 | BRACKET: display screen, single, fixed, ceiling mounted | 1 | 1 |  | to slave display screen
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | ITCL-362 | DISPLAY SCREEN: medical equipment, slave | 1 | 1 |  | for viewing ultrasound imaging by clinicians for procedures, may also be wall mounted
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MIUS-021 | DEVICE: warmer, ultrasound gel, benchtop | 1 | 1 |  | may be integral to ultrasound machine
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | optional - for patient property, 1 mounted at 1200H if provided
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MIUS-011 | RACK: ultrasound probes, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | selection to suit service requirements, may require cut out section for cardiac scans
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQDW-164.02 | WORKSTATION: straight, adjustable height, electric, 720H nom, 750D x 1200W | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQGE-161 | STOOL: step | 1 | 1 |  | optional - for patient access to examination trolley, provision dependent on adjustable height range of trolley
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MIUS-036 | ERGONOMIC AID: ultrasound, arm/wrist support sling, on articulated arm, ceiling mounted | 1 | 1 |  | optional
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMBE-354 | HANDLE: fixed arm, patient self-assist transfer and positioning aid, bed/trolley mounted | 1 | 1 |  | optional
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional - provided if reticulated nitrous oxide provided, provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to pathology area for microscope
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | FIHR-115 | BRACKET: sharps bin, trolley mounted | 1 | 1
ULTR-PR | Ultrasound Room - Procedures | Medical Imaging | FFE | MMTR-002.07 | TROLLEY: stainless steel, 600W x 490D x 900H nom, 5 drawer | 1 | 1
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
UTRM | Uptake Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-005] automated, hold open
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1 | [ELGP-122]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | [ELBO-012] inside and outside room, to be reviewed to suit operational requirements
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 1 | 1 |  | [ITCL-012 + FIHR-077]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] handsfree to control room
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | MIGE-076 | ACCESS PANEL: penetration, uptake room, pass-through for radioisotope injector | 1 | 3 | Wall Finish 2 | [MMMI-219] optional
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
UTRM | Uptake Room | Nuclear Medicine / PET | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 5 | 1 | Wall Finish 1 | [WLWA-020]
UTRM | Uptake Room | Nuclear Medicine / PET | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | [MMBE-091] consider bariatric capacity as required
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
UTRM | Uptake Room | Nuclear Medicine / PET | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
UTRM | Uptake Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
UTRM | Uptake Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109]
UTRM | Uptake Room | Nuclear Medicine / PET | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101]
WAIT-10 | Waiting, 10m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WAIT-10 | Waiting, 10m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001] quantity and location to suit local IPC policies
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FIHR-046 | RACK: magazine/pamphlet, wall mounted | 1 | 3 |  | [FIHR-045] optional
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
WAIT-10 | Waiting, 10m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FQBS-102 | CHAIR: visitor, clinical areas, bariatric | 1 | 1 |  | [FQBS-027] quantity to be confirmed at project level depending on service requirements
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FQBS-116 | CHAIR: visitor, waiting areas | 6 | 1 |  | [FQBS-032]
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 3 |  | [FQGE-002] optional
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FQTA-201 | TABLE: square, 450H, 500L | 1 | 1 |  | [FQTA-071]
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WAIT-10 | Waiting, 10m2 | Public Areas | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITBU-011]
WAIT-10 | Waiting, 10m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
WAIT-10 | Waiting, 10m2 | Public Areas | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022] as required to suit loose furniture layout; crash rails are also acceptable
WAIT-10 | Waiting, 10m2 | Public Areas | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] height to be coordinated with adjacent wall protection
WAIT-10 | Waiting, 10m2 | Public Areas | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to display screen
WAIT-10 | Waiting, 10m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
WAIT-10 | Waiting, 10m2 | Public Areas | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | [ITIN-070] may be replaced with data outlet in accordance with local ICT policy
WAIT-10 | Waiting, 10m2 | Public Areas | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
WAIT-10 | Waiting, 10m2 | Public Areas | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook is desirable
WAIT-10 | Waiting, 10m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-003] carpet tiles are also acceptable
WAIT-20 | Waiting, 20m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WAIT-20 | Waiting, 20m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
WAIT-20 | Waiting, 20m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
WAIT-20 | Waiting, 20m2 | Public Areas | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] height to be coordinated with adjacent wall protection
WAIT-20 | Waiting, 20m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
WAIT-20 | Waiting, 20m2 | Public Areas | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022] as required to suit loose furniture layout; crash rails are also acceptable
WAIT-20 | Waiting, 20m2 | Public Areas | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to display screen
WAIT-20 | Waiting, 20m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
WAIT-20 | Waiting, 20m2 | Public Areas | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | [ITIN-070] may be replaced with data outlet in accordance with local ICT policy
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FIHR-046 | RACK: magazine/pamphlet, wall mounted | 1 | 3 |  | [FIHR-045] optional
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 3 |  | [FQGE-002] optional
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001] quantity and location to suit local IPC policies
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FQBS-102 | CHAIR: visitor, clinical areas, bariatric | 2 | 1 |  | [FQBS-027] quantity to be confirmed at project level depending on service requirements
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FQBS-116 | CHAIR: visitor, waiting areas | 14 | 1 |  | [FQBS-032]
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | FQTA-201 | TABLE: square, 450H, 500L | 2 | 1 |  | [FQTA-071]
WAIT-20 | Waiting, 20m2 | Public Areas | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITBU-011]
WAIT-20 | Waiting, 20m2 | Public Areas | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
WAIT-20 | Waiting, 20m2 | Public Areas | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook is desirable
WAIT-20 | Waiting, 20m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-003] carpet tiles are also acceptable
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] height to be coordinated with adjacent wall protection
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022] as required to suit loose furniture layout; crash rails are also acceptable
WAIT-30 | Waiting, 30m2 | Public Areas | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109] to display screen
WAIT-30 | Waiting, 30m2 | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
WAIT-30 | Waiting, 30m2 | Public Areas | SER | ITIN-076 | OUTLET: MATV, wall mounted | 2 | 1 |  | [ITIN-070] may be replaced with data outlet in accordance with local ICT policy
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIHR-046 | RACK: magazine/pamphlet, wall mounted | 1 | 3 |  | [FIHR-045] optional
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQGE-002 | ARTWORK: wall mounted | 2 | 3 |  | [FQGE-002] optional
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001] quantity and location to suit local IPC policies
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 2 | 1 |  | [FIHR-006]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQBS-102 | CHAIR: visitor, clinical areas, bariatric | 2 | 1 |  | [FQBS-027] quantity to be confirmed at project level depending on service requirements
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQBS-116 | CHAIR: visitor, waiting areas | 21 | 1 |  | [FQBS-032]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | FQTA-201 | TABLE: square, 450H, 500L | 3 | 1 |  | [FQTA-071]
WAIT-30 | Waiting, 30m2 | Public Areas | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 2 | 1 |  | [ITBU-011]
WAIT-30 | Waiting, 30m2 | Public Areas | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
WAIT-30 | Waiting, 30m2 | Public Areas | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook is desirable
WAIT-30 | Waiting, 30m2 | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-003] carpet tiles are also acceptable
WAIT-S | Waiting, Sub | Public Areas | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001] quantity and location to suit local IPC policies
WAIT-S | Waiting, Sub | Public Areas | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 1 |  | [FIDI-056]
WAIT-S | Waiting, Sub | Public Areas | FFE | FQBS-102 | CHAIR: visitor, clinical areas, bariatric | 1 | 1 |  | [FQBS-027] quantity to be confirmed at project level depending on service requirements
WAIT-S | Waiting, Sub | Public Areas | FFE | FQBS-116 | CHAIR: visitor, waiting areas | 2 | 1 |  | [FQBS-032]
WAIT-S | Waiting, Sub | Public Areas | FFE | FQTA-201 | TABLE: square, 450H, 500L | 1 | 1 |  | [FQTA-071]
WAIT-S | Waiting, Sub | Public Areas | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 3 |  | [ITCL-008] optional
WAIT-S | Waiting, Sub | Public Areas | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional
WAIT-S | Waiting, Sub | Public Areas | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
WAIT-S | Waiting, Sub | Public Areas | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] to be coordinated with adjacent area
WAIT-S | Waiting, Sub | Public Areas | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminium skirting are acceptable if carpet tiles provided; to be coordinated with adjacent area
WAIT-S | Waiting, Sub | Public Areas | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] height to be coordinated with adjacent wall protection
WAIT-S | Waiting, Sub | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
WAIT-S | Waiting, Sub | Public Areas | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022] as required to suit loose furniture layout; crash rails are also acceptable
WAIT-S | Waiting, Sub | Public Areas | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
WAIT-S | Waiting, Sub | Public Areas | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-003] carpet tiles are also acceptable; to be coordinated with adjacent area
WAIT-SEC | Waiting - Secure | Mental Health | D+W | DOHI-144.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel, with integral blind | 1 | 1 | Internal - Door 1 | from external corridor
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both sides
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
WAIT-SEC | Waiting - Secure | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 3 | 1 | Floor Skirting
WAIT-SEC | Waiting - Secure | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 2 | 1 | Wall Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
WAIT-SEC | Waiting - Secure | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
WAIT-SEC | Waiting - Secure | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment display screen and CPU
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | 1 to each intercom
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to patient entertainment display screen and CPU
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | FQTA-202 | TABLE: square, 450H, 600L | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1
WAIT-SEC | Waiting - Secure | Mental Health | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 2 | 1 |  | to doors
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
WAIT-SEC | Waiting - Secure | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
WAIT-SEC | Waiting - Secure | Mental Health | D+W | DOHI-144.02 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel, with integral blind | 1 | 1 | Internal - Door 2 | to mental health unit; provision of tamper proof, anti-ligature and anti-barricade hardware to be confirmed to suit service requirements
WAIT-SEC | Waiting - Secure | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1
WAIT-SEC | Waiting - Secure | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2
WAIT-SEC | Waiting - Secure | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIRT-121 | GRAB RAIL: toilet, straight, horizontal | 1 | 1 |  | [FIRT-007]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1 |  | [FIRT-006]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FIRT-191 | BACK REST: toilet, accessible | 1 | 1 |  | [FIGE-011]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FQGE-361 | CHANGE TABLE: baby, wall mounted | 1 | 3 |  | [FQBS-035] optional
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYBA-146 | BASIN: type C, handwashing, accessible | 1 | 1 |  | [HYBA-005] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYTP-052 | TAPWARE: basin, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-035] selection of basin and tapware to be coordinated to ensure compatibility
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYWC-033 | TOILET SUITE: patient, accessible | 1 | 1 |  | [HYWC-001]
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 3 |  | [ITCL-006] optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 3 |  | [ITCL-008] optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
WCAC | Toilet - Accessible | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
WCAC | Toilet - Accessible | Sanitary Facilities | FFE | HYTP-003 | FLUSH BUTTON: toilet suite, accessible | 1 | 1 |  | [HYWC-001]
WCAC | Toilet - Accessible | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 3 |  | outside door, placement to ensure visibility along paths of travel; optional, to be provided if room located in a patient treatment area for use by patients
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
WCAC | Toilet - Accessible | Sanitary Facilities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038] optional, may be provided if room is for staff use and located in a public / patient treatment area
WCAC | Toilet - Accessible | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, emergency release required if inward opening door
WCPT | Toilet - Patient | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
WCPT | Toilet - Patient | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] with privacy latch, emergency release required if inward opening door
WCPT | Toilet - Patient | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006]
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
WCPT | Toilet - Patient | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
WCPT | Toilet - Patient | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
WCPT | Toilet - Patient | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WCPT | Toilet - Patient | Sanitary Facilities | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
WCPT | Toilet - Patient | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
WCPT | Toilet - Patient | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
WCPT | Toilet - Patient | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 1 | 1 |  | [FIHR-026]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
WCPT | Toilet - Patient | Sanitary Facilities | FFE | HYWC-021 | TOILET SUITE: standard | 1 | 1 |  | [HYWC-008]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1 |  | [FIRT-006]
WCPT | Toilet - Patient | Sanitary Facilities | FFE | FIRT-136 | GRAB RAIL: toilet, drop down | 1 | 3 |  | [FIRT-008] optional
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
WCPT | Toilet - Patient | Sanitary Facilities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
WCPT | Toilet - Patient | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; placement to ensure visibility along paths of travel
WCPU | Toilet - Public | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
WCPU | Toilet - Public | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WCPU | Toilet - Public | Sanitary Facilities | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
WCPU | Toilet - Public | Sanitary Facilities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with privacy latch, emergency release required if inward opening door
WCPU | Toilet - Public | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
WCPU | Toilet - Public | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
WCPU | Toilet - Public | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
WCPU | Toilet - Public | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
WCPU | Toilet - Public | Sanitary Facilities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
WCPU | Toilet - Public | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 1 | 1 |  | [FIHR-026]
WCPU | Toilet - Public | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
WCPU | Toilet - Public | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
WCPU | Toilet - Public | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WCPU | Toilet - Public | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
WCPU | Toilet - Public | Sanitary Facilities | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
WCPU | Toilet - Public | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
WCPU | Toilet - Public | Sanitary Facilities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
WCPU | Toilet - Public | Sanitary Facilities | FFE | HYWC-021 | TOILET SUITE: standard | 1 | 1 |  | [HYWC-008]
WCPU | Toilet - Public | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
WCPU | Toilet - Public | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
WCPU | Toilet - Public | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
WCPU | Toilet - Public | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
WCPU | Toilet - Public | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
WCPU | Toilet - Public | Sanitary Facilities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
WCPU | Toilet - Public | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
WCST | Toilet - Staff | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
WCST | Toilet - Staff | Sanitary Facilities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with privacy latch, emergency release required if inward opening door
WCST | Toilet - Staff | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
WCST | Toilet - Staff | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
WCST | Toilet - Staff | Sanitary Facilities | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
WCST | Toilet - Staff | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
WCST | Toilet - Staff | Sanitary Facilities | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
WCST | Toilet - Staff | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
WCST | Toilet - Staff | Sanitary Facilities | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
WCST | Toilet - Staff | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006]
WCST | Toilet - Staff | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
WCST | Toilet - Staff | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
WCST | Toilet - Staff | Sanitary Facilities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
WCST | Toilet - Staff | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 1 | 1 |  | [FIHR-026]
WCST | Toilet - Staff | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
WCST | Toilet - Staff | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
WCST | Toilet - Staff | Sanitary Facilities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
WCST | Toilet - Staff | Sanitary Facilities | FFE | HYWC-021 | TOILET SUITE: standard | 1 | 1 |  | [HYWC-008]
WCST | Toilet - Staff | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
WCST | Toilet - Staff | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
WCST | Toilet - Staff | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
WCST | Toilet - Staff | Sanitary Facilities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
WCST | Toilet - Staff | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
WCST | Toilet - Staff | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
WCST | Toilet - Staff | Sanitary Facilities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional, may be provided if room located in a public / patient treatment area
WCST | Toilet - Staff | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
XRAY | General X-Ray Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
XRAY | General X-Ray Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
XRAY | General X-Ray Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
XRAY | General X-Ray Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
XRAY | General X-Ray Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
XRAY | General X-Ray Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
XRAY | General X-Ray Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
XRAY | General X-Ray Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | optional - to control workstation area
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
XRAY | General X-Ray Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
XRAY | General X-Ray Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | to imaging area
XRAY | General X-Ray Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to change room if provided
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to change room side
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
XRAY | General X-Ray Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control workstation side
XRAY | General X-Ray Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | if this room is located within an emergency department the quantity of services may need to align with acute treatment bays to support use with trauma patients
XRAY | General X-Ray Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
XRAY | General X-Ray Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
XRAY | General X-Ray Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 above medical services panel, 1 to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | 1 close to imaging device, 1 to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
XRAY | General X-Ray Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | outside all room entries, to automatically turn on when modality is in use
XRAY | General X-Ray Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | to control workstation area, main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
XRAY | General X-Ray Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation
XRAY | General X-Ray Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
XRAY | General X-Ray Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-312 | ISOLATOR: three phase, with socket outlet, wall mounted | 1 | 1 |  | to generator cabinet, power requirements to be confirmed with MME vendor
XRAY | General X-Ray Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 3 | 1 |  | to control workstation area, extent of UPS to be confirmed to suit service and equipment requirements
XRAY | General X-Ray Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 2 | 1 |  | 1 to PACS CPU, 1 to x-ray CPU
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | on dual arm bracket
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
XRAY | General X-Ray Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 2 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | to control workstation area
XRAY | General X-Ray Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-025 | GENERATOR: general x-ray, floor standing | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-023 | BOARD: electrical distribution (EDB), general x-ray | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-005 | IMAGING DEVICE: general x-ray, wall bucky, fixed | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-009 | TABLE: patient, general x-ray | 1 | 1 |  | may be floating top or elevating table
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-001 | IMAGING DEVICE: general x-ray, tube head, ceiling suspended | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-012 | CONTROL CONSOLE: general x-ray, dual display screens, keyboard and mouse, control unit, desktop | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-016 | COMPUTER: general x-ray, central processing unit (CPU) | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-036 | CHARGER: general x-ray, detector, battery, desktop | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-041 | STAND: general x-ray, image stitching, lead ruler, mobile | 1 | 1 |  | optional - may be shared between multiple rooms
XRAY | General X-Ray Room | Medical Imaging | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | optional - patient transfer methods and equipment to meet local WHS policies
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | optional - provide if patient slide required
XRAY | General X-Ray Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
XRAY | General X-Ray Room | Medical Imaging | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-026 | GENERATOR: general x-ray, wall mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | MIXR-033 | HOLDER: general x-ray, detector, floor standing | 1 | 1 |  | to control workstation area, under bench, for storage of charged imaging plates
XRAY | General X-Ray Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
XRAY | General X-Ray Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1
XRAY | General X-Ray Room | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 1 | 1 |  | on dual arm bracket
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | to imaging area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to both sides
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | optional - to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room to x-ray area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 3 | optional - to change room if provided
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 2 | for observation from control room to OPG area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 3 | to change room side
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to imaging room side
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control workstation side
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 3
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to x-ray area, if this room is located within an emergency department the quantity of services may need to align with acute treatment bays to support use with trauma patients
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to OPG area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 above x-ray medical services panel, 1 to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | 1 between imaging devices, 1 to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to workstation, over desk for portable devices
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to room entry, 1 to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | outside all room entries, to automatically turn on when modality is in use
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 2 | 1 |  | to control workstation area, 1 to x-ray, 1 to OPG, main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-312 | ISOLATOR: three phase, with socket outlet, wall mounted | 1 | 1 |  | to generator cabinet, power requirements to be confirmed with MME vendor
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-161 | GPO: single, UPS, wall mounted | 3 | 1 |  | to control workstation, to x-ray control, extent of UPS to be confirmed to suit service and equipment requirements
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | to OPG imaging device
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to OPG imaging device
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to OPG imaging device
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to control workstation, as required for OPG imaging device connection to remote activation panel
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | 1 to x-ray MSP, 1 to OPG MSP
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | 1 to x-ray MSP, 1 to OPG MSP
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 2 | 1 |  | 1 to x-ray area, 1 to OPG area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 3 | 1 |  | 1 to OPG PACS CPU, 1 to x-ray PACS CPU, 1 to x-ray control CPU
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | to control workstation, to x-ray control, on dual arm bracket
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | JOBE-251 | CAP: cable access | 3 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | to control workstation area
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-025 | GENERATOR: general x-ray, floor standing | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-023 | BOARD: electrical distribution (EDB), general x-ray | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-005 | IMAGING DEVICE: general x-ray, wall bucky, fixed | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-009 | TABLE: patient, general x-ray | 1 | 1 |  | may be floating top or elevating table
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-001 | IMAGING DEVICE: general x-ray, tube head, ceiling suspended | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-012 | CONTROL CONSOLE: general x-ray, dual display screens, keyboard and mouse, control unit, desktop | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-016 | COMPUTER: general x-ray, central processing unit (CPU) | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-036 | CHARGER: general x-ray, detector, battery, desktop | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | optional
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-191 | DISPENSER: emesis bags, wall mounted | 1 | 1 |  | optional
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | optional
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-041 | STAND: general x-ray, image stitching, lead ruler, mobile | 1 | 1 |  | optional - may be shared between multiple rooms
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | optional - patient transfer methods and equipment to meet local WHS policies
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | optional - provide if patient slide required
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements, operational policies for stock centralisation/decanting and infection prevention and control policies
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-026 | GENERATOR: general x-ray, wall mounted | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIXR-033 | HOLDER: general x-ray, detector, floor standing | 1 | 1 |  | to control workstation area, under bench, for storage of charged imaging plates
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | optional - for microfibre wipes
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to control workstation, to x-ray control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-171 | DISPLAY SCREEN: computer | 1 | 1 |  | to control workstation, to x-ray control, on dual arm bracket
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MMTR-001.02 | TROLLEY: stainless steel, 490W x 490D x 900H nom, 2 tier | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-341 | SCANNER: desktop, document, flatbed, desktop | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 1 | 1 |  | to control workstation, to OPG control
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIOC-001 | IMAGING DEVICE: orthopantomogram (OPG) | 1 | 1
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | MIOC-011 | CONTROL PANEL: orthopantomogram (OPG), remote activation | 1 | 1 |  | to control workstation
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | located close to OPG MSP
XRAY-OPG | General X-Ray / OPG Room | Medical Imaging | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.