## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | Translation and QA Only | 20 | 2700 | 1BR-SP-B | 6 | 07.04.2026 |  | 24 hours | 1 patient; 1-2 visitors; up to 4 staff intermittently | A 1 Bed Room - CCU will accommodate one patient and support the delivery of a range of clinical care, minor procedures and diagnostic tests, with clinical staff requiring access to both sides of the bed. | ~ 1 Bed Room - CCU may vary in configuration to suit different Ensuite options including inboard, outboard and stacked (also known as 'back-to-back' or 'nested') configurations. In each configuration, sufficient clearance is required for equipment and staff to access both sides of the bed. ~ Glazed doors and observation windows may be provided for visibility of high acuity patients and monitoring equipment. The provision of observation windows and the use of interstitial blinds or privacy curtains is to be supported by operational models for observation as well as support for patient privacy. ~ The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring and diagnostic equipment. ~ Natural light and outlook is essential and the patient will need to have an external outlook from either the chair or the bed, preferably both. | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] to corridor; extent of glazing to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | [DWPR-001] to ensuite side
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to ensuite
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to bedroom side
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | WIFX-008.01 | WINDOW: fixed, internal, single glazed, sill at 1050H | 1 | 3 | Internal - Window 1 | [DWOB-001] optional; extent of glazing to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1 | [DWWH-005] external, natural light and outlook essential
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | [FIHR-016] optional, mobile sharps bin may be provided to be shared between multiple rooms
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004] to patient entertainment screen; configuration will be dependent on operational and ICT policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047] to door and observation window
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010] to door and observation window
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1 |  | [FQSN-051] type and extent of storage for patient property to suit operational policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013] z
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | [FQCW-044] optional, mobile sharps bin may be provided to be shared between multiple rooms
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012] configuration will be dependent on operational and ICT policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | [ITNE-049] optional, to patient locker; provision dependent on operational policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | [FIJO-209] type and extent of storage for patient property to suit operational policies
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1 |  | [MMBE-010]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMGE-019 | CHAIR: patient | 1 | 1 |  | [MMGE-019]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FFE | MMPM-021 | MONITOR: patient, high acuity | 1 | 1 |  | [MMHA-005] telemetry provision to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] ceiling tiles may also be acceptable dependent upon the acuity of patients to be accommodated and procedures to be performed within the room
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-010] to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-002]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 9 | 1 | Panel 1 | [ELGP-122] type and quantity to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1 | [ITIN-025] quantity to suit service requirements
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Panel 1 | [MMGE-002]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] to bedhead; low level for electric bed
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] adjacent to patient chair
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-106.01 | GPO: single, ceiling mounted, horizontal | 1 | 1 |  | [ELGP-101] to patient entertainment system
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELGP-231.01 | GPO: double, emergency power, wall mounted, horizontal | 1 | 1 |  | [ELGP-223] to patient monitor
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1 |  | [ELBO-005]
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006] on services panel
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 to general room lighting, 1 to night lighting, 1 on services panel to reading light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] on services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] above services panel, with indicator button and light
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] on services panel
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to patient monitor
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment screen, may be replaced with data outlet in accordance with ICT policy
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | [LIFX-017] switch to patient handset and wall near entry
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011] switch to patient handset and services panel
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
1BR-CCU | 1 Bed Room - CCU | Cardiac Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware