## Room Template Data
1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 (1BR-CO-OU2) - Room Template Properties and Room Template Data
2025-12-15
No. of Standard Components = 1
Code | Template Name | Standard Component Set | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | 19 | 2700 |  | 1 | 15.12.2025 | 24 hours | 1 patient; 1-2 visitors; 1-4 staff intermittently | The 1-Bed Room - Carer Overnight, Outboard Ensuite, Type 2 provides space and amenities for accommodating one patient, as well as one carer/family member to stay overnight, and supporting the delivery of clinical care and treatment. This Standard Component is used in conjunction with the Ensuite - Inboard/Outboard (ENS-IN-OU), and the ensuite and bedroom should be planned as a unit. | ~ Spatial allowances accommodate equipment and staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption. Clearances for use of mobile patient lifting equipment must be considered on both sides of the patient bed. It is recommended that a minimum of 1100mm clear is provided to both sides of the patient bed. ~ This room may be utilised as a standard pressure (S-Class) isolation room. On these occasions, provision of appropriate personal protective equipment (PPE) such as gloves, masks, face shields, gowns, etc. will be required close to the entry of the room. Proximity to existing PPE bays, provision of clear area for parking a PPE trolley or the ability to temporarily hang additional PPE holders on the wall adjacent to the door should be considered during planning. A document frame to hold isolation precaution signage when it is needed may be attached to the wall or door to alert staff to isolation precaution requirements. For additional information on standard pressure (S-Class) rooms, as well considerations and requirements for positive pressure (P-Class) and negative pressure (N-Class) rooms, refer to 'AusHFG Isolation Rooms - Design and Engineering Requirements' and 'Part D: infection Prevention and Control'. ~ Alcohol-based hand rub (ABHR) may be provided in a wall mounted dispenser or in a holder that can be attached to the end of the patient bed. The location of ABHR is to be confirmed at project level to support staff to comply with the ‘5 Moments of Hand Hygiene’ practices and local IPC policies. ~ The handwashing basin is to be located at least 1.2m from patient beds; refer to Part D Section 4.1.2-5 for more information. Clear access for bed movement must also be considered when determining basin location. ~ The content and configuration of the medical services panel (MSP), including type and quantity of medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. This includes confirming any increase/change in services where this Standard Component is used in specific clinical settings and/or high acuity settings. ~ Access to natural light and outlook is essential; patients are to have access to an external outlook from either the bed or the chair, preferably both. ~ Requirements for staff notetaking/write-up at the bedside, including use of electronic medical records, are to be confirmed at project level to suit clinical service requirements and local ICT policies. This may include the use of workstations on wheels (WOWs) that are kept with staff members and require parking areas and charging facilities in central locations within the unit, or provision of fixed wall mounted computers in each bedroom, requiring tap-on login capability. Facilities with paper-based medical record systems or hybrid paper/digital systems may require provision of a document holder within the bedroom (typically hung on the end of the bed) or just outside the bedroom to hold patient records. ~ Additional ICT requirements within high acuity settings or in remote facilities (e.g. for patient monitoring, virtual patient consultation/monitoring, etc.) are to be confirmed at project level to suit clinical service requirements. Where a patient monitor is provided, appropriate structural support in the wall/bedhead joinery is required for mounting the monitor. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient areas is to suit local security and WHS policies and operational service requirements. ~ A patient lifting track is shown as optional in this Standard Component. Provision of a lifting track, and the type and quantity of bedrooms they are provided in, is to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling. Configuration (fixed track or traverse track), installation (ceiling mounted or recessed), weight rating/safe working load (SWL) requirements, and extent (i.e. for bed to chair/wheelchair/commode transfer only, full room coverage, full transfer to ensuite, etc.) must also be considered and confirmed by project teams. Selected equipment is to meet local IP&C policies and cleaning requirements. Charging and storage of patient lifter cassette motors is to be confirmed at project level. Cassette motors may be stored within the patient room, or a small number of cassette motors may be shared between multiple rooms that have patient lifer tracks and are predominantly stored in a central equipment store. Requirements for charging and storage within the patient bedroom are dependent on operational models and product specifications/operating requirements. ~ A wall mounted sharps bin is indicated in this Standard Component. Depending on clinical service requirements and local waste management policies, sharps bins may alternatively be trolley or cart mounted and brought in as required for treatment. ~ Provision of kits/bags containing emergency airway equipment/consumables and associated storage methods (e.g. hook, basket, etc.) is to be confirmed at project level to suit clinical service requirements. ~ Patient property storage facilities, including provision and configuration of a wardrobe and configuration of the bedside locker, are to be confirmed at project level to suit operational models and clinical service requirements, including considerations for anticipated length of stay. ~ Furniture to accommodate a carer within the room is to be confirmed at project level, including consideration of anticipated length of stay, operational models for provision of linen, provision of carer property storage, and the ability/requirement to fold-up or pack away furniture used for sleeping when it is not in use. Fixed joinery items may be considered to provide this function; however, freestanding furniture is recommended where flexibility is required. Cleaning processes/products, and infection prevention and control (IPC) requirements must also be considered in assessment of furniture and upholstery selection. ~ This Standard Component shows the entry door swinging outwards into the corridor into a niche created by the arrangement of the bedroom with an inboard ensuite. An inward swinging door is also acceptable. ~ The extent of glazing provided to the door (i.e. size of the vision panel) is to be confirmed at project level based on clinical service requirements for patient observation, balanced with patient privacy requirements. Paediatric, maternity and other settings where small children are regularly patients/visitors may consider lowering the bottom of the vision panel to support visibility of children behind the door before opening. Provision of integral blinds to door glazing may be considered, however, this must be assessed in relation to other workflows, e.g. use of mobile imaging equipment through glazing of observation panels for infectious patients under standard isolation precautions, where an integral blind could interfere. ~ Provision of an additional power outlet located on the wall at the foot of the bed for mobile equipment (e.g. mobile x-ray machines) or fall detection monitoring devices is to be confirmed at project level to suit clinical service requirements. ~ Patient entertainment systems may be mounted on the wall, ceiling or bedhead. Configuration of the patient entertainment system (type, size, mounting and location) is to be confirmed at project level to suit local ICT policies and operational models. Services (power, data and/or AV connection) are to be confirmed to suit selected systems. Appropriate structural support in the wall, ceiling or bedhead joinery is required for mounting the patient entertainment system. ~ Nurse call indicator lights are noted to be located in the corridor outside the bedroom door, location to ensure clear line of sight along paths of travel. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessment. Refer to Part D Section 6.4 for more information. ~ Notes applied to floor finish ratings relate to AS4586 and associated HB198 requirements. Compliance with current regulations must be verified by project teams on each project. | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
Standard Components - Items in Room Template
2025-12-15
No. of Standard Components = 1
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to both sides
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | optional; provision dependent on frame material and finish and equipment movement in adjacent area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish and equipment movement in adjacent area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | type, material and cleaning requirements of window coverings to be confirmed at project level
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | to be shadow angle cornice if drop-in ceiling tiles are provided
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | finish to be suitable for clinical environments, refer to local engineering services guidance for acoustic performance requirements (i.e. reverberation time control, sound absorption class, etc.); drop-in ceiling tiles may also be acceptable depending on local IPC policies and patient cohort requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | to ensuite (see ENS-IN-OU)
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | to corridor; extent of glazing to suit clinical service requirements for patient observation and patient privacy requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | optional; may be included for patient lifter track where provided if storage and charging of patient lifter cassette motor required in room, provision dependent on clinical requirements and operational models for sharing and storing lifting equipment, product selection, and local WHS policies.
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-116 | GPO: single, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit clinical service requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to carer's area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead, for patient/visitor use
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELGP-211 | GPO: double, joinery mounted | 1 | 1 |  | to bedhead; low height for bed and mattress
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 2
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | 1 to general room lights, 1 to night light
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | for patient care information
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided in a holder on the end of the patient bed
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIDI-386 | FRAME: document, A4, wall mounted | 1 | 3 |  | optional; outside room to wall or door, for infection control precaution and/or patient needs information; provision dependent on operational models
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-029 | HOOK: equipment | 2 | 3 |  | optional; for emergency airway kit if provided; an alternative storage solution may be required depending on use of bag or box kits
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 3 |  | optional; sharps bin may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIHR-351 | BRACKET: patient entertainment system, fixed, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQBS-282 | RECLINER: visitor, clinical areas, fold out bed | 1 | 1 |  | selected item to suit operational models and local IPC policies
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQSN-100 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQTA-401 | TABLE: round, 450H, 500 diameter | 1 | 1 |  | to carer's area
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 3 |  | optional; may alternatively be provided on a dedicated cart or clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies, size to suit clinical requirements and operational models for frequency of disposal
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware to be coordinated to ensure compatibility
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside bedroom door, placement to ensure visibility along paths of travel
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ITCL-173 | BUTTON: nurse call, patient to staff call and staff assist call, with cancel, with handset connection point, with assistive device connection points, on services panel | 1 | 1 | Panel 2 | requirements for assistive device connection point to be confirmed at project level; may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 |  | with holder and cable management items as required; inclusion of intercom function may be considered at project level
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | configuration to be confirmed to suit local ICT policies and operational models; services to be confirmed to suit selected system
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; to telephone if provided
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | ITIN-076 | OUTLET: MATV, wall mounted | 1 | 1 |  | to patient entertainment system; services to be confirmed to suit selected system, may be replaced with data outlet or alternate AV outlet depending on system requirements and local ICT policies
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, provision dependent on operational models
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | JOBH-021 | BEDHEAD: full height | 1 | 1 |  | wall protection panel with in-wall medical services panel is also acceptable
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | size and configuration to be confirmed at project level; may be provided at a height that allows for a cleanable shelf on top for gifts/cards or patient property (maximum 1500 AFFL); where the height is increased a bulkhead is to be provided over the joinery unit
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | control to entry door and patient handset
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | control to bedhead and patient handset
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | optional; provision, type, weight rating/SWL and extent to be confirmed at project level to suit clinical service requirements and local WHS policies for patient handling
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store; where it is dedicated to a room, configuration of the lifting track should consider extension to a 'parking' location that allows the cassette motor to be stored out of the way
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMBE-261 | SLING: patient lifter | 1 | 1 |  | optional; for patient lifter track where provided; may be shared between multiple rooms with lifting tracks and stored in a central equipment store
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-019 | CHAIR: patient | 1 | 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | with tubing storage/management accessories as required
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FFE | MMGE-436 | KIT: emergency airway equipment, portable | 1 | 3 |  | optional; provision is dependent on clinical service requirements; use of bag or box kit is to be confirmed to inform storage solution requirements
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to clinical side (closest to entry door); content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient/visitor side; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | WIFX-058.04 | WINDOW: fixed, internal, double glazed, sill at 1050H, with integral blind | 1 | 1 | Internal - Window 1 | optional; provision dependent on clinical service requirements for patient observation
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | D+W | WIFX-155.01 | WINDOW: fixed, external, double glazed, sill at 600H | 1 | 1 | External - Window 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin
1BR-CO-OU2 | 1 Bed Room - Carer Overnight, Outboard Ensuite, Type 2 | Inpatient Accommodation | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | 1 | Wall Protection