## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
1BR-H-12 | 1 Bed Room, 12m2 | 12 |  | 1 patient; 1-2 staff; 1-2 visitors | 24 Hours |  | A 1 Bed Room, 12m2, will accommodate one patient for the delivery of short term nursing and medical care (e.g. day only procedures) including observation, assessment or treatment. The room layout is to allow movement of equipment around the bed space. Natural light and outlook is essential. The 1 Bed Room, 12m2, may also be used as an Isolation Room - Class S (standard pressure). Door glazing and an internal window is recommended with this option pending location of Ensuite if provided. Acoustics: acoustic privacy required. Body protected electrical area.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 1000 | Floor finish | 1 | Carpet optional, Significant change in colour to be avoided. | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 2000 | Skirting | 1 | feather edge vinyl skirting if carpeted | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 2525 | Wall protection | 1 |  |  |  | Bed protection wall panel | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 2526 | Floor finish | 1 | Significant change in colour to be avoided. | Vinyl | Non-slip | Seamless coved | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 2529 | Door protection | 1 |  | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 2530 | Door protection | 1 |  | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 2535 | Wall protection | 1 |  |  |  | Corner guards to 900 AFFL | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 2906 | Wall finish | 1 | Selection of material to comply with Part D Infection Prevention and Control AusHFG. |  |  | Splashback behind basin | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 5010 | Ceiling - Plasterboard | 1 | Acoustic tiles acceptable (excluding negative pressure isolation room) | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 7001 | Windows | 1 | natural light & outlook essential. |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 7010 | Observation | 1 | For isolation room use. | Glass | Clear | Through door/s | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 7030 | Observation | 1 | Optional, to rooms with an outboard ensuite (if ensuite required). | Alum/ Glass | Powdercoat | Internal window, door height | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | Fabrics | 9128 | Door - 1200mm | 1 | 1200mm (single door)/ 1400mm (1 +1/2 door) clear opening, half leaf optional; obs panel for Isolation use | Solid Core/ Glass | Paint | 1 1/2 leaf, observation panel | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FE | FE-2800 | Basin - handwash, Type B | 1 | Elbow action levers or handsfree optional. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FE | FE-5622 | Bed - inpatient, electric + standard patient mattress | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FE | FE-5857 | Light - procedures small, ceiling | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-1252 | Blind - Venetian integral | 2 | No dependant on number of windows |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-12900 | Wire panel - for storage-bins | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-1465 | Bracket - suction bottle | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-150 | Air flowmeter | 1 | Optional |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-16200 | Table - overbed | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-16250 | Oxygen flowmeter | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-21950 | Suction adapter | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-22000 | Suction bottle | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-24405 | Whiteboard - magnetic | 1 | Optional; Clinical use |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-2650 | Chair - visitor, patient | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-4600 | Curtain track - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-5000 | Curtain - bed screen | 1 | Number to suit bed and curtain track configuration. |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FE | FF-5547 | Patient entertainment | 1 | Optional in accordance with ICT Policy |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-5580 | Storage bins - stainless steel wire mesh | 3 | For wired panels, optional. Depends on functionality, infection control and cleaning policies. |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-5825 | Bracket - patient entertainment, ceiling | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-5828 | External window dressing | 1 | Number to align with window configuration. Window dressing type to comply with Infection Control policy. |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-5830 | Dispenser - antiseptic hand rub | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-6153 | Dispenser - moisturiser | 1 | Optional. Depends on Operational Policy. |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-1006 | Voice / Data outlet: double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-1090 | TV: MATV | 1 | If patient entertainment system required. May be replaced with data outlet, in accordance with ICT policy |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-11000 | Wall panel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-1412 | Special examination downlight | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-1951 | Staff assist call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-6050 | Special: reading | 1 | Up light optional or dimmable room lighting. |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-6060 | Special: night lights | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-6200 | Light switches | 3 | Room, reading and night light |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-7000 | Oxygen (O2) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-7020 | Medical Air (MA) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-7040 | Suction | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-8000 | Patient/ Staff call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-8005 | Patient call handset | 1 | call button & light switch on the handset |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-9000 | GPO: Single | 1 | if patient entertainment system required |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-9000 | GPO: Single | 4 | Bedhead |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-9001 | GPO: Double | 2 | Bedhead, low level, for electric bed and mattress, when required |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-9010 | GPO: Emergency power, single (V) | 4 | Bedhead |  |  |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room, 12m2 | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No