## RDS
Standard Components - Room Data Sheet
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | 17.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room will accommodate one patient for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist); (c) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite.The 1 Bed Room will also be used to plan a positive pressure room. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. The 1 Bed Room may vary in configuration to suit different Ensuite options including: inboard, outboard and back to back (also known as 'nested'). Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 3 | optional | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | DWWD-001 | BLIND: blackout | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELBO-015 | SWITCH: light, single | 3 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-109 | GPO: single, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ELPR-006 | RCD: residual current device | 2 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIHR-019 | BRACKET: for suction bottle | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FIRT-041 | TRACK: curtain, privacy, U shaped, angled | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQBS-030 | CHAIR: visitor, patient | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQGE-010 | CURTAIN: privacy screen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | FQTA-013 | TABLE: overbed | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 |  | Yes | Yes | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone | No | Yes | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | LIFX-017 | LIGHT: night light | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MGFP-004 | FLOWMETER: oxygen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-010 | BED: patient, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMGE-002 | ADAPTER: suction | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMGE-019 | CHAIR: patient | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FFE | MMGE-100 | SUCTION BOTTLE | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin | No | No | No | No | No | No | No | No | No