## RDS
Standard Components - Room Data Sheet
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
2BR-ST-B | 2 Bed Room - Outboard Ensuite | 28 | 24 Hours | 2 patient; 2-3 staff; 2-4 visitors |  | Acoustic privacy is required | A 2 Bed Room will accommodate two patients for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur in the space in between the beds. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist). Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed. Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite. The 2 Bed Room may vary in configuration to suit different Ensuite options including: inboard and outboard. Each 2 Bed Room will need direct access to the Ensuite. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | obs panel could alternatively be provided in wall | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blind if required | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | DWWD-007 | BLIND: venetian, integral | 1 | optional, if internal observation window is provided, 2 way control | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 4 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | for ceiling mounted display screen | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-105 | GPO: single, on services panel | 8 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-109 | GPO: single, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELGP-208 | GPO: double, wall mounted | 2 | bedhead low level, for electric bed | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ELPR-006 | RCD: residual current device | 4 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIHR-019 | BRACKET: for suction bottle | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 2 | wardrobe | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIRT-022 | TRACK: curtain, bedscreen, 2nd bed | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FIRT-042 | TRACK: curtain, bedscreen, U shaped, angled | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQBS-030 | CHAIR: visitor, patient | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQGE-009 | CURTAIN: bed screen | 3 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | FQTA-013 | TABLE: overbed | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 2 |  | Yes | Yes | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | + indicator button & light | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 2 | on services panel, + light switch on the handset | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | on services panel, 1 outlet for telephone | No | Yes | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | ITIN-070 | OUTLET: MATV | 2 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2 |  | No | Yes | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | LIFX-011 | LIGHT: reading light | 2 | up/down light | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | LIFX-017 | LIGHT: night light | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MGFP-002 | FLOWMETER: medical air | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MGFP-004 | FLOWMETER: oxygen | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-010 | BED: patient, electric with mattress | 2 |  | Yes | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 2 | optional, for patient lifter track | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 2 | optional, for patient lifter motor | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 2 | optional | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMGE-002 | ADAPTER: suction | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMGE-019 | CHAIR: patient | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FFE | MMGE-100 | SUCTION BOTTLE | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin | No | No | No | No | No | No | No | No | No