## RDS
Standard Components - Room Data Sheet
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
4BR-ST | 4 Bed Room - Inboard Ensuite | 58 | 24 Hours | 4 patient; 2-4 staff; 4-6 visitors |  | Acoustic privacy is required | A 4 Bed Room will accommodate four patients for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate (a) staff working at either side of the bed, however it is assumed that nursing care will predominately occur in the space in between the beds. The arrangement of the medical services panel reflects this assumption; (b) the movement of equipment around all sides of the bed (e.g. a mobile hoist). Natural light and outlook is essential and the patients will need to have an external outlook from either the chair or the bed. An inboard Ensuite is shown and each 4 Bed Room will need direct access to an Ensuite. Ideally, each 4 Bed Room will have direct access to an additional patient toilet or Ensuite. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 4 | joinery can optionally be used as bulkhead above cupboard | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 2 | to ensuites | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | DWWD-001 | BLIND: blackout | 2 | to windows, provide additional anti glare blind if required | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | DWWH-005 | WINDOW | 2 | natural light & outlook essential | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 4 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELBO-015 | SWITCH: light, single | 5 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-101 | GPO: single, ceiling mounted | 4 | for ceiling mounted display screen | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-105 | GPO: single, on services panel | 16 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-109 | GPO: single, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-122 | GPO: emergency power, single, on services panel | 16 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELGP-208 | GPO: double, wall mounted | 4 | bedhead low level, for electric bed | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ELPR-006 | RCD: residual current device | 8 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIHR-019 | BRACKET: for suction bottle | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 4 | wardrobe | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIRT-022 | TRACK: curtain, bedscreen, 2nd bed | 2 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 2 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQBS-030 | CHAIR: visitor, patient | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQGE-009 | CURTAIN: bed screen | 6 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | FQTA-013 | TABLE: overbed | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 4 |  | Yes | Yes | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-004 | BUTTON: nurse call, emergency | 4 | + indicator button & light | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 4 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-008 | BUTTON: nurse call, staff assist | 4 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 4 | on services panel, + light switch on the handset | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 4 | on services panel, 1 outlet for telephone | No | Yes | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | ITIN-070 | OUTLET: MATV | 4 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | ITNE-049 | TELEPHONE: handset, desktop | 4 |  | No | Yes | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | LIFX-011 | LIGHT: reading light | 4 | up/down light | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | LIFX-017 | LIGHT: night light | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MGFP-002 | FLOWMETER: medical air | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MGFP-004 | FLOWMETER: oxygen | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-010 | BED: patient, electric with mattress | 4 |  | Yes | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 4 | optional, for patient lifter track | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 4 | optional, for patient lifter motor | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 4 | optional | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMGE-002 | ADAPTER: suction | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMGE-019 | CHAIR: patient | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FFE | MMGE-100 | SUCTION BOTTLE | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MMSP-026 | SERVICES PANEL: wall mounted | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 4 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 6 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin | No | No | No | No | No | No | No | No | No