## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ADLD | ADL Dining | Allied Health | Translation and QA Only | 12 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 4 patients;; 1-2 staff | The ADL Dining provides a flexible space for the training and assessment of patients in Activities of Daily Living (ADL) tasks. Typically collocated with the ADL Kitchen, the Dining room supports small group discussions and demonstrations between both rooms and provides a space for debriefing after training and assessment of ADL tasks in the Kitchen. | ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. ~ External outlook and access to natural light is desirable. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ADLD | ADL Dining | Allied Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004]
ADLD | ADL Dining | Allied Health | D+W | WIFX-057.01 | WINDOW: fixed, internal, double glazed, sill at 900H | 1 | 1 | Internal - Window 1 | [DWWH-005] desirable
ADLD | ADL Dining | Allied Health | FFE | FQBS-151 | CHAIR: dining areas | 3 | 1 |  | [FQBS-015]
ADLD | ADL Dining | Allied Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1 |  | [FQGE-002]
ADLD | ADL Dining | Allied Health | FFE | FQTA-226.05 | TABLE: square, 750H nom, 1000L, adjustable height | 1 | 1 |  | [FQTA-085] height adjustable between 750-850H
ADLD | ADL Dining | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
ADLD | ADL Dining | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
ADLD | ADL Dining | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
ADLD | ADL Dining | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
ADLD | ADL Dining | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
ADLD | ADL Dining | Allied Health | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-022]
ADLD | ADL Dining | Allied Health | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006]
ADLD | ADL Dining | Allied Health | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
ADLD | ADL Dining | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
ADLD | ADL Dining | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ADLD | ADL Dining | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLD | ADL Dining | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLD | ADL Dining | Allied Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]