## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ADLK | ADL Kitchen | Allied Health | Translation and QA Only | 12 | 2700 | ADLK-OP | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 patients;; 1-2 staff | The ADL Kitchen provides an accessible space for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The space is to be functional for a range of patients including wheelchair users. | ~ The kitchen can include a combination of fittings and appliances such as a sink, cooktop, oven/grill, microwave and refrigerator to support common ADL training and assessment tasks as per service requirements. Room exhaust to be provided to range hood over cooktop. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. ~ The room may be enclosed with a lockable door depending on security requirements. ~ External outlook and access to natural light is desirable. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ADLK | ADL Kitchen | Allied Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004]
ADLK | ADL Kitchen | Allied Health | D+W | WIFX-161.01 | WINDOW: fixed, external, double glazed, sill at 1500H | 1 | 1 | Internal - Window 1 | [DWWH-005] desirable
ADLK | ADL Kitchen | Allied Health | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
ADLK | ADL Kitchen | Allied Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
ADLK | ADL Kitchen | Allied Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 1 | 1 |  | [FQCA-067] on bench
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-121 | APPLIANCE: toaster, benchtop, domestic | 1 | 1 |  | [FQCA-080]
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-141 | APPLIANCE: kettle, electric, benchtop, domestic | 1 | 1 |  | [FQCA-046]
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-272 | COOKTOP: electric, induction, domestic | 1 | 1 |  | [FQCA-089] controls to be located close to front
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-321 | RANGEHOOD: electric, domestic | 1 | 1 |  | [FQCA-072] over cooktop
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-341 | OVEN: electric, domestic | 1 | 1 |  | [FQCA-063] retractable/side opening doors
ADLK | ADL Kitchen | Allied Health | FFE | FQCA-402 | FRIDGE: domestic, 300L nom, single door | 1 | 1 |  | [FQCA-031]
ADLK | ADL Kitchen | Allied Health | FFE | FQSM-051 | PEDESTAL: mobile, 660H nominal, 2 equal wire basket drawers | 1 | 1 |  | [FQSM-040] under bench
ADLK | ADL Kitchen | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
ADLK | ADL Kitchen | Allied Health | FFE | HYBA-323 | SINK: 1 1/2 bowl, with drainer | 1 | 1 |  | [HYBA-041] heat lined, warm water
ADLK | ADL Kitchen | Allied Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
ADLK | ADL Kitchen | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-020]
ADLK | ADL Kitchen | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-059]
ADLK | ADL Kitchen | Allied Health | FFE | JOBE-221 | BENCH SUPPORT: end panel | 3 | 1 |  | [FIJO-213]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-131]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-051 | CUPBOARD: tall, with built in oven | 1 | 1 |  | [FIJO-223]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 2 | 1 |  | [FIJO-156]
ADLK | ADL Kitchen | Allied Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-143]
ADLK | ADL Kitchen | Allied Health | FFE | JODW-001 | DRAWER: under bench, single | 6 | 1 |  | [FIJO-205]
ADLK | ADL Kitchen | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
ADLK | ADL Kitchen | Allied Health | FFE | JOGE-011 | PANEL: fixed, infill | 5 | 1 |  | [FIJO-224] to sink and cooktop
ADLK | ADL Kitchen | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
ADLK | ADL Kitchen | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
ADLK | ADL Kitchen | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting | [FLSK-010]
ADLK | ADL Kitchen | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10; pendulum P3 or agreed equivalent around sink
ADLK | ADL Kitchen | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
ADLK | ADL Kitchen | Allied Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-007]
ADLK | ADL Kitchen | Allied Health | SER | ELGE-001 | DIRECT CONNECTION: power | 2 | 1 |  | [ELGE-001] to cooktop and oven
ADLK | ADL Kitchen | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | [ELGP-109] to range hood and fridge
ADLK | ADL Kitchen | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | [ELGP-208]
ADLK | ADL Kitchen | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
ADLK | ADL Kitchen | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ADLK | ADL Kitchen | Allied Health | SER | ELSW-101 | SWITCH: isolation | 1 | 1 |  | [ELBO-007] to cooktop and oven