## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ADLL | ADL Laundry | Allied Health | Translation and QA Only | 8 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; 1 staff | The ADL Laundry provides domestic facilities for the training and assessment of patients in Activities of Daily Living (ADL) tasks. The room will include a domestic washing machine and dryer which, if front loading models are selected, may be placed on plinths to raise machines to an accessible height to support common ADL training and assessment tasks as per service requirements. A laundry tub and storage for ironing equipment are also provided. | ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. If multiple ADL rooms are combined into an ADL suite nurse call buttons can be rationalised into a central location. ~ The space may be provided as an open bay that is collocated with other ADL rooms. If open, the impact of noise on adjacent areas must be considered. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ADLL | ADL Laundry | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ADLL | ADL Laundry | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ADLL | ADL Laundry | Allied Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional
ADLL | ADL Laundry | Allied Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
ADLL | ADL Laundry | Allied Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
ADLL | ADL Laundry | Allied Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
ADLL | ADL Laundry | Allied Health | FFE | FQCL-101 | WASHING MACHINE: laundry, domestic, front loading | 1 | 1 |  | [FQCW-063]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-111 | DRYER: laundry, domestic | 1 | 1 |  | [FQGE-015]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-121 | PLINTH: washing machine, domestic | 2 | 1 |  | [MMAH-039]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-152 | APPLIANCE: iron, laundry, electric, domestic | 1 | 1 |  | [FQGE-028]
ADLL | ADL Laundry | Allied Health | FFE | FQCL-186 | TROLLEY: laundry basket | 1 | 3 |  | [FQSM-030] optional
ADLL | ADL Laundry | Allied Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
ADLL | ADL Laundry | Allied Health | FFE | HYBA-411 | SINK: laundry, single bowl | 1 | 1 |  | [HYBA-064] with overflow drain, warm water
ADLL | ADL Laundry | Allied Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
ADLL | ADL Laundry | Allied Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059] with inset laundry tub
ADLL | ADL Laundry | Allied Health | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-222]
ADLL | ADL Laundry | Allied Health | FFE | JOCU-101 | CUPBOARD: wall mounted, single door | 1 | 1 |  | [FIJO-156]
ADLL | ADL Laundry | Allied Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 2 | 1 |  | [FIJO-135]
ADLL | ADL Laundry | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
ADLL | ADL Laundry | Allied Health | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
ADLL | ADL Laundry | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided
ADLL | ADL Laundry | Allied Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] flush set ceiling is also acceptable
ADLL | ADL Laundry | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
ADLL | ADL Laundry | Allied Health | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
ADLL | ADL Laundry | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
ADLL | ADL Laundry | Allied Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007]
ADLL | ADL Laundry | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to washing machine and dryer
ADLL | ADL Laundry | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] 30mA RCD protection
ADLL | ADL Laundry | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006] type 1 10mA in accordance with AS/NZS 3003
ADLL | ADL Laundry | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ADLL | ADL Laundry | Allied Health | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
ADLL | ADL Laundry | Allied Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] to washing machine
ADLL | ADL Laundry | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms
ADLL | ADL Laundry | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light, may be rationalised to central location if collocated with other ADL Rooms