## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
AHDR | After Hours Drug Store | Clinical Support Set 1 | Translation and QA Only | 5 | 2700 |  | 4 | 07.04.2026 |  | 24 hours | 1-2 staff intermittently | The After Hours Drug Store is a secure room for the storage of medications that may be required after hours. Stock is replenished by pharmacy personnel and, depending on the location of the room, there may be direct access from within the pharmacy. | ~ Secure access to the room for authorised personnel is required. ~ A duress alarm may be required if room accessed from a public or patient care area. ~ Refrigerated storage will be required for some medications. ~ Refer to project specific requirements for automated medication management systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] to corridor
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-007] optional, to pharmacy if room located with direct access
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to pharmacy side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
AHDR | After Hours Drug Store | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 2 | [ITSE-038]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | FQSM-211 | SHELVING UNIT: mobile, adjustable shelves, 600D x 400W x 2100H nominal | 2 | 1 |  | [FQSM-045] storage solution/mix of storage options to be tailored to suit project requirements
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 3 |  | [ITSE-012] optional, provision and placement dependent on local policies
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FFE | MMPH-021 | FRIDGE: medication/vaccine, 150L nom, single door, under bench | 1 | 1 |  | [MMGE-036]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
AHDR | After Hours Drug Store | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to drug fridge, for temperature monitoring
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 3 |  | [ITSE-006] optional
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
AHDR | After Hours Drug Store | Clinical Support Set 1 | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to drug fridge