## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | Translation and QA Only | 12 | 2700 |  | 3 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | The Airlock, 12m2 is a transitional space, typically associated with an entry area or waiting/reception area, which provides wind/weather protection and supports efficient temperature regulation within the building. Final configuration of the airlock will be dependent on site, internal layout and access requirements. | ~ The Airlock is intended to be used by a wide range of people including fully ambulant people, persons using a wide range of walking aids and persons in wheelchairs. ~ The Airlock may need to support the movement of beds/trolleys (e.g. at an ambulance or transit lounge entry) requiring a configuration that provides a relatively straight path of travel. ~ Additional area to accommodate door movement and circulation will be required if entry from multiple directions provided. ~ Extent of glazing to entry doors and airlock walls to be confirmed at project level to suit façade requirements and visual access from nearby reception or security areas. Wall materials shown are indicative and will be dependent on facade design and internal layout. ~ Motorisation of doors to be confirmed by project team to suit access requirements. ~ Access control may require the provision of swipe card readers, keypads, intercoms, push to open buttons (e.g. to exit after hours), door release buttons from nearby security or reception, etc. Provision of these items will depend on security requirements and operational policies (e.g. for after-hours access). Lockdown and emergency egress requirements must also be considered. A hold open function to the internal door will also typically be required for cleaning. ~ Flooring in the Airlock typically supports the capture of dirt and moisture at the building entry to reduce cleaning requirements. Floor finishes are to be specified/detailed to reduce the risk of trips, slips and falls, (e.g. minimise changes in finished height at transitions). Drainage requirements to floor matting must be considered. ~ Depending on layout and alignment of openings when the doors are open, an air curtain may be required to prevent the entry of draughts, insects, odours, etc. ~ At public/patient entries, the provision of culturally appropriate artwork (e.g. with film on glazing) may be considered to create a welcoming atmosphere. ~ Hand hygiene facilities, such as alcohol-based hand rub, should be provided nearby upon entry in line with local infection prevention and control (IPC) policies. It is not recommended that these items are provided within the airlock so the need for users to stop within the airlock is avoided and the path of travel is kept clear. ~ A small amount of concise signage may be required within the airlock. However, it is recommended that extensive wayfinding information is made readily accessible upon entry so the need for users to stop within the airlock is avoided and the path of travel is kept clear. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AFWFI-022 | WINDOW FINISH: decal | 1 | 1 | Internal - Door 1 | to fixed glazed panel, high visibility for safety and luminance contrast requirements
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AFWFI-022 | WINDOW FINISH: decal | 1 | 1 | External - Door 1 | to fixed glazed panel, high visibility for safety and luminance contrast requirements
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-051] inside airlock, to enter after hours
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-051] to adjacent internal area, to exit after hours
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-001 | BUTTON: door release, push to enter/exit, wall mounted | 1 | 1 | External - Door 1 | [ITSE-051] inside airlock, to exit after hours
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-101 | DOOR CONTROL: key switch, mode selection, automatic door | 1 | 1 | External - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDEC-101 | DOOR CONTROL: key switch, mode selection, automatic door | 1 | 1 | Internal - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDMO-011 | DOOR MOTORISATION: stacking, 1 leaf | 1 | 1 | Internal - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDMO-011 | DOOR MOTORISATION: stacking, 1 leaf | 1 | 1 | External - Door 1
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-012 | DOOR SENSOR: door activation, motion detection, integral to frame | 1 | 1 | Internal - Door 1 | to adjacent internal area
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-012 | DOOR SENSOR: door activation, motion detection, integral to frame | 1 | 1 | External - Door 1 | to adjacent external area
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-015 | DOOR SENSOR: door activation, motion detection, ceiling mounted | 1 | 1 | Internal - Door 1 | inside airlock
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | AHDSS-015 | DOOR SENSOR: door activation, motion detection, ceiling mounted | 1 | 1 | External - Door 1 | inside airlock
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | [CLGE-001] to external door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLBK-011 | BULKHEAD: flush set | 1 | 1 | Ceiling Finish 2 | [CLGE-001] to internal door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 3 | [CLFS-006]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | DOST-312.01 | DOOR: stacking, bi-parting, 2 leaves + 2 fixed panels, 1600 clear opening, fully glazed, framed with mid-rail | 1 | 1 | Internal - Door 1 | [DWGL-050] internal door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | DOST-312.01 | DOOR: stacking, bi-parting, 2 leaves + 2 fixed panels, 1600 clear opening, fully glazed, framed with mid-rail | 1 | 1 | External - Door 1 | [DWGL-050] external door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125] to security camera
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FFE | FIDI-055 | DISPENSER: umbrella cover, floor standing | 1 | 3 |  | [FIDI-055] optional
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | FLGE-081 | FLOOR FINISH: entrance matting, recessed, indoor | 1 | 1 | Floor Finish 2 | [FLGE-016]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | FLSK-031 | SKIRTING: aluminium, concealed fixing | 1 | 1 | Floor Skirting | [FLSK-008]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011] to security camera
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 1 |  | [ITSE-012+FIHR-002] as required for access control and security in line with local operational policies
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ITSE-191 | INTERCOM: audio-visual, slave, outdoor, wall mounted | 1 | 1 |  | [ITSE-049] as required for access control and security in line with local operational policies; may include integral swipe card reader; may be located to internal door
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | D+W | ITSE-266 | READER: security, access control, proximity card, outdoor, wall mounted | 1 | 1 | External - Door 1 | [ITSE-050] as required for access and security to suit operational policies; may be integral to intercom
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | ITSE-301 | ALARM: door release, emergency, break glass, wall mounted | 1 | 1 |  | [ITSE-024]
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | SER | MESU-006 | AIR CURTAIN: external door | 1 | 3 |  | [MEEX-018] optional
AIRLE-12 | Airlock - Entry, 12m2 | Public Areas | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]