## Room Template Data
Anaesthetic Preparation Room (ANAES) - Room Template Properties and Room Template Data
2025-05-08
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ANAES | Anaesthetic Preparation Room | 16 | ANAE-16 | 2 | 06.05.2025 | Up to 24 hours | FALSE |  |  |  |  | 1 patient; 1 parent; up to 3 staff | The Anaesthetic Preparation Room is for the holding and preparation of patients on a bed/trolley prior to their surgical procedure. Depending on operational processes, local, regional or general anaesthesia may be administered in this room or once the patient is taken into the Operating Room. Direct access to the Operating Room is required. | ~ Anaesthetic Preparation Rooms are typically provided to facilitate patient flow and support patient preparation. Provision to be determined during planning with consideration of local operational policies and patient throughput. ~ If serving an Operating Room with cardiac protected power, the Anaesthetic Preparation Room should also have cardiac protected power. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ Ready access is required from the Anaesthetic Preparation Room to shared support spaces such as medication fridges and blanket warmer bays. ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Anaesthetic Preparation Room. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Spout and tap placement at the handwashing basin should provide sufficient height to allow washing up to the elbow. The selection of handwashing basins and tapware should be coordinated and approved by clinical staff as a single unit. Type of spout to handwashing basin (i.e. gooseneck, straight, etc.) to be confirmed to suit local infection prevention and control policies. ~ Provision of an articulated examination light or ceiling recessed examination light to be conﬁrmed to suit service requirements. ~ Depending on the use of x-ray equipment within the adjacent Operating Room, radiation shielding may be required to this room and is to be assessed by a Radiation Consultant. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-05-08
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ANAES | Anaesthetic Preparation Room | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
ANAES | Anaesthetic Preparation Room | D+W | AHDMO-001 | DOOR MOTORISATION: swing | 1 | 1 | Internal - Door 1 | delayed action closing
ANAES | Anaesthetic Preparation Room | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2
ANAES | Anaesthetic Preparation Room | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
ANAES | Anaesthetic Preparation Room | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to operating room (see OR-GEN), cover required to vision panel if laser is to be used
ANAES | Anaesthetic Preparation Room | D+W | DOSL-212.01 | DOOR: sliding, bi-parting, 2 leaves, 1600 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | to corridor
ANAES | Anaesthetic Preparation Room | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | FFE | FIDI-261 | DISPENSER: soap, antiseptic, wall mounted | 1 | 1 |  | to basin
ANAES | Anaesthetic Preparation Room | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
ANAES | Anaesthetic Preparation Room | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 5 | 1
ANAES | Anaesthetic Preparation Room | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | HYTP-076 | TAPWARE: basin, sensor, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | ITCL-067 | CLOCK: electric, master clock system, slave, digital | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | computer may alternatively be on a bench top or wall mounted
ANAES | Anaesthetic Preparation Room | FFE | LIFX-122 | LIGHT: procedure, minor, articulated, ceiling mounted | 1 | 1 |  | a recessed ceiling examination light may be provided in lieu of small procedure light to suit service requirements
ANAES | Anaesthetic Preparation Room | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | MMOP-161 | MACHINE: anaesthetic | 1 | 1 |  | optional - may be provided within the anaesthetic preparation room or within the operating room (see OR-GEN)
ANAES | Anaesthetic Preparation Room | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | optional - drug safe may alternatively be located in the operating room; with card reader, safe location and type of medication stored is dependent on the operational policies and medication management regulations in different jurisdictions
ANAES | Anaesthetic Preparation Room | FFE | FIDI-251 | DISPENSER: alcohol-based hand rub, surgical, antimicrobial, chlorhexidine, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FQWS-072 | BIN: recycling, commingled, 30L | 1 | 1
ANAES | Anaesthetic Preparation Room | FFE | FQWS-237 | BIN: clinical waste, 120L | 1 | 1 |  | optional - provision dependent on waste management policy
ANAES | Anaesthetic Preparation Room | FFE | MMTR-013.01 | TROLLEY: stainless steel, wire mesh drawers, 900W x 490D x 900H nom, 3 drawers | 3 | 1
ANAES | Anaesthetic Preparation Room | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ANAES | Anaesthetic Preparation Room | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2
ANAES | Anaesthetic Preparation Room | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
ANAES | Anaesthetic Preparation Room | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10 / pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
ANAES | Anaesthetic Preparation Room | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
ANAES | Anaesthetic Preparation Room | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
ANAES | Anaesthetic Preparation Room | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2
ANAES | Anaesthetic Preparation Room | MSP | ELGP-146 | GPO: single, emergency power, on service panel | 3 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | ITCL-133 | BUTTON: patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | ITCL-251 | HANDSET: patient to staff call | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ANAES | Anaesthetic Preparation Room | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ANAES | Anaesthetic Preparation Room | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | MGFP-051 | ADAPTER: scavenge | 2 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ANAES | Anaesthetic Preparation Room | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 3 | 1
ANAES | Anaesthetic Preparation Room | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 3 | 1 |  | to bench
ANAES | Anaesthetic Preparation Room | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1
ANAES | Anaesthetic Preparation Room | SER | ITCL-181 | BUTTON: staff assist, with cancel, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | SER | ITCL-191 | BUTTON: emergency, with cancel, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | SER | ITCL-211 | BUTTON: orderly / porter, with cancel, wall mounted | 1 | 1 |  | optional - depending on operational processes
ANAES | Anaesthetic Preparation Room | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to telephone
ANAES | Anaesthetic Preparation Room | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to bench
ANAES | Anaesthetic Preparation Room | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1
ANAES | Anaesthetic Preparation Room | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
ANAES | Anaesthetic Preparation Room | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 1 | 1 |  | controlled from operating room
ANAES | Anaesthetic Preparation Room | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | controlled from operating room
ANAES | Anaesthetic Preparation Room | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
1BR-IC
1BR-BA