## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
ANCRT | Angiography Control/ Reporting Room | 14 |  | Up to 3 staff | Available 24 Hours | Acoustic privacy is required | Room adjacent to Angiography Procedure Room/s with direct visibility to the patient for remote control of equipment, and review and reporting of procedure images. The Control/ Reporting room may serve two procedure rooms. Acoustics: Acoustic privacy is required Additional Design Considerations: - Radiation shielding as advised by Radiation Consultant - Cable ducts from Angiography Procedure Room and Computer/Equipment room may be required

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
ANCRT | Angiography Control/ Reporting Room | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | Fabrics | 5060 | Ceiling - Acoustic | 1 |  | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | Fabrics | 7025 | Observation | 1 | to procedure room | Lead glass | Clear | Internal window | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | Fabrics | 8000 | Door protection | 1 |  | Vinyl | Prefinished | Kickplate, 300mm high | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | Fabrics | 9004 | Door - 1100mm | 1 | 910mm clear opening | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FE | FE-11400 | Computer - PC & monitor | 1 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FE | FE-35951 | Monitor (dual screen) | 1 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FE | FE-41100 | Printer - networked | 1 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FE | FE-54510 | Telephone - handset, standard | 2 | on bench |  |  |  | No | Yes | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FE | FE-62150 | IMG - console, control | 1 | Angiography control monitors |  |  |  | Yes | Yes | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-1050 | Bench - laminate | 3 | at 900H |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-16840 | Partitions - laminate | 2 | as required |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-17250 | Pedestal drawer unit - mobile, 660mmH | 1 | under bench |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-17360 | Pinboard - fabric covered | 3 | over bench |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-1950 | Chair - ergonomic, high | 3 |  |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-20000 | Shelving unit - adjustable | 6 | for books, manuals, over bench |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-24405 | Whiteboard - magnetic | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | FF | FF-3400 | Coathook | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-1006 | Voice / Data outlet: double | 6 | 3 outlets under bench for telephone |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-1040 | Intercom | 1 | with handsfree microphone to Angio room |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-6055 | Special: task light, built in | 4 | under O/H shelving |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-6200 | Light switches | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-9001 | GPO: Double | 9 |  |  |  |  | No | No | No | No | No | No | No | No | No
ANCRT | Angiography Control/ Reporting Room | SE | S-9060 | GPO: Special: for equipment | 1 | Angiography console equipment |  |  |  | No | No | No | No | No | No | No | No | No