## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
AUD-TR | Audiology Testing Room | Allied Health | Translation and QA Only | 14 | 2700 | AUDIO | 4 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | 1 patient; 1 carer / support person; 1-2 staff | The Audiology Testing Room provides an acoustically treated, soundproof space for clinical assessments to be carried out under controlled conditions. | ~ Testing Rooms may be modular proprietary items or constructed in situ and are generally designed as rooms within rooms in order to isolate the Testing Room from the rest of the building as much as possible. All designs should be reviewed and confirmed by an acoustic design expert. ~ The Audiology Testing Room currently indicates a layout (with an adjacent control room) that is suitable for paediatric testing. Layouts will vary to suit service requirements and the provided layout will need to be altered to suit services for older children and adults. ~ The audiometric booth is to be ventilated and connected to air-conditioning, power and data. Noise from mechanical services is to be minimised with air-conditioning to be designed for low noise operation to meet ambient noise requirements for testing. ~ The floor of the Treatment Room should be flush with the floor of the Control Room, or the adjacent corridor where a Control Room is not provided, for access by patients in wheelchairs. | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
AUD-TR | Audiology Testing Room | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to testing room side
AUD-TR | Audiology Testing Room | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to control room side
AUD-TR | Audiology Testing Room | Allied Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] acoustic seals to suit testing requirements
AUD-TR | Audiology Testing Room | Allied Health | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029] for headphones
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1 |  | [FQBS-014]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-161 | CHAIR: play areas, child | 1 | 1 |  | [FQBS-012]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQBS-251 | ARMCHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-039]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1 |  | [FQDW-001]
AUD-TR | Audiology Testing Room | Allied Health | FFE | FQTA-096 | TABLE: play areas, child | 1 | 1 |  | [FQTA-003]
AUD-TR | Audiology Testing Room | Allied Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
AUD-TR | Audiology Testing Room | Allied Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-145]
AUD-TR | Audiology Testing Room | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-201 | BOOTH: audiometric, integrated system | 1 | 1 |  | [MMAH-005] with one way window (non-reflective)
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-207 | SPEAKER: audiology, wall mounted | 2 | 1 |  | [ITAV-061] wall mounted, calibrated for testing space
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-211 | CONTROL CONSOLE: audiology, audiometric booth | 1 | 1 |  | [MMAH-036]
AUD-TR | Audiology Testing Room | Allied Health | FFE | MMAH-217 | DEVICE: audiology, visual reinforcement audiometry | 2 | 1 |  | [MMAH-043] wall mounted, may be provided as a screen or puppet box, inclusion is dependent on service requirements
AUD-TR | Audiology Testing Room | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
AUD-TR | Audiology Testing Room | Allied Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
AUD-TR | Audiology Testing Room | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208] provision of emergency power to be determined based on service requirements
AUD-TR | Audiology Testing Room | Allied Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
AUD-TR | Audiology Testing Room | Allied Health | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
AUD-TR | Audiology Testing Room | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
AUD-TR | Audiology Testing Room | Allied Health | SER | ITIN-151 | AV PANEL: power and data outlets, wall mounted | 4 | 3 |  | [MMSP-032] optional, as required for remote operation of equipment
AUD-TR | Audiology Testing Room | Allied Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]