## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BATH | Bathroom | Sanitary Facilities | Translation and QA Only | 15 | 2700 |  | 5 | 07.04.2026 |  | 24 hours | 1 patient;; 1-2 staff assisting | The Bathroom provides facilities for assisted bathing, dressing and grooming of patients. | ~ The layout is to allow for maneuvering of a patient on a lifting device, commode chair, wheelchair or shower trolley. ~ A height adjustable bath may be provided instead of a shower trolley depending on service requirements. ~ The location of the toilet should provide sufficient space on each side to allow for staff to provide assistance from either/both sides. ~ Grab rails are to be securely fixed to the wall with the structural support required to meet weight ratings/SWL that must be confirmed at project level (generally accommodating patients up to 150kg for standard patient spaces). Provision of structural support and FF&E that is suitable for supporting bariatric patients (typically up to 250kgs) may be considered and confirmed at a project level. ~ Signage with tactile Braille nominating 'Bathroom' required to room. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BATH | Bathroom | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
BATH | Bathroom | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
BATH | Bathroom | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
BATH | Bathroom | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
BATH | Bathroom | Sanitary Facilities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
BATH | Bathroom | Sanitary Facilities | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021] privacy latch
BATH | Bathroom | Sanitary Facilities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
BATH | Bathroom | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] over basin
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1 |  | [FIDI-049] soap dispenser is also acceptable, to shower
BATH | Bathroom | Sanitary Facilities | FFE | FIDI-308 | DISPENSER: toilet paper, to drop-down grab rail | 1 | 1 |  | [FIRT-008]
BATH | Bathroom | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-061 | TRACK: curtain, shower | 2 | 3 |  | [FIRT-034] 1 to entry door, 1 to shower; optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-137 | GRAB RAIL: toilet, drop down, with holder for toilet roll | 1 | 1 |  | [FIRT-008]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-138 | GRAB RAIL: toilet, drop down, with bracket for nurse call button | 1 | 1 |  | [FIRT-008]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-153 | GRAB RAIL: shower, straight, vertical | 1 | 1 |  | with bracket for hand held shower mounted on vertical rail
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-166 | GRAB RAIL: shower, T-shaped, vertical and horizontal | 1 | 1 |  | [FIRT-045] with bracket for hand held accessible shower mounted on vertical rail
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-191 | BACK REST: toilet, accessible | 1 | 1 |  | [FIGE-011]
BATH | Bathroom | Sanitary Facilities | FFE | FIRT-206 | RAIL: towel, wall mounted | 1 | 1 |  | [FIRT-016] with grab rail strength/fixings
BATH | Bathroom | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
BATH | Bathroom | Sanitary Facilities | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
BATH | Bathroom | Sanitary Facilities | FFE | FQGE-102 | CURTAIN: shower | 2 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
BATH | Bathroom | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
BATH | Bathroom | Sanitary Facilities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
BATH | Bathroom | Sanitary Facilities | FFE | HYBA-148 | BASIN: type C, handwashing, accessible, with integral double shelf | 1 | 1 |  | [HYBA-005] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
BATH | Bathroom | Sanitary Facilities | SER | HYDR-021 | DRAIN: floor waste, round | 2 | 1 |  | [HYDR-004] special floor drain required if height adjustable bath provided
BATH | Bathroom | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
BATH | Bathroom | Sanitary Facilities | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | [HYTP-020]
BATH | Bathroom | Sanitary Facilities | FFE | HYSH-057 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail, accessible | 1 | 1 |  | [HYTP-045]
BATH | Bathroom | Sanitary Facilities | FFE | HYTP-052 | TAPWARE: basin, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-035] selection of basin and tapware to be coordinated to ensure compatibility
BATH | Bathroom | Sanitary Facilities | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039]
BATH | Bathroom | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to shower
BATH | Bathroom | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to shower
BATH | Bathroom | Sanitary Facilities | FFE | HYWC-033 | TOILET SUITE: patient, accessible | 1 | 1 |  | [HYWC-001]
BATH | Bathroom | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
BATH | Bathroom | Sanitary Facilities | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-006] IPX4 rating required; to shower
BATH | Bathroom | Sanitary Facilities | SER | ITCL-130 | BUTTON: nurse call, patient to staff call, with cancel, to drop-down grab rail, wet area | 1 | 1 |  | [ITCL-006] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 0 | 1 |  | [ITCL-008] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-004] IPX4 rating required
BATH | Bathroom | Sanitary Facilities | FFE | MMBE-161 | TROLLEY: patient, shower, hydraulic | 1 | 1 |  | [FQSM-033] height adjustable bath is also acceptable
BATH | Bathroom | Sanitary Facilities | FFE | MMGE-024 | CHAIR: shower | 1 | 1 |  | [MMGE-024] commode chair is also acceptable
BATH | Bathroom | Sanitary Facilities | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 6 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable