## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | Full AHIA Review | 4 | 2700 |  | 2 | 31.03.2026 |  | Up to 24 hours | 1-2 patients / visitors intermittently;; 1 staff assisting as required | The Bay - Beverage, Mental Health is provided to allow consumers and support persons access to self-serve facilities for cold drinks and snacks (as determined by operational models for food service), including 24-hour access to chilled water. | ~ The Beverage Bay - Mental Health is typically collocated with consumer dining and lounge areas. ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ The temperature of hot water, if made available, should be suitable to prepare tea and coffee, with safety/locking mechanisms to control and staff only access to the water unit itself. ~ A side approach to the sink for wheelchair access has been shown; front access may be required and is to be determined at project level. ~ It is recommended that joinery is designed will finger pull edges for opening in lieu of fixed handles. Requirements for locks to cupboards and drawers are to be confirmed at project level to suit service requirements. ~ Locking/restricting access to beverage bays should be avoided where possible, but may be required depending on the service requirements of the unit. If access to the space is to be restricted, provision of an appropriate solution to enclose and lock the bay (such as roller shutter) is to be considered. Where roller shutters are provided, robustness must be considered, and design is to meet local work health and safety (WHS) requirements for manual handling of the door curtain. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ Size, type and quantity of waste bins is dependent on service requirements and environmental management policies for waste stream separation and frequency of waste removal. ~ Fridge dimensions will vary depending on the number of consumers, service requirements, operational models for food service and item selection. Adequate clear area must be provided for the fridge to allow for ventilation and full opening of door. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 25
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | to be coordinated with adjacent area
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELGP-101 | GPO: single, wall mounted | 2 | 1 |  | 1 to fridge, 1 to boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | optional; to be coordinated with lighting controls for adjacent area
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 1 | 1 | Floor Skirting
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10/pendulum P3 or agreed equivalent
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQCA-401 | FRIDGE: domestic, 120L nom, single door, under bench | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | size, type and quantity of waste bins will be dependent on service requirements and operational models for waste management
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | size, type and quantity of waste bins will be dependent on service requirements and operational models for waste management
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | filter unit to be in lockable cupboard; ventilation requirements to be confirmed to suit selection
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | to boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink tapware
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 2 | 1 |  | optional; extent of storage to be confirmed to suit service requirements; lockable
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | lockable; confirm ventilation requirements for boiling/chilled water unit
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 2 | 1 |  | lockable
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | optional; to wall mounted cupboards if provided
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2
BBEV-MH | Bay - Beverage, Mental Health | Mental Health | FIN | WLPR-006.04 | WALL PROTECTION: corner guards, to 1500 AFFL | 1 | 1 | Wall Finish 3 | to be coordinated with adjacent wall protection