## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BBEV | Bay - Beverage | Logistics / Support Services | Translation and QA Only | 4 | 2700 | BBEV-OP | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 persons intermittently;;; | The Beverage Bay is an area for preparation (including heating as required) of refreshments, snacks and small meals, washing some utensils, storing small mounts of food and drink and disposing of food waste (in accordance with food hygiene requirements). | ~ Beverage bays may allocated to patient care areas, staff areas and meeting/education facilities. ~ Ready access to a handwashing basin is recommended. ~ If an instantaneous boiling water tap/unit is provided, it should be hardwired and access restricted to the unit e.g. within cupboard. If system is located within a joinery unit, ensure appropriate ventilation is provided. ~ A side approach to the sink for wheelchair access has been shown; front access may be required depending on local/jurisdictional policies and service requirements. ~ The Beverage Bay should be adequately recessed to avoid encroachment into the corridor. If the space is to be enclosed and/or access is restricted, an increase in area is required. The door will require an observation panel. ~ Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. ~ Fridge dimensions will vary depending on selection and service requirements; clear area provided for the fridge is to allow for adequate ventilation and full opening of door ~ Provision and type of ice machine will be dependent on service requirements and local infection prevention and control policies. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BBEV | Bay - Beverage | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002] to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | SER | ELGP-101 | GPO: single, wall mounted | 3 | 1 |  | [ELGP-109] 1 to fridge, 1 to microwave, 1 to boiling/ chilled water unit
BBEV | Bay - Beverage | Logistics / Support Services | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] over bench
BBEV | Bay - Beverage | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, lighting and controls to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BBEV | Bay - Beverage | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10/pendulum P3 or agreed equivalent around sink; coordinated with adjacent area, significant change in colour to be avoided
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQCA-101 | APPLIANCE: microwave, benchtop, domestic | 1 | 1 |  | [FQCA-067]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQCA-231 | ICE MACHINE: commercial, benchtop | 1 | 3 |  | [FQCA-015] optional; item to comply with infection control requirements
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQCA-402 | FRIDGE: domestic, 300L nom, single door | 1 | 1 |  | [FQCA-032] clear area for fridge to allow for adequate ventilation and full opening of door
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] size, type and quantity of bins dependent on local waste management policies
BBEV | Bay - Beverage | Logistics / Support Services | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | [FQCW-062] size, type and quantity of bins dependent on local waste management policies
BBEV | Bay - Beverage | Logistics / Support Services | FFE | HYBA-304 | SINK: single bowl, with drainer, accessible | 1 | 1 |  | [HYBA-080]
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
BBEV | Bay - Beverage | Logistics / Support Services | FFE | HYGE-111 | WATER SYSTEM: filter unit and tap, boiling/chilled | 1 | 1 |  | [HYGE-003] + [HYTP-029] instant hot/cold water tap to sink; provide grille in joinery for ventilation
BBEV | Bay - Beverage | Logistics / Support Services | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] to boiling/ chilled water unit
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
BBEV | Bay - Beverage | Logistics / Support Services | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-069] minimum depth 600mm; where an ice machine is provided the depth may need to increase to accommodate
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOCU-041 | CUPBOARD: tall, with 1 microwave shelf unit | 1 | 1 |  | [FIJO-163]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 3 |  | [FIJO-143] optional; configuration of joinery to meet storage requirements
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 2 | 1 |  | [FIJO-104]
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
BBEV | Bay - Beverage | Logistics / Support Services | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | [FIJO-212] optional, provide if wall mounted joinery provided, plasterboard bulkhead is also acceptable
BBEV | Bay - Beverage | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BBEV | Bay - Beverage | Logistics / Support Services | FIN | WLFI-101 | SPLASHBACK: vinyl | 2 | 1 | Wall Finish 2 | [WLWA-007] to back of bench and return wall
BBEV | Bay - Beverage | Logistics / Support Services | FIN | WLPR-006.01 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | 1 | Wall Protection | [WLPR-010] coordinated with adjacent wall protection