## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BBW | Bay - Blanket / Fluid Warmer | Perioperative | Translation and QA Only | 1 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | The Bay - Blanket / Fluid Warmer provides clear area and services for a single warming cabinet. The warming cabinet may be for fluids only, blankets only or a combination of fluids and blankets. | ~ Collocation of blanket warming cabinets with linen bays is common and supports efficient workflows. ~ Locating the bay with ready access to patient areas or operating/procedure areas is recommended. ~ The capacity of warming cabinets varies and must be considered in relation to the area/number of patients to be served. The throughput of patients must also be considered as a higher turnover will require higher capacity/additional cabinets. ~ Warming cabinet sizes vary and the clear area of the bay is to suit the dimensions of the equipment selected as well as ensuring adequate space for ventilation as per manufactures specifications. The bay should deep enough to ensure that the warming cabinet itself does not impede adjacent corridor circulation. Clearance to be provided in adjacent circulation space to allow for opening of the door for intermittent use and restocking. Where fluids are kept, processes for labelling fluids need to be accommodated without impeding circulation. ~ Various cabinet configurations, including benchtop, under bench, freestanding, mobile and built-in cabinets may be selected. See manufacturer's specifications for installation requirements. ~ Temperatures for fluids need to be monitored. A data outlet, or alternative connection to suit project/equipment requirements, may be required for connection the Building Management System (BMS) depending on provision of fluid warming. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FFE | MMGE-473 | CABINET: fluid/blanket warmer, floor standing | 1 | 1 |  | [MMGE-010] for fluids only, blankets only or a combination of fluids and blankets; configuration to suit service requirements
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] square set cornice acceptable if flush set ceiling is provided; coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] flush set ceiling is also acceptable; to be coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BBW | Bay - Blanket / Fluid Warmer | Perioperative | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BBW | Bay - Blanket / Fluid Warmer | Perioperative | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
BBW | Bay - Blanket / Fluid Warmer | Perioperative | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional; provide for connection to BMS where temperature monitoring required for fluids; alternative connection may be required depending on BMS or equipment requirements