## Room Data
Standard Components - Room Data Sheet
Date of issue: 12.07.2023
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
BIRM-B | Birthing Room, With Pool | 40.5 | 24 Hours | 1 mother; 1-2 support persons; up to 4 staff |  | Sound attenuation level high, Acoustic privacy is required. | The Birthing Room - With Pool provides area and amenities for the entire birthing process including mother's preparation, active birthing exercises, water immersion during labour, relaxation and analgesia during labour, birthing, infant resuscitation, postnatal recovery and observation. The room includes an active birthing/bed zone, birthing pool an area to accommodate a support person, a staff observation and write up area, an infant resuscitation area, an equipment store, and a hand hygiene area with type A handwashing basin. Birthing Pool: The use of birthing pools should be based on local policies and protocols for water immersion during labour and birth. Birthing pools can vary significantly in shape and the pool shown on the RLS is indicative only. Final selection may have implications for required area and clearances. The birthing pool must be deep and wide enough for effective water immersion for pain relief during labour and birth. Ergonomic assessment of birthing pool options should be undertaken prior to selection, including the height of the pool for mothers getting into and out of the pool, as well as access for staff assisting the mother from the side of the pool. The location of grabrails and supports, including those integral with the bath design are to be considered to support transfers without impeding access to the mother by staff. Pools may be installed with steps built around them to provide easy access into the pool from a seated position. Provision of stairs is to be assessed to ensure they do not limit access with floatation transfer devices in the event of an emergency. Handrails to be provided to stairs to reduce risk of slips in wet area around the pool. A ceiling mounted hoist has not been included as there are better and more timely ways to remove a mother from the birthing pool should her condition deteriorate. Consideration for ready access to floatation devices for transfer from the pool is required. The tapware and drain for the birthing pool are to be carefully considered. Taps need to allow the bath to be filled rapidly. Water also needs to be able to be drained quickly, preferably without needing to reach into the bath after birthing. Additional Considerations: The room will have direct access to an Ensuite - Birthing. Air should not be recirculated to other areas from the Birthing Room. Negative pressure air conditioning is required for clearance of anaesthetic gases. Clinical items such as medical gases and services as well as neonatal resuscitation equipment may be concealed to support the provision of a calm environment. Even while concealed, items are to be within easy reach of the active birthing zone. The availability of proprietary items for in-room infant resuscitation may change and this can inform the use of built in or mobile equipment. Overall dimensions and configuration of storage for the resuscitaire equipment are to be evaluated based on the selection of equipment and it is recommended that a test-fit is conducted, ensuring appropriate clearances are provided for emergency procedures to be undertaken, in order to confirm room layout requirements. Equipment storage to be configured to suit service requirements including models for sharing equipment between multiple rooms. Storage requirements within the room will vary between facilities depending on models of centralising or decanting and restocking consumables. Configuration and extent of storage to be determined based on service requirements. Various supportive fixtures for active birthing are to be considered, for example, a wall mounted ladder, bench or mantlepiece for support and leaning, or ceiling mounted hooks for supportive fabrics to be hung. Consider mounting heights and providing support for various postures at multiple heights. A mother's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. A fixed workstation for staff write-up and observation has been shown. Sufficient space for dual monitors may be provided as required to suit operational, EMR and ICT requirements. A workstation on wheels is also acceptable. An examination light is required for suturing and small procedures. It is preferred that the light be as unobtrusive as possible and be able to be pushed away so that it is not dominating the area. Lighting options to be provided, including dimmable room lighting, reading lights and night lights to provide flexible lighting across the space. Coloured lighting and calming light artworks may be considered by projects. Systems, including portable items, to facilitate the selection and control of music by the mother are to be considered. Acoustics treatment may be required to support this without disruption to adjacent rooms. Provision of a telephone for patient use will be dependent on the operational model for transferring calls. Natural light and outlook essential. Window sill to be low enough to see view while laying in bed. Treatment, to windows to allow blinds to be kept open as desired but privacy to be maintained, may need to be considered depending on overlook from nearby buildings.

## Items
Standard Components - Items in room
Date of issue: 12.07.2023
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
BIRM-B | Birthing Room, With Pool | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
BIRM-B | Birthing Room, With Pool | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
BIRM-B | Birthing Room, With Pool | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to birthing pool
BIRM-B | Birthing Room, With Pool | FA | WLPR-006 | WALL PROTECTION: corner guards | 2
BIRM-B | Birthing Room, With Pool | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
BIRM-B | Birthing Room, With Pool | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
BIRM-B | Birthing Room, With Pool | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
BIRM-B | Birthing Room, With Pool | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1
BIRM-B | Birthing Room, With Pool | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
BIRM-B | Birthing Room, With Pool | FA | DWWH-005 | WINDOW | 2
BIRM-B | Birthing Room, With Pool | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | with hold open device to support bed movement as required
BIRM-B | Birthing Room, With Pool | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
BIRM-B | Birthing Room, With Pool | FA | DWGE-017 | DOOR: concertina folding leaf | 1 | 1800 wide
BIRM-B | Birthing Room, With Pool | FFE | MGFP-002 | FLOWMETER: medical air | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | FFE | FQBS-001 | BASSINET | 1 | optional
BIRM-B | Birthing Room, With Pool | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1
BIRM-B | Birthing Room, With Pool | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | mounted on trolley
BIRM-B | Birthing Room, With Pool | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | FFE | DWWD-004 | BLIND: roller | 2
BIRM-B | Birthing Room, With Pool | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
BIRM-B | Birthing Room, With Pool | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
BIRM-B | Birthing Room, With Pool | FFE | FIDI-019 | DISPENSER: gown/apron | 1
BIRM-B | Birthing Room, With Pool | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1
BIRM-B | Birthing Room, With Pool | FFE | FIDI-014 | DISPENSER: disposable glove | 2 | 1 to basin, 1 to room
BIRM-B | Birthing Room, With Pool | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 | type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | FFE | FQBS-044 | LOUNGE: 2 seat, sofa bed | 1
BIRM-B | Birthing Room, With Pool | FFE | FQTA-013 | TABLE: overbed | 1
BIRM-B | Birthing Room, With Pool | FFE | MGFP-004 | FLOWMETER: oxygen | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | FFE | MMMA-011 | MIXER: oxygen and nitrous oxide | 1
BIRM-B | Birthing Room, With Pool | FFE | FIJO-194 | SHELF: laminate | 2 | to equipment store cupboard, type and quantity of storage options to be determined based on service requirements
BIRM-B | Birthing Room, With Pool | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | for suturing and small procedures
BIRM-B | Birthing Room, With Pool | FFE | MMGE-002 | ADAPTER: suction | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | FFE | MMGE-100 | SUCTION BOTTLE | 2 | 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | FFE | FQSM-016 | TROLLEY | 1 | to equipment store cupboard
BIRM-B | Birthing Room, With Pool | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
BIRM-B | Birthing Room, With Pool | FFE | MMBE-005 | BED: patient, birthing, electric | 1
BIRM-B | Birthing Room, With Pool | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin
BIRM-B | Birthing Room, With Pool | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
BIRM-B | Birthing Room, With Pool | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | to staff write-up, dual monitors may be provided as required to suit operational, EMR and ICT requirements; a workstation on wheels is also acceptable
BIRM-B | Birthing Room, With Pool | FFE | MMMA-015 | RESUSCITAIRE: infant, mobile | 1
BIRM-B | Birthing Room, With Pool | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
BIRM-B | Birthing Room, With Pool | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2 | 1 to shower, 1 to spout for birthing pool
BIRM-B | Birthing Room, With Pool | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | optional, to patient locker
BIRM-B | Birthing Room, With Pool | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | FFE | FIJO-129 | CUPBOARD: tall, single door, adj shelves | 1 | type and extent of storage to suit service requirements
BIRM-B | Birthing Room, With Pool | FFE | HYTP-021 | SHOWER: hand-held, over bath | 1
BIRM-B | Birthing Room, With Pool | FFE | HYBA-023 | BATH: birthing | 1 | Birthing pools can vary significantly in shape and the pool shown is indicative only. Final selection will have implications for required area and clearances. Ergonomic assessment of birthing pool options should be undertaken prior to selection.
BIRM-B | Birthing Room, With Pool | FFE | FIJO-099 | CAC: cable access cap | 1
BIRM-B | Birthing Room, With Pool | FFE | FIJO-162 | CUPBOARD: tall, single door, to conceal services | 1
BIRM-B | Birthing Room, With Pool | FFE | FIJO-209 | CUPBOARD: tall, single door, adj shelves and clothes rail, recessed | 1 | wardrobe, type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | FFE | FIJO-212 | BULKHEAD: joinery | 5
BIRM-B | Birthing Room, With Pool | FFE | FIHR-068 | BRACKET: for alcohol based hand rub, attached to bed | 1
BIRM-B | Birthing Room, With Pool | FFE | MMMA-019 | SUPPORT FIXTURE: birthing, ladder, wall mounted, wet area | 1
BIRM-B | Birthing Room, With Pool | FFE | MMMA-031 | DEVICE: patient, fetal, cardiotocography (CTG), on trolley | 1 | to equipment store cupboard
BIRM-B | Birthing Room, With Pool | FFE | MMMA-043 | SUPPORT FIXTURE: birthing, hook, ceiling mounted | 1 | optional, provision dependent on birthing aids/supportive equipment to be used
BIRM-B | Birthing Room, With Pool | FFE | FIJO-233 | CUPBOARD: tall, infant resuscitaire | 1
BIRM-B | Birthing Room, With Pool | FFE | HYTP-048 | SPOUT: birthing pool, high flow, wall mounted | 1
BIRM-B | Birthing Room, With Pool | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to staff write-up for wall mounted phone
BIRM-B | Birthing Room, With Pool | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to staff write-up
BIRM-B | Birthing Room, With Pool | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | ELPR-006 | RCD: residual current device | 5 | 3 to bedhead, 2 to infant resuscitaire
BIRM-B | Birthing Room, With Pool | SE | ITIN-070 | OUTLET: MATV | 1 | to patient entertainment system, may be replaced with data outlet depending on ICT policies
BIRM-B | Birthing Room, With Pool | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | to patient entertainment system
BIRM-B | Birthing Room, With Pool | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | with indicator button and light, 1 to bedhead, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | HYDR-004 | DRAIN: floor waste | 1 | to birthing pool area
BIRM-B | Birthing Room, With Pool | SE | LIFX-011 | LIGHT: reading light | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | LIFX-017 | LIGHT: night light | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | ELBO-015 | SWITCH: light, single | 1 | to bedhead for reading light
BIRM-B | Birthing Room, With Pool | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | to infant resuscitaire
BIRM-B | Birthing Room, With Pool | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to infant resuscitaire
BIRM-B | Birthing Room, With Pool | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to infant resuscitaire
BIRM-B | Birthing Room, With Pool | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | with indicator button and light
BIRM-B | Birthing Room, With Pool | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light, 1 to bedhead, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level for patient bed
BIRM-B | Birthing Room, With Pool | SE | ELGP-208 | GPO: double, wall mounted | 3 | 2 to staff write-up, 1 to lounge
BIRM-B | Birthing Room, With Pool | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 4 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
BIRM-B | Birthing Room, With Pool | SE | ELPR-001 | BODY PROTECTED ELECTRICAL AREA | 1
BIRM-B | Birthing Room, With Pool | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
BIRM-B | Birthing Room, With Pool | SE | ITSE-006 | BUTTON: duress, fixed | 2 | 1 to staff write-up, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | MMSP-026 | SERVICES PANEL: wall mounted | 6 | 3 to bedhead, 1 to infant resuscitaire, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | SE | ELBO-012 | SWITCH: light, dimmer | 1 | 1 to entry door, 1 to staff write up for general room lights
BIRM-B | Birthing Room, With Pool | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | to birthing pool
BIRM-B | Birthing Room, With Pool | SE | ELGP-205 | GPO: double, on services panel | 2 | to infant resuscitaire
BIRM-B | Birthing Room, With Pool | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2 | to infant resuscitaire
BIRM-B | Birthing Room, With Pool | SE | MGAS-033 | OUTLET: nitrous oxide (N2O), wall mounted | 1 | to birthing pool
BIRM-B | Birthing Room, With Pool | SE | MGAS-055 | OUTLET: scavenge, wall mounted | 1 | to birthing pool
BIRM-B | Birthing Room, With Pool | SE | ELGP-109.1 | GPO: single, wall mounted (V) | 4 | to bedhead
BIRM-B | Birthing Room, With Pool | SE | HYGE-028 | DEVICE: backflow prevention | 1 | to birthing pool area