## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BIRM-B | Birthing Room, With Pool | Maternity | Translation and QA Only | 40.5 | 2700 |  | 2 | 07.04.2026 |  | 24 hours | 1 mother; 1-2 support persons; up to 4 staff | The Birthing Room - With Pool provides area and amenities for the entire birthing process including mother's preparation, active birthing exercises, water immersion during labour, relaxation and analgesia during labour, birthing, infant resuscitation, postnatal recovery and observation. The room includes an active birthing/bed zone, birthing pool an area to accommodate a support person, a staff observation and write up area, an infant resuscitation area, an equipment store, and a hand hygiene area with type A handwashing basin. | Birthing Pool: ~ The use of birthing pools should be based on local policies and protocols for water immersion during labour and birth. ~ Birthing pools can vary significantly in shape and the pool shown on the RLS is indicative only. Final selection may have implications for required area and clearances. ~ The birthing pool must be deep and wide enough for effective water immersion for pain relief during labour and birth. ~ Ergonomic assessment of birthing pool options should be undertaken prior to selection, including the height of the pool for mothers getting into and out of the pool, as well as access for staff assisting the mother from the side of the pool. The location of grabrails and supports, including those integral with the bath design are to be considered to support transfers without impeding access to the mother by staff. ~ Pools may be installed with steps built around them to provide easy access into the pool from a seated position. Provision of stairs is to be assessed to ensure they do not limit access with floatation transfer devices in the event of an emergency. Handrails to be provided to stairs to reduce risk of slips in wet area around the pool. ~ A ceiling mounted hoist has not been included as there are better and more timely ways to remove a mother from the birthing pool should her condition deteriorate. ~ Consideration for ready access to floatation devices for transfer from the pool is required. ~ The tapware and drain for the birthing pool are to be carefully considered. Taps need to allow the bath to be filled rapidly. Water also needs to be able to be drained quickly, preferably without needing to reach into the bath after birthing. Other Considerations: ~ The room will have direct access to an Ensuite - Birthing. ~ Air should not be recirculated to other areas from the Birthing Room. Negative pressure air conditioning is required for clearance of anaesthetic gases. ~ Clinical items such as medical gases and services as well as neonatal resuscitation equipment may be concealed to support the provision of a calm environment. Even while concealed, items are to be within easy reach of the active birthing zone. ~ The availability of proprietary items for in-room infant resuscitation may change and this can inform the use of built in or mobile equipment. Overall dimensions and configuration of storage for the resuscitaire equipment are to be evaluated based on the selection of equipment and it is recommended that a test-fit is conducted, ensuring appropriate clearances are provided for emergency procedures to be undertaken, in order to confirm room layout requirements. ~ Equipment storage to be configured to suit service requirements including models for sharing equipment between multiple rooms. ~ Storage requirements within the room will vary between facilities depending on models of centralising or decanting and restocking consumables. Configuration and extent of storage to be determined based on service requirements. ~ Various supportive fixtures for active birthing are to be considered, for example, a wall mounted ladder, bench or mantlepiece for support and leaning, or ceiling mounted hooks for supportive fabrics to be hung. Consider mounting heights and providing support for various postures at multiple heights. A mother's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. ~ A fixed workstation for staff write-up and observation has been shown. Sufficient space for dual monitors may be provided as required to suit operational, EMR and ICT requirements. A workstation on wheels is also acceptable. ~ An examination light is required for suturing and small procedures. It is preferred that the light be as unobtrusive as possible and be able to be pushed away so that it is not dominating the area. ~ Lighting options to be provided, including dimmable room lighting, reading lights and night lights to provide flexible lighting across the space. Coloured lighting and calming light artworks may be considered by projects. ~ Systems, including portable items, to facilitate the selection and control of music by the mother are to be considered. Acoustics treatment may be required to support this without disruption to adjacent rooms. ~ Provision of a telephone for patient use will be dependent on the operational model for transferring calls. ~ Natural light and outlook essential. Window sill to be low enough to see view while laying in bed. Treatment, to windows to allow blinds to be kept open as desired but privacy to be maintained, may need to be considered depending on overlook from nearby buildings. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 1 | [DWWD-004]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 2 | [DWWD-004]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | DOFD-301 | DOOR: folding, bi-parting, 4 leaves, 1800 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWGE-017] to equipment storage area
BIRM-B | Birthing Room, With Pool | Maternity | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] with hold open device to support bed movement as required
BIRM-B | Birthing Room, With Pool | Maternity | D+W | WIFX-108.01 | WINDOW: fixed, external, single glazed, sill at 1050H | 1 | 1 | External - Window 2 | [DWWH-005]
BIRM-B | Birthing Room, With Pool | Maternity | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1 |  | [FIDI-014]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-019]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-247 | HOLDER: alcohol-based hand rub, bed mounted | 1 | 1 |  | [FIHR-068]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019] 1 to bedhead, 1 to resuscitaire
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016] mounted on trolley
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051] for suturing and small procedures
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQBS-372 | SOFA BED: 2 seat | 1 | 1 |  | [FQBS-044]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQSN-101 | BEDSIDE TABLE: floor standing, patient locker | 1 | 1 |  | [FQSN-051] type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYBA-281 | POOL: birthing, back to wall | 1 | 1 |  | [HYBA-023] birthing pools can vary significantly in shape and the pool shown is indicative only. Final selection will have implications for required area and clearances. Ergonomic assessment of birthing pool options should be undertaken prior to selection.
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 1 | 1 |  | [HYTP-021] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039] 1 to shower, 1 to spout for birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FFE | HYTP-381 | TAPWARE: birthing pool, spout, high flow, wall mounted | 1 | 1 |  | [HYTP-048]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | [ITNE-049] optional, to patient locker
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] to staff write-up, dual monitors may be provided as required to suit operational, EMR and ICT requirements; a workstation on wheels is also acceptable
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-020]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOBE-221 | BENCH SUPPORT: end panel | 2 | 1 |  | [FIJO-213] 1 below FIJO-156 to separate dirty linen trolley from hand wash, storage for clean and dirty linen to suit local operational policies, 1 below write-up bench
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099] to staff write-up bench
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-001 | CUPBOARD: tall, single door | 1 | 1 |  | [FIJO-129] type and extent of storage to suit service requirements
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-006 | CUPBOARD: tall, single door, for medical services panel | 1 | 1 |  | [FIJO-162]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-145] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | [FIJO-209] wardrobe, type and extent of storage for patient property to suit operational policies
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOGE-001 | BULKHEAD: joinery | 5 | 1 |  | [FIJO-212]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOSH-401 | SHELF: wall mounted, laminate | 2 | 1 |  | [FIJO-194] to equipment store cupboard, type and quantity of storage options to be determined based on service requirements
BIRM-B | Birthing Room, With Pool | Maternity | FFE | JOSP-001 | JOINERY UNIT: bespoke, birthing, tall, infant resuscitaire storage | 1 | 1 |  | [FIJO-233] Configuration of joinery to suit resuscitare equipment selected, including consideration of maneuverability and provision of sufficient space for emergency resuscitation procedures. Confirm design with users at project level.
BIRM-B | Birthing Room, With Pool | Maternity | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMBE-126 | BED: patient, electric, with mattress, birthing | 1 | 1 |  | [MMBE-005]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100] 1 to bedhead cupboard, 1 to resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-031 | BASSINET: infant, mobile | 1 | 3 |  | [FQBS-001] optional
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-051 | DEVICE: patient, fetal, cardiotocography (CTG) | 1 | 1 |  | [MMMA-031] to equipment store cupboard
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-061 | RESUSCITAIRE: infant, mobile | 1 | 1 |  | [MMMA-015]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-116 | SUPPORT FIXTURE: birthing, ladder, wall mounted | 1 | 1 |  | [MMMA-041]
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMMA-121 | SUPPORT FIXTURE: birthing, hook, ceiling mounted | 1 | 3 |  | [MMMA-043] optional, provision dependent on birthing aids/supportive equipment to be used
BIRM-B | Birthing Room, With Pool | Maternity | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 1 |  | [FQSM-016] to equipment store cupboard
BIRM-B | Birthing Room, With Pool | Maternity | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
BIRM-B | Birthing Room, With Pool | Maternity | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 2 | [FLVY-009] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-010] to basin
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-002]
BIRM-B | Birthing Room, With Pool | Maternity | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 5 | 1 | Panel 1 | [ELGP-122]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2 | [ELGP-122]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 6 | 1 | Panel 3 | [ELGP-122]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2 | [ELPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 1 | [ELPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 2 | 1 | Panel 3 | [ELPR-006]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | [ELBO-015] to reading light
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] with indicator button and light
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] with indicator button and light
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Panel 1 | [ITCL-028]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 2 | [ITIN-025]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 3 | [ITIN-025]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 2 | [MGAS-022]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 3 | [MGAS-022]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 2 | [MGAS-032]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 4 | [MGAS-032]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 2 | [MGAS-042]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 3 | [MGAS-042]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 4 | [MGAS-042]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 2 | [MGAS-053]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 4 | [MGAS-053]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2 | [MGAS-062]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 3 | [MGAS-062]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 3 | [MGFP-002]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 2 | [MGFP-002]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2 | [MGFP-004]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 3 | [MGFP-004]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 4 | [MGFP-004]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Panel 4 | [MMGE-001]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Panel 2 | [MMGE-001]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2 | [MMGE-002]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 3 | [MMGE-002]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MGFP-082 | BLENDER: oxygen (O2) and nitrous oxide (N20) | 1 | 1 | Panel 2 | [MMMA-011]
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026] to bedhead
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | [MMSP-026] to bedhead cupboard
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 3 | [MMSP-026] to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 4 | [MMSP-026] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] low level for patient bed
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-106.01 | GPO: single, ceiling mounted, horizontal | 1 | 1 |  | [ELGP-101] to patient entertainment system
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-131.01 | GPO: single, emergency power, wall mounted, horizontal | 1 | 1 |  | [ELGP-123]
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] 2 to staff write-up, 1 to lounge
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] to infant resuscitaire cupboard
BIRM-B | Birthing Room, With Pool | Maternity | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | [ELBO-012] 1 to entry door, 1 to staff write up for general room lights
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] to birthing pool area
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028] to birthing pool area
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to birthing pool tapware
BIRM-B | Birthing Room, With Pool | Maternity | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to birthing pool tapware
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] to bedhead
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to staff write-up for wall mounted phone
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to staff write-up
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment system, may be replaced with data outlet depending on ICT policies
BIRM-B | Birthing Room, With Pool | Maternity | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 2 | 1 |  | [ITSE-006] 1 to staff write-up, 1 to birthing pool
BIRM-B | Birthing Room, With Pool | Maternity | SER | LIFX-151 | LIGHT: night, wall mounted | 1 | 1 |  | [LIFX-017] to bedhead
BIRM-B | Birthing Room, With Pool | Maternity | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011] to bedhead