## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | Translation and QA Only | 4 | 2700 | BMEQ-4 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | An open bay for storage and recharging frequently used mobile equipment. Equipment may include wheelchairs, mobile scales, commode chairs, patient lifting devices or observation/diagnostic equipment. | ~ The bay should deep enough to ensure that equipment does not impede adjacent corridor circulation; a depth range from 800mm to 1500mm is recommended. Consider the manoeuverability of equipment to be stored as some items may have large turning circles and will need to be parked perpendicular, requiring a deeper bay. Power outlets may be located on the sides of deeper bays to be accessible when equipment is parked. ~ If portable imaging equipment is to be stored additional area may be required. Data outlets may be required depending on equipment. ~ Equipment may be recharged while stored in this space; provision of appropriately located power outlets is required. ~ Items may be hung in this bay, e.g. a patient slide, and appropriate in-wall supports are required for mounting hooks. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 3 |  | [FIHR-030] optional
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 3 |  | [MMBE-042] optional
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-020] height dependent on type and height of mobile equipment, crash rails are also acceptable
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | FIN | WLPR-006 | WALL PROTECTION: corner guards | 1 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BMEQ | Bay - Mobile Equipment | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] type, quantity and configuration of outlets to be determined based on equipment requirements