## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | Translation and QA Only | 3 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Bay - Pathology Point of Care Testing (POCT) provides the area and facilities for the preparation and testing of specimens close to patient care areas allowing for rapid results to improve clinical decision making and patient care. | ~ Two benchtop POCT devices have been indicated, with additional devices requiring added space and services. The devices shown are placeholders as there are many POCT devices available and various combinations of devices may be provided depending on the service requirements of the unit in which this bay is located. ~ Ready access to handwashing bay is recommended. ~ Ready access may be required to a pneumatic tube bay that is in a staff supervised area. ~ If providing wall mounted joinery over the bench consider clearance heights for benchtop machines, including for futureproofing. ~ Weight requirements for machines should be considered to ensure adequate support is provided to the bench. ~ POCT devices should not to be located in direct sunlight as they can overheat. ~ Refrigerator temperature monitoring may be required and is to be connected to the building management system (BMS). The alarm is to provide alerts where 24-hour monitoring is undertaken, within the unit and/or remotely. ~ Type and extent of storage to suit testing requirements, including ambient temperature storage for cartridges. ~ Ensure adequate lighting over workspace. ~ Power requirements (type/quantity) to be considered to suit equipment and service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044] with wide opening
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] quantity and type of bins to be based on local waste management policies
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005] quantity and type of bins to be based on local waste management policies
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049] may be wall mounted
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 3 |  | [ITNE-003] optional, dependent on software requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-056]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-069] laboratory grade
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141] lockable; extent of storage to suit testing requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106] lockable; extent of storage to suit testing requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | MMLA-003 | DEVICE: analyser, blood gas, point of care | 2 | 1 |  | [MMLA-049] quantity and type to suit service requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FFE | MMLA-201 | FRIDGE: laboratory, 150L nom, single door, under bench | 1 | 1 |  | [MMLA-055] lockable; temperature monitored
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | WLFI-116 | SPLASHBACK: laminate, prefinished | 3 | 1 | Wall Finish 2 | [WLWA-009] coved, integral to bench
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 5 | 1 |  | [ELGP-223] quantity to suit project specific equipment requirements, confirm UPS requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITBU-401 | ALARM: equipment monitoring, temperature | 1 | 1 |  | [ITBU-001] to fridge, dependent on requirements, may be integral to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to fridge
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026] quantity to suit project specific equipment requirements
BPATH | Bay - Pathology Point of Care Testing (POCT) | Pathology | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] to computer