## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BPTS | Bay - Pneumatic Tube Station | Pathology | Translation and QA Only | 1 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed by staff intermittently | The Bay - Pneumatic Tube Station (PTS) provides an area for dispatching and receiving of items via the pneumatic tube system. | ~ This Standard Component represents a department based bay and additional area, FFE and services will be required for a central receiving and processing area in a pathology or pharmacy department. ~ To be collocated or located with clear oversite from a staff station or within a staff only area. ~ Arrival notification alarms must be programmable for different times and scenarios depending on service requirements. ~ Security requirements are to be considered. If the station is to receive deliveries from Pharmacy or is in an area accessed by the public then secure access to a lockable receiving basket may be required depending on location of the bay. ~ Station may be a pass through or end station and receive/dispatch through the floor or ceiling depending on location and system configuration. ~ Radio frequency identification (RFID) technology may be considered by projects to reduce errors, improve traceability and to enable dynamic/intuitive routing to reduce "traffic jams". This technology involves embedded RFID tags in cannisters that are read by receivers at tube stations on dispatch/arrival and at interchange points in the system. ~ Where multiple services send/receive products via the pneumatic tube system, e.g. pathology and pharmacy, colour coding the cannisters for the different streams is recommended. Colour coding to differentiate between cannisters from high priority areas, e.g. emergency and intensive care vs general wards may also be considered. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-451 | STATION: pneumatic tube | 1 | 1 |  | [MMGE-097] with audible alarm
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-452 | BASKET: pneumatic tube | 1 | 1 |  | [FQSN-001] may be lockable depending on location, service and security requirements
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-453 | RACK: pneumatic tube, canister | 1 | 1 |  | [MMLA-072] quantity to suit service requirements
BPTS | Bay - Pneumatic Tube Station | Pathology | FFE | MMGE-454 | LIGHT: pneumatic tube, alert light | 1 | 1 |  | [LIFX-015]
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BPTS | Bay - Pneumatic Tube Station | Pathology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BPTS | Bay - Pneumatic Tube Station | Pathology | SER | ELGE-001 | DIRECT CONNECTION: power | 1 | 1 |  | [ELGE-001] direct connection to station