## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | Translation and QA Only | 1.5 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | accessed intermittently;;; | A open bay to provide supervised holding of the resuscitation trolley and associated equipment. The bay should be located close to a Staff Station. Rapid access to the trolley and from this bay to patient areas is essential. | ~ Requirements for specialised resuscitation trolleys should be considered (e.g. specific trolleys are required for paediatric and neonatal departments and non-magnetic trolleys are required for some medical imaging modalities). ~ If a department requires more than one type of resuscitation trolley to be accommodated in their bay (e.g. both adult and paediatric trolleys) additional area will be required. ~ Additional equipment, such as ECG machines, may be accommodated in this bay in some departments. ~ The bay shall be a minimum depth of 800mm to ensure that equipment does not impede adjacent corridor circulation. ~ A patient slide may need to be readily available if the resuscitation trolley is required and may be provided within this bay. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 3 |  | [FIHR-030] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | FIHR-173 | BRACKET: gas cylinder, single, trolley mounted | 1 | 3 |  | [FIHR-090] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MGGE-011.01 | CYLINDER: medical gas, C size, oxygen | 1 | 3 |  | [MMHA-033] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 3 |  | [MMBE-042] optional
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002]
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMHA-016 | DEVICE: variable suction and oxygen unit (twin-o-vac) | 1 | 1 |  | [MMHA-016]
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1 |  | [MMHA-027] type dependent on service requirements
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 4 | 1 | Floor Skirting | [FLSK-010] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] to be coordinated with adjacent area
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-020] crash rails are also acceptable
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006] coordinated with adjacent wall protection
BRES | Bay - Resuscitation Trolley | Clinical Support Set 2 | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | [ELGP-223]