## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | Translation and QA Only | 4.5 | 2700 | CHPT-D | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient intermittently;; 1 staff / carer assisting as required | The Change Cubicle - Patient, Accessible provides the area and amenities for patients using wheelchairs, walking aids and/or requiring assistance to change into a hospital gown or appropriate clothes prior to physical therapy, examination, diagnostic imaging, treatment, procedures or surgery, and to re-dress afterwards. The cubicle should provide facilities for temporarily hanging clothes and a bench seat or chair for the patient to sit on whilst changing. | ~ Provision of a door, cubicle partition system, or privacy curtain to enclose the change cubicle is to be determined to suit patient cohort and service requirements. Where possible, the cubicle should be located so the entry opening is discreet and not facing into high traffic areas. ~ Where door is provided it must swing outward. For door to swing inward, additional area for circulation and emergency release hardware is required. In both cases it is required that the door can be opened from the outside in an emergency. ~ The selection of door hardware, namely handles and locks/privacy latches, must ensure usability by people with limited dexterity and motor skills. ~ Lighting control may be provided external to the change cubicle to serve a number of change cubicles in an area, particularly where cubicle systems or privacy curtains are provided. Enclosed change cubicles may have individual light switches or motion controlled lighting. ~ Where two-way access is provided, e.g. from a corridor and directly from a treatment or imaging room, additional area may be required to provide appropriate circulation at the second entry. ~ Where adjacent or with direct access to an imaging room or treatment room where imaging devices are used, the change room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant. ~ Where paediatric services are provided, additional area within change cubicles will be required to support parents/carers assisting children to change. The provision of multiple benches with different seating heights (450mm-520mm for adults and 350mm for children) may also be considered to support paediatric patients. ~ Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. ~ The depth of the seat is to be adequate to support movement while changing, and the weight rating of all seating, including provision for bariatric capacity, is to be considered. The colour of seating is to contrast with the flooring and walls to support visibility and reduce the risk of falls. ~ An operational model for responding to calls from staff/patients will be required to support the provision of the patient to staff call button, staff assist call button and emergency call button, and inclusion is to be determined based on service requirements. Additional staff assist and emergency call buttons my be located outside of the cubicle and shared between a number of change rooms depending on service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-002]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-002] drop-in ceiling tiles are also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] outward opening, with privacy latch; cubicle partition system or curtain track with privacy curtain are also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ELSW-031 | SWITCH: light, motion sensor, ceiling mounted | 1 | 1 |  | [ITSE-044] manual light switch is also acceptable
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-005]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIGE-021 | BENCH SEAT: fixed, indoor, wall mounted | 1 | 1 |  | [FIGE-003] colour of seating to contrast with flooring and walls as per AS1428 luminance contrast requirements
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026] 1 mounted at accessible height to AS1428.1 requirements
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FFE | FIRT-105 | GRAB RAIL: 90 degree | 1 | 1 |  | [FIRT-006]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] low height for access from seated position or floor
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
CHPT-AC | Change Cubicle - Patient, Accessible | Sanitary Facilities | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]