## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CHST-10 | Change - Staff, 10m2 | Staff Amenities | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 3 staff intermittently | The Change - Staff, 10m2 provides the space and fit-out for staff to change into appropriate work clothing or gowns, to store their street clothing and to perform personal ablutions. The room may be comprised of a combination of showers, toilets, basins and lockers, with numbers to suit service and staff requirements. | ~ Change rooms are typically allocated as separate male and female areas and sized on a proportional basis. ~ Secure storage for personal property (e.g. lockers) may be provided within the change room or separately within the unit dependent on operational policies and service requirements. ~ Accessible change facilities for staff to be provided nearby. ~ A proportion (minimum 2%) of lockers may be required to be accessible with locking devices located between 900mm to 1100mm AFFL. ~ Secure, staff-only access to change rooms is required. ~ Visual privacy from the entry door to the changing areas and cubicles is to be considered during planning. ~ If provided for staff to change for sterile procedures, access to clean linen will be required | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008] wall trim fixing acceptable if drop-in ceiling tiles are provided
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with closer as required for privacy
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 2 | 1 |  | [FIDI-030] 1 to basin, 1 to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 3 |  | [FIDI-049] optional, to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIGE-021 | BENCH SEAT: fixed, indoor, wall mounted | 2 | 1 |  | [FIGE-003] to changing area
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIGE-023 | BENCH SEAT: fixed, indoor, wet area, wall mounted | 1 | 1 |  | [FIGE-003] to shower cubicle
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026] 1 to toilet cubicle, 1 to shower cubicle
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional, to changing area; quantity to be based on staffing and service requirements
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-033] optional
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 12 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | [FLVY-009] tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQSN-323 | LOCKER: floor standing, 2 door, with shoe storage | 2 | 1 |  | [FQSN-054]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQSN-343 | LOCKER: floor standing, 4 door, with shoe storage | 2 | 1 |  | [FQSN-055]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | FQWS-331 | BIN: sanitary waste | 1 | 3 |  | [FQCW-037] optional, to toilet in female change rooms
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYBA-143 | BASIN: type C, handwashing, with integral double shelf | 1 | 1 |  | [HYBA-012]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYDR-081 | DRAIN: clear out, round | 1 | 1 |  | [HYDR-009]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYSH-001 | SHOWER: fixed rose, wall mounted | 1 | 1 |  | [HYTP-018]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYTP-251 | TAPWARE: shower, mixer | 1 | 1 |  | [HYTP-039]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 2 | 1 |  | 1 to basin tapware, 1 to shower
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | HYWC-021 | TOILET SUITE: standard | 1 | 1 |  | [HYWC-008] with clear out access point
CHST-10 | Change - Staff, 10m2 | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | [FIJO-212] optional, over lockers; plasterboard bulkhead is also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 6 | 1 | Wall Finish 1 | [WLWA-004]
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 4 | 1 | Wall Finish 2 | [WLWA-023] to shower; tiles are also acceptable
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLPT-061 | PARTITION SYSTEM: cubicle, toilet | 1 | 1 | Wall Finish 5 | [WLPT-005] lift off hinges to inward opening sanitary compartment doors
CHST-10 | Change - Staff, 10m2 | Staff Amenities | FIN | WLPT-071 | PARTITION SYSTEM: cubicle, shower | 1 | 1 | Wall Finish 4 | [WLPT-004]