## Room Data
Standard Components - Room Data Sheet
Date of issue: 13.05.2020
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | 60 | Available 24 Hours | 1 patient; up to 6 staff |  | Acoustic privacy is required | A highly specialised procedure room where interventional Cardiac Catheter procedures are undertaken in an aseptic environment and may include administration of sedation or general anaesthesia. The Catheter Laboratory - Electrophysiology Studies may also be used for electrophysiology (EP) studies and treatment and is typically only provided in hospitals of tertiary level or higher, where required. A Control room will be located adjacent and may serve more than one procedure room. A clinical scrub area should be located immediately adjacent to the room staff entry. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. A strut channel system able to carry moving loads may be required. Cable ducts from Control Room and Equipment room will be required. 'X-Ray in Use' lights are required outside each entry door. Power to imaging equipment should be on emergency supply. The Catheter Laboratory for EP studies will require radiofrequency shielding.

## Items
Standard Components - Items in room
Date of issue: 13.05.2020
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | at 3000 mm AFFL
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWOB-009 | OBSERVATION: internal window, lead glass, clear | 1 | to control room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWGL-006 | DOOR: 910mm c/o, single leaf, observation panel, solid core/lead glass, lead shielding, paint | 2 | staff access to sterile stock/ scrub areas
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | DWSC-034 | DOOR: 1800mm c/o, double leaf, solid core, lead shielding, paint | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MGFP-002 | FLOWMETER: medical air | 3 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIHR-019 | BRACKET: for suction bottle | 4 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | wall mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-119 | TROLLEY: equipment | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 | for slave monitor
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-122 | TROLLEY: gowns | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-045 | IV STAND: mobile | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MGFP-004 | FLOWMETER: oxygen | 4 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-106 | CUPBOARD: drawer unit, 4 equal | 1 | under bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMHA-027 | TROLLEY: resuscitation, adult | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-088 | SAFE: dangerous drugs, small | 1 | optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-142 | TROLLEY: sharps bin | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FQBS-052 | STOOL: mobile, high, adj height | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-002 | ADAPTER: suction | 4 | on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-100 | SUCTION BOTTLE | 4 | on pendant mounted brackets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMOP-040 | MACHINE: anaesthetic with integral monitors | 1 | optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMSP-015 | PENDANT: single, anaesthetic (fixed or adjustable height) | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | ITCL-021 | CLOCK: clock system slave dual time / elapsed time | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMHA-002 | DEFIBRILLATOR | 1 | on resus trolley
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMSP-029 | LIGHT: operating, single, 550 diam nom. | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-032 | DISPLAY SCREEN: slave, for patient monitor | 1 | on wall bracket
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMSP-018 | PENDANT: single, wet and dry combination (fixed or adjustable height) | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-329 | DEVICE: imaging, ultrasound scanning unit | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FQCW-008 | BIN: waste, clinical, 50L | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-100 | INJECTOR: contrast, CT | 1 | optionally can be on table or ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-212 | BULKHEAD: joinery | 1 | over cupboards
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-377 | WARMER: contrast | 1 | on bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-385 | SYSTEM: imaging, cath lab, dual plane, ceiling | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-389 | TABLE: operating, fixed, narrow table plate, cath lab, dual plane | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-390 | SHIELD: radiation, upper body, mobile, cath lab | 2 | ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-396 | DISPLAY SCREEN: cath lab, multi modality | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-220 | CUPBOARD: tall, double door, glazed, catheter hanging | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-398 | SYSTEM: electrophysiology, cath lab | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | MMMI-400 | STAND: ceiling, with traverse bridge, cath lab | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | FFE | FIJO-221 | CUPBOARD: tall, double door, glazed | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | handsfree to control room, outside room, to control room, delete from room list if listed in adjacent accessway
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELPR-006 | RCD: residual current device | 4 | 1 to each pendant, 1 for wall mounted outlets and 1 for floor box outlets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 1 | under table
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-003 | CONTROL PANEL: lighting | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-001 | BUTTON: emergency stop | 1 | optional, for equipment shut-off
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | LIFX-008 | LIGHT: task light, built in | 2 | over bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 3 | outside all entry points. Delete from room list if listed in adjacent room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGFP-001 | ALARM PANEL: medical gases | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | 2 above bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 9
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELPR-004 | MONITOR: line isolation | 2 | 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | WLSH-004 | SHIELDING: lead lining | 1 | to walls and doors as specified
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITCL-023 | CONTROL PANEL: master clock system | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELBO-012 | SWITCH: light, dimmer | 4
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ITIN-024 | OUTLET: data, double RJ45, on pendant | 2 | on pendant, 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 3 | on pendant, 2 to EP pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 2 | on pendant, 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on pendant, 2 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on pendant, 2 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MGAS-051 | OUTLET: scavenge, on pendant | 2 | on pendant, 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on pendant, 2 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-121 | GPO: emergency power, single, on pendant | 16 | on pendant, 8 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELGP-225 | GPO: emergency power, double, in floorbox | 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | MEEX-016 | RETURN AIR: grille, low level | 4
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | SE | ELPR-007 | UPS: status indicator | 2