## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | Translation and QA Only | 60 | 3000 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; up to 6 staff | A highly specialised procedure room where interventional Cardiac Catheter procedures are undertaken in an aseptic environment and may include administration of sedation or general anaesthesia. | ~ The Catheter Laboratory - Electrophysiology Studies may also be used for electrophysiology (EP) studies and treatment and is typically only provided in hospitals of tertiary level or higher, where required. ~ A Control room will be located adjacent and may serve more than one procedure room. ~ A clinical scrub area should be located immediately adjacent to the room staff entry. ~ Radiation shielding as advised by Radiation Consultant. ~ A strut channel system able to carry moving loads may be required. ~ Cable ducts from Control Room and Equipment room will be required. ~ 'X-Ray in Use' lights are required outside each entry door. ~ Power to imaging equipment should be on emergency supply. ~ The Catheter Laboratory for EP studies will require radiofrequency shielding. | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to procedure room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to control room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to sterile stock side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to procedure room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to procedure room side
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 3 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 3 | [DWGL-006] staff access to sterile stock/ scrub areas, with sliding cover for privacy
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | DOHI-013.07 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass, with cover | 1 | 1 | Internal - Door 2 | [DWGL-006] to control room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-034] to corridor
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] to control room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 4 | 1 |  | [FIHR-019] on pendant/s
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] for slave monitor
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 2 | 1 |  | [FQBS-052]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1 |  | [FQCW-008]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITBU-474 | CLOCK: digital display, dual sided, electric, synchronised slave, wired internet protocol (IP), wall mounted, cantilevered | 1 | 1 |  | [ITCL-023]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITBU-482 | CLOCK: digital display, with time and elapsed time, electric, synchronised slave, wired internet protocol (IP), wall recessed | 1 | 1 |  | [ITCL-021]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 2 | 1 |  | [ITNE-008+MMGE-164]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOCU-023 | CUPBOARD: tall, double door, glazed | 1 | 1 |  | [FIJO-221]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 3 | 1 |  | [FIJO-108]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JODW-041 | DRAWER UNIT: under bench, 4 drawers, equal | 1 | 1 |  | [FIJO-106] under bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] over cupboards
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | JOSP-121 | JOINERY UNIT: bespoke, endoscopy, tall, catheter hanging | 1 | 1 |  | [FIJO-220]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | LIFX-141 | LIGHT: operating, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [MMSP-029]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-006 | IMAGING DEVICE: catheter lab, dual plane, floor mounted and on ceiling mounted track | 1 | 1 |  | [MMMI-385]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-007 | TRACK: catheter lab, imaging device, ceiling mounted | 1 | 1 |  | [MMMI-400]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-008 | BRACKET: catheter lab, imaging device cable management, ceiling mounted | 1 | 1 |  | [MMMI-400]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-009 | TABLE: patient, catheter lab | 1 | 1 |  | [MMMI-389]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MICC-041 | DEVICE: catheter lab, electrophysiology (EP) | 1 | 1 |  | [MMMI-398]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIGE-001 | SHIELD: radiation, mobile | 2 | 1 |  | [MMMI-390] ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1 |  | [MMMI-377] on bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIGE-051 | INJECTOR: contrast, pedestal, mobile | 1 | 3 |  | [MMMI-100] optionally can be on table or ceiling mounted
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MIUS-001 | IMAGING DEVICE: ultrasound | 1 | 1 |  | [MMMI-329]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMGE-045 | POLE: IV, mobile | 2 | 1 |  | [MMGE-045]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMGE-191 | CANNISTER: suction bottle | 4 | 1 |  | [MMGE-100] on pendant mounted brackets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMHA-002 | DEVICE: defibrillator | 1 | 1 |  | [MMHA-002] on resus trolley
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMHA-031 | TROLLEY: resuscitation, adult | 1 | 1 |  | [MMHA-027]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMOP-161 | MACHINE: anaesthetic | 1 | 3 |  | [MMOP-040] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 3 |  | [MMGE-088] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMPM-051 | MONITOR: patient, slave, remote monitoring and control | 1 | 1 |  | [MMGE-032] on wall bracket
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FFE | MMTR-121 | TROLLEY: gowns/scrubs, 1060W x 490D x 1830H nominal | 1 | 1 |  | [MMGE-122]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] at 3000 mm AFFL
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | [WLWA-019]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 1 - Arm 1 | [ELGP-121]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-151 | GPO: single, emergency power, on pendant services head | 8 | 1 | Pendant 2 - Arm 1 | [ELGP-121]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [ELGP-132]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ELGP-181 | GPO: single, UPS, on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [ELGP-132]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | FIHR-345 | BRACKET: display screen, single, articulated, on pendant arm | 1 | 1 | Pendant 3 - Arm 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [ITIN-024]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | ITIN-024 | OUTLET: data, double RJ45, on pendant services head | 1 | 1 | Pendant 2 - Arm 1 | [ITIN-024]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 1 | 1 | Pendant 1 - Arm 1 | [MGAS-021]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-021 | OUTLET: medical air, on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [MGAS-021]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | [MGAS-031] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant services head | 1 | 3 | Pendant 2 - Arm 1 | [MGAS-031] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [MGAS-041]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-041 | OUTLET: oxygen (O2), on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [MGAS-041]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 3 | Pendant 1 - Arm 1 | [MGAS-051] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-051 | OUTLET: scavenge, on pendant services head | 1 | 3 | Pendant 2 - Arm 1 | [MGAS-051] optional
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 1 - Arm 1 | [MGAS-061]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGAS-061 | OUTLET: suction, on pendant services head | 2 | 1 | Pendant 2 - Arm 1 | [MGAS-061]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 2 | 1 | Pendant 1 - Arm 1 | [MGFP-002]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 2 - Arm 1 | [MGFP-002]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1 - Arm 1 | [MGFP-004]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 2 - Arm 1 | [MGFP-004]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 1 - Arm 1 | [MMGE-002]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MGFP-061 | ADAPTER: suction | 2 | 1 | Pendant 2 - Arm 1 | [MMGE-002]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MICC-062 | DISPLAY SCREEN: catheter lab, multi-modality | 1 | 1 | Pendant 3 - Arm 1
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 1 | [MMSP-018]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-111 | PENDANT: single arm, ceiling mounted | 1 | 1 | Pendant 3
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-114 | PENDANT: single arm, on imaging system track | 1 | 1 | Pendant 2 | [MMSP-015] electrophysiology pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-171 | MEDICAL SERVICES HEAD: vertical, on pendant arm | 1 | 1 | Pendant 1 - Arm 1 | [MMSP-018] anaesthetic pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | MSP | MMSP-181 | MEDICAL SERVICES HEAD: horizontal, on pendant arm | 1 | 1 | Pendant 2 - Arm 1 | [MMSP-015]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 9 | 1 |  | [ELGP-123.1]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] 2 above bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELGP-256 | GPO: double, emergency power, in floor box | 3 | 1 |  | [ELGP-225]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 2 | 1 |  | [ELPR-004] 1 to each pendant
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 2 | 1 |  | [ELPR-007]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-051 | PANEL: equipotential (EP) test point, wall mounted | 1 | 1 |  | [ELBO-005]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006] 1 to each pendant, 1 for wall mounted outlets and 1 for floor box outlets
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 4 | 1 |  | [ELBO-012]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELSW-051 | CONTROL PANEL: lighting | 1 | 1 |  | [ELBO-003]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 3 |  | [ELBO-001] optional, for equipment shut-off
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | [ITCL-008] to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | [ITCL-004] to wall, + indicator button & light
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1 |  | [ITIN-022]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1 |  | [ITIN-143] under table
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] handsfree to control room, outside room, to control room, delete from room list if listed in adjacent accessway
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | [ITSE-025]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] over bench
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | [LIFX-002] outside all entry points. Delete from room list if listed in adjacent room
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | MEEX-046 | GRILLE: return air, wall mounted, low level | 4 | 1 |  | [MEEX-016]
CLAB-EP | Catheter Laboratory - Electrophysiology Studies | Cardiac Investigations | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1 |  | [MGFP-001]