## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | Translation and QA Only | 14 | 2700 | CLCRT | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 3 staff | Room adjacent to Catheter Lab Interventional Procedure Room/s with direct visibility to the patient for remote control of equipment, and review and reporting of images. | ~ The Control Room may serve two procedure rooms. ~ Radiation shielding as advised by Radiation Consultant. ~ Cable ducts from Catheter Lab Procedure Room and Equipment room will be required. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to procedure room side
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1 | [DWWD-004] to observation window for patient privacy; refer to local infection control policies
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | DOHI-013.05 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass | 1 | 1 | Internal - Door 1 | [DWGL-006] to procedure room
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 2 | [DWGL-002] to corridor
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] to procedure room
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 3 | 1 |  | [FIHR-075]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | [FIHR-070]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FQBS-171 | CHAIR: office, ergonomic | 3 | 1 |  | [FQBS-018]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 2 | 1 |  | [ITAV-014] part of communications system integrated with imaging system
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 3 |  | [ITAV-057] optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 1 |  | [ITBU-013] patient journey board
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-071 | TELEPHONE: handset, desktop | 2 | 3 |  | [ITNE-049] on bench, 1 cordless optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1 |  | [ITNE-009]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 3 | 1 |  | [ITNE-068]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | [ITNE-069]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] for reporting station
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | [FIJO-031]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOBE-251 | CAP: cable access | 5 | 1 |  | [FIJO-099]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-143]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | MICC-071 | CONTROL WORKSTATION: catheter lab, acquisition, dual display screens, keyboard and mouse, control console, microphone and speaker, desktop | 2 | 1 |  | [MMMI-386]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FFE | MIGE-046 | CONTROL CONSOLE: contrast injector, touch screen | 1 | 1 |  | [MMMI-369]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-161 | GPO: single, UPS, wall mounted | 7 | 1 |  | [ELGP-130]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 8 | 1 |  | [ELGP-223]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 3 |  | [ELBO-001] optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 6 | 1 |  | [ITIN-026] 2 outlets for telephone
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | [LIFX-002]
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 3 |  | [MEGE-007] for control room temperature, optional
CLCR-I | Catheter Laboratory Interventional Control Room | Cardiac Investigations | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1 |  | [MGFP-001]