## Room Data
Standard Components - Room Data Sheet
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | 20 | 24 Hours | 1 - 2 staff intermittently |  |  | The Clean Store / Medication Room, 20m² provides a space for the storage of clean consumables and the secure storage of medications, including intravenous fluids. The room may provide storage for drugs of dependence in accordance with relevant legislation. Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. Secured staff only access to the room is required. The provision and placement of CCTV cameras is dependent on jurisdictional policies. Refer to project specific requirements for the provision of automated medication management systems.

## Items
Standard Components - Items in room
Date of issue: 18.01.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 10
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 3 | extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 3 | extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | MMGE-087 | SAFE: dangerous drugs, medium | 1 | size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-108 | CUPBOARD: drawer unit, baskets, 3 x Wire (400mm wide) | 8
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | ITSE-012 | CAMERA: CCTV | 1 | optional, provision and placement dependent on local policies
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | MMGE-034 | FRIDGE: drugs, large | 1 | size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1 | plasterboard bulkhead also acceptable
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQSM-046 | SHELVING: storage solution, 600W x 400D x 2100H nom., wire, mobile | 5 | type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQCW-061 | BIN: waste, pharmaceutical | 1
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FQSM-048 | SHELVING: storage solution, shelving, 600W x 400D x 2100H nom., wire, mobile | 4 | type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | FFE | FIDI-052 | DISPENSER: sticker roll | 1 | optional
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to drug fridge, for temperature monitoring
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 2 x optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | LIFX-008 | LIGHT: task light, built in | 2 | under wall mounted joinery
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELBO-015 | SWITCH: light, single | 1 | to task light
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELBO-010 | SWITCH: light, 2-way | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELGP-208 | GPO: double, wall mounted | 2
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to drug fridge
CLN-MED-20 | Clean Store / Medication Room, 20m2 | SE | ITSE-038 | READER: access control, general | 2