## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | Translation and QA Only | 20 | 2700 |  | 1 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Clean Store / Medication Room, 20m2 provides a small space for the storage of clean consumables and the secure storage of medications, including intravenous fluids. | ~ This room may provide storage for drugs of dependence in accordance with relevant legislation. ~ Controlled temperature and humidity is required for medication storage and internal temperatures should not rise above 25°C. ~ Secured staff only access to the room is required. ~ The provision and placement of CCTV cameras is dependent on jurisdictional policies. ~ Refer to project specific requirements for the provision of automated medication management systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-003]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-072 | DISPENSER: sticker roll, wall mounted | 1 | 3 |  | [FIDI-052] optional
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQSM-152 | STORAGE SOLUTION: modular system, mobile, 400D x 600W x 2100H nominal | 5 | 1 |  | [FQSM-046] type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQSM-202 | SHELVING UNIT: mobile, adjustable shelves, 400D x 600W x 2100H nominal | 4 | 1 |  | [FQSM-048] type and quantity of storage options to be determined based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | FQWS-271 | BIN: pharmaceutical waste, 20L | 1 | 1 |  | [FQCW-061]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | ITSE-121 | CAMERA: security, CCTV, indoor, dome, ceiling mounted | 1 | 3 |  | [ITSE-012] optional, provision and placement dependent on local policies
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 1 |  | [FIJO-145]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JODW-032 | DRAWER UNIT: under bench, 3 drawers, equal, wire baskets | 8 | 1 |  | [FIJO-108]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | MMPH-002 | SAFE: dangerous drugs, wall mounted, medium | 1 | 1 |  | [MMGE-087] size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FFE | MMPH-024 | FRIDGE: medication/vaccine, 1000L nom, double door | 1 | 1 |  | [MMGE-034] size and quantity to be based on service requirements
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 3 | [WLWA-020] extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023] extent dependent on type and height storage solution
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 3 |  | [ELGP-223] optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to drug fridge
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208]
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 3 |  | [ITIN-026] optional, for future provision of automated dispensing cabinets
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] to task light
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to drug fridge, for temperature monitoring
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] under wall mounted joinery
CLN-MED-20 | Clean Store / Medication Room, 20m2 | Clinical Support Set 1 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-010] 2-way