## Room Template Data
Clean-Up Room (CLNUP) - Room Template Properties and Room Template Data
2025-05-08
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CLNUP | Clean-Up Room | 12 | CLUP-10 | 2 | 06.05.2025 | Up to 24 hours | FALSE |  |  |  |  | 1-2 staff | The Clean-Up Room provides space and amenity for gross decontamination of instruments used in Operating Rooms or Procedure Rooms, storage for cleaning supplies and equipment, as well as storage of waste prior to collection. A Clean-up Room can serve multiple Operating Rooms or Procedure Rooms and should be located nearby to support post procedure processes. | ~ Clearance around the surgical waste management system and docking station, as informed by equipment specifications, is to be maintained at all times. ~ The requirement to provide a door to this room will vary across jurisdictions and is to be confirmed to suit local infection prevention and control policies. ~ Number, size and type of bins, including sharps, to be confirmed to suit waste management policies and service requirements. ~ Provision of cleaner's sink to be confirmed to suit operational policies and service requirements. ~ Type of spout provided to handwashing basin (i.e. gooseneck, straight, etc.) to be confirmed to meet local infection prevention and control policies. ~ Backflow prevention device requirements to be confirmed for all hydraulic fixtures to suit service requirements. ~ Air-conditioning and exhaust requirements to be confirmed to suit service requirements (i.e. extent of gross decontamination of instruments occurring within this room), operational processes (e.g. frequency of waste removal), and equipment selection. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-05-08
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CLNUP | Clean-Up Room | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to both side of the door leaf
CLNUP | Clean-Up Room | D+W | DOHI-015.01 | DOOR: hinged, 1 leaf, 1000 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | sliding door may also be acceptable dependent on infection prevention and control and work health and safety policies, provision of manual hold open device to be confirmed to suit operational requirements
CLNUP | Clean-Up Room | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1
CLNUP | Clean-Up Room | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CLNUP | Clean-Up Room | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | FFE | FIDI-261 | DISPENSER: soap, antiseptic, wall mounted | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | FFE | FIHR-039 | RACK: broom/mop, wall mounted | 1 | 1
CLNUP | Clean-Up Room | FFE | FIHR-143 | RACK: bottle, wall mounted | 1 | 1
CLNUP | Clean-Up Room | FFE | FQCL-052 | BUCKET: cleaner, mopping | 1 | 1
CLNUP | Clean-Up Room | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | quantity is dependent on service requirements (e.g. use of single use drapes)
CLNUP | Clean-Up Room | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1
CLNUP | Clean-Up Room | FFE | HYBA-301 | SINK: single bowl | 1 | 1
CLNUP | Clean-Up Room | FFE | HYBA-451 | SINK: cleaner, with grate, wall mounted | 1 | 1 |  | optional - depending on operating room cleaning equipment and procedures
CLNUP | Clean-Up Room | FFE | HYTP-066 | TAPWARE: basin, tap set, wall mounted | 1 | 1
CLNUP | Clean-Up Room | FFE | HYTP-182 | TAPWARE: sink, tap set, wall mounted, lever handles | 1 | 1
CLNUP | Clean-Up Room | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | with integral stainless steel splashback
CLNUP | Clean-Up Room | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1
CLNUP | Clean-Up Room | FFE | JOSH-403 | SHELF: wall mounted, wire | 1 | 1
CLNUP | Clean-Up Room | FFE | LIFX-122 | LIGHT: procedure, minor, articulated, ceiling mounted | 1 | 1
CLNUP | Clean-Up Room | FFE | MMIC-496 | TROLLEY: transfer, instruments, dirty | 1 | 1 |  | optional - depending on RMD sterilizing transport processes, stored in room prior to transfer to sterilising unit
CLNUP | Clean-Up Room | FFE | MMOP-401 | MACHINE: surgical waste management system | 1 | 1 |  | optional - machine and docking station may be required only in a selection of clean up rooms across the unit (i.e. approx. 1 per 4 OR's)
CLNUP | Clean-Up Room | FFE | MMOP-406 | DOCKING STATION: surgical waste management system | 1 | 1 |  | optional, direct connect waste outlet to sewer system; docking station may be required only in a selection of clean up rooms across the unit (i.e. approx. 1 per 4 OR's)
CLNUP | Clean-Up Room | FFE | FQWS-004 | BIN: sharps, clinical, large | 1 | 1 |  | optional - for laparoscopic sharps as required
CLNUP | Clean-Up Room | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1 |  | optional - to laparoscopic sharps bin if provided
CLNUP | Clean-Up Room | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | to basin
CLNUP | Clean-Up Room | FFE | FQWS-063 | BIN: general waste, slimline, 90L | 1 | 1 |  | size, type and quantity of bins will be dependent on local waste management policies for waste separation
CLNUP | Clean-Up Room | FFE | FQWS-103 | BIN: recycling, paper/cardboard, slimline, 90L | 1 | 1
CLNUP | Clean-Up Room | FFE | FQWS-123 | BIN: recycling, plastics, slimline, 90L | 1 | 1
CLNUP | Clean-Up Room | FFE | FQWS-131 | BIN: recycling, soft plastics, 20L | 1 | 1
CLNUP | Clean-Up Room | FFE | FQWS-143 | BIN: recycling, soft plastics, slimline, 90L | 1 | 1 |  | for sterile wraps
CLNUP | Clean-Up Room | FFE | FQWS-151 | BIN: recycling, glass, 20L | 1 | 1
CLNUP | Clean-Up Room | FFE | FQWS-171 | BIN: recycling, metal, 20L | 1 | 1
CLNUP | Clean-Up Room | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 1
CLNUP | Clean-Up Room | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
CLNUP | Clean-Up Room | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
CLNUP | Clean-Up Room | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | minimum slip rating R10 / pendulum P3 or agreed equivalent
CLNUP | Clean-Up Room | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
CLNUP | Clean-Up Room | SER | ELGP-133 | GPO: single, emergency power, wall mounted, waterproof | 1 | 1 |  | optional - to surgical waste docking station if provided
CLNUP | Clean-Up Room | SER | ELSW-001 | SWITCH: light | 1 | 1
CLNUP | Clean-Up Room | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1
CLNUP | Clean-Up Room | SER | HYDR-103 | TUNDISH: wall mounted | 1 | 1
CLNUP | Clean-Up Room | SER | HYDR-151 | TRAP: plaster | 1 | 1 |  | optional
CLNUP | Clean-Up Room | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1
CLNUP | Clean-Up Room | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin, one to sink
CLNUP | Clean-Up Room | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink
CLNUP | Clean-Up Room | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink
CLNUP | Clean-Up Room | SER | HYDR-201.01 | DIRECT CONNECTION: waste water, general | 3 | 1 |  | 1 to basin, 1 to sink, 1 optional - to surgical waste management system docking station if provided
CLNUP | Clean-Up Room | SER | HYDR-201.02 | DIRECT CONNECTION: waste water, trade | 1 | 1 |  | optional, to plaster trap if provided
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
1BR-IC
1BR-BA