## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
CLRM-10 | Cleaner's Room, 10m2 | 10 |  | 1 - 2 intermittently | 24 Hours |  | A secure room for the storage and decanting of cleaning materials and agents, storage of cleaning equipment and trolley, washing and storage of mops, buckets, brooms etc. and for waste disposal. The larger floor area provides for additional storage or trolley holding.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
CLRM-10 | Cleaner's Room, 10m2 | FE | FE-40600 | Polisher scrubber - floor | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
CLRM-10 | Cleaner's Room, 10m2 | FE | FE-49200 | Sink - cleaner | 1 |  |  |  |  | No | No | Yes | Yes | Yes | No | Yes | No | No
CLRM-10 | Cleaner's Room, 10m2 | FE | FE-58400 | Vacuum cleaner - commercial | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
CLRM-10 | Cleaner's Room, 10m2 | FE | FE-9300 | Dispenser - detergent/ chemical mixer | 1 | optional |  |  |  | No | No | Yes | No | Yes | No | No | No | No
CLRM-10 | Cleaner's Room, 10m2 | FE | FE-4045 | Tapware - long elbow mixer | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | FF | FF-13660 | Metal shelving - 900x400x2100 | 3 | heavy duty | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | FF | FF-1485 | Hook rack - broom/ mop | 1 | 4 hooks, on mounting plate | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | FF | FF-3200 | Trolley - cleaner's | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | FF | FF-6152 | Dispenser - disposable glove | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | FF | FF-6156 | Dispenser - soap | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | SE | S-9001 | GPO: Double | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | SE | S-4033 | Floor waste | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | SE | S-4050 | Cold water: hosecock | 1 | to chemical mixer if required | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | SE | S-5015 | Ventilation | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | SE | S-5019 | Exhaust | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | SE | S-6000 | General fluorescent | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | SE | S-6200 | Light switches | 1 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 1020 | Floor finish | 1 |  | Vinyl, non-slip | Safety | Seamless, coved | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 3052 | Wall finish | 1 | tiles also acceptable | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 5023 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 8010 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | Protection plate to 900 AFFL | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 8040 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | To door frame | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 9001 | Door - 1100mm | 1 | 910mm clear opening; lock set | Solid Core | Paint | Single leaf | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | bar: Connections Ele to Connections Stm
CLRM-10 | Cleaner's Room, 10m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | bar: Connections Ele to Connections Stm