## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CLRM | Cleaner's Room | Logistics / Support Services | Translation and QA Only | 5 | 2700 | CLRM-5 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Cleaner's Room is a secure room for the storage and decanting of cleaning materials, washing and storage of cleaning equipment and cleaner's trolley, and for liquid waste disposal. | ~ This room may be shared between multiple units depending on service requirements. ~ Size requirements for a Cleaner's Room will be dependent on the department to be serviced and operational models for staffing and cleaning regimens that may dictate the type of equipment and number of trolleys to be accommodated. Where more than one trolley will be stored an additional 1.5m2 is required per trolley. ~ The requirements to accommodate vacuum cleaners, floor scrubbers or other floor cleaning equipment within the Cleaners Room is to be determined at a project/department level in conjunction with assessment of finishes and cleaning requirements. Where operational models do not provide a centralised area for the storage of large cleaning equipment (e.g. floor scrubbers), additional area may be required in units or in shared areas between units depending on the additional equipment to be stored. ~ Considerations regarding detergent/chemical management system to be confirmed at a project level, including water connection and associated services requirements (including back flow prevention). ~ Extent and type of storage for chemicals and consumables is to suit service requirements. Consideration of the weight of chemical bottles is required when determining appropriate storage solutions (i.e. if storing chemicals in bottles over 1 litre then low-height shelving is required to avoid lifting of heavy items from high shelves). ~ Hold open door hardware may be provided for hinged doors to allow for easy movement of trolleys in and out of the room. ~ Controlled, staff-only access may be required if this room is provided in a public or patient care area. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CLRM | Cleaner's Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CLRM | Cleaner's Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CLRM | Cleaner's Room | Logistics / Support Services | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] to corridor
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 3 |  | [FIDI-021] optional, type of PPE dispensers to be provided to suit service requirements
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-211 | HOLDER: eye wash bottles, wall mounted | 1 | 3 |  | [FIDI-057] optional, provide as required depending chemical safety data sheets and WHS policies
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIDI-296 | DISPENSER: detergent/chemical mixer, wall mounted | 1 | 1 |  | [FIDI-010]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FIHR-039 | RACK: broom/mop, wall mounted | 1 | 1 |  | [FIHR-040]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FQCL-041 | TROLLEY: cleaner | 1 | 1 |  | [FQSM-021]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FQCL-051 | BUCKET: cleaner | 1 | 1 |  | [FQCW-045] on cleaner's trolley
CLRM | Cleaner's Room | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYBA-141 | BASIN: type C, handwashing | 1 | 1 |  | [HYBA-011] with detachable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYBA-451 | SINK: cleaner, with grate, wall mounted | 1 | 1 |  | [HYBA-040]
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
CLRM | Cleaner's Room | Logistics / Support Services | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to cleaner's sink
CLRM | Cleaner's Room | Logistics / Support Services | FFE | JOSH-402 | SHELF: wall mounted, stainless steel | 1 | 1 |  | [FIJO-196] type and extent of storage to suit service requirements and operational policies for the decanting and storage of chemicals and consumables
CLRM | Cleaner's Room | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
CLRM | Cleaner's Room | Logistics / Support Services | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023]
CLRM | Cleaner's Room | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208] quantity to suit equipment charging requirements
CLRM | Cleaner's Room | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYTP-431 | OUTLET: water, cold | 1 | 3 |  | [HYTP-008] optional, provision dependent on detergent/chemical mixer requirements
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CLRM | Cleaner's Room | Logistics / Support Services | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CLRM | Cleaner's Room | Logistics / Support Services | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 |  | [ITSE-038] optional, dependent on security requirements