## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CLUP-10 | Clean-Up Room - Shared, 10m2 | 10 | 24 Hours | 1 - 2 staff |  | The Clean-Up Room - Shared is used for rinsing and cleaning of medical equipment used in the Operating Rooms or Procedure Rooms. The shared Clean-up Room should be located between or close to the two Operating Rooms or Procedure rooms it serves. Backflow prevention required on all hydraulic fixtures.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
CLUP-10 | Clean-Up Room - Shared, 10m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FA | DWGE-016 | DOOR: frame only | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | optional, for surgical waste management system | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIDI-010 | DISPENSER: detergent/chemical mixer | 1 |  | No | No | Yes | No | No | Yes | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIHR-040 | RACK: broom/mop | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIHR-069 | RACK: bottle | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1 | over sink bench | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | under sink bench | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 | min. R11 rating | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FQCW-012 | BIN: waste, cytotoxic, 20L | 1 | optional | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | FQCW-058 | MOP | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | HYDR-008 | TRAP: plaster | 1 | optional | No | No | No | No | No | No | Yes | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | SE | HYDR-012 | DRAIN: wall drain | 1 | optional, for surgical waste management system; floor drain connection in lieu of wall connection is also acceptable if allowed for in product specifications | No | No | No | No | No | No | Yes | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | SE | HYTP-008 | OUTLET: cold water | 1 | optional, for surgical waste management system | No | No | Yes | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | SE | HYTP-008 | OUTLET: cold water | 1 | for detergent dispenser | No | No | Yes | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 2 | one to sink, one to basin | No | No | Yes | No | Yes | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | MMGE-142 | TROLLEY: sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | MMIC-121 | TROLLEY: instruments transfer | 1 | temporarily located within room | No | No | No | No | No | No | No | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FFE | MMOP-020 | DOCKING STATION: surgical waste management system | 1 | optional, direct connect waste outlet to sewer system; docking station may be required only in a selection of clean up rooms across the unit (ie approx 1 per 4 ORs) | Yes | No | Yes | No | No | No | Yes | No | No
CLUP-10 | Clean-Up Room - Shared, 10m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 |  | No | No | No | No | No | No | No | No | No