## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
CLUP-15 | Clean-Up Room - Shared, 15 m2 | 15 |  | 1 - 2 | 24 Hours |  | The Clean-Up Room, Shared is used for rinsing and cleaning of medical equipment or endoscopes used in the Operating Rooms or Procedure Rooms. Low temperature sterilisation of endoscopes may also be undertaken in this room. The shared Clean-up Room should be located between two Minor Operating Rooms or Procedures rooms where endoscopy procedures are undertaken.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FE | FE-2800 | Basin - handwash, Type B | 1 |  |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FE | FE-49100 | Sink - 750x500x300D | 1 | hot water |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FE | FE-49800 | Sink - flushing rim | 1 | in bench |  |  |  | No | No | Yes | Yes | No | No | Yes | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FE | FE-52450 | Steriliser - low temperature, peracetic acid | 1 | optional |  |  |  | Yes | No | Yes | Yes | No | No | Yes | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FE | FE-4045 | Tapware - elbow mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-1010 | Bench - stainless steel | 1 | with wet edge and inset sinks |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-1050 | Bench - laminate | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-1470 | Bracket - sharps | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-150 | Air flowmeter | 1 | for tube drying |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-19810 | Shelf - SS, over | 1 | over sink bench |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-19820 | Shelf - SS, under | 1 | under sink bench |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-21950 | Suction adapter | 1 | for tube cleaning |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-24125 | Waste bin - clinical | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-4430 | Cupboard - drawer unit | 3 | under dry bench |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-4460 | Cupboard - wall mounted | 2 | over dry bench |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-6152 | Dispenser - disposable glove | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | FF | FF-44614 | Overbench single door (600hx425wx350d) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-9011 | GPO: Emergency power, double (H) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-9060 | GPO: Special: for equipment | 1 | optional, for low temp steriliser |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-4000 | Hot water: outlet | 1 | for low temp steriliser, optional |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-4010 | Cold water: outlet | 1 | for low temp steriliser, optional |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-4033 | Floor waste | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-4037 | Tundish drain | 1 | for low temp steriliser, optional |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-5019 | Exhaust | 1 | efficient exhaust required |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-6200 | Light switches | 3 |  |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-6055 | Special: task light, built in | 3 | under O/H cupboards |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-7020 | Medical Air (MA) | 1 | over dry bench for tube drying |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | SE | S-7040 | Suction | 1 | near sink for tube cleaning |  |  |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 1020 | Floor finish | 1 |  | Vinyl, non-slip | Safety | Seamless, coved | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 3052 | Wall finish | 1 |  | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 5023 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 8010 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 8040 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 9004 | Door - 1100mm | 1 | 1100 mm clear opening to ORs, double swing, sliding cover to observation panel | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
CLUP-15 | Clean-Up Room - Shared, 15 m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No