## Room Data
Standard Components - Room Data Sheet
Date of issue: 31.01.2024
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
COMM | Communications Room | 15 | 24 Hours | 1 - 2 intermittently |  |  | A secure room for engineering services to accommodate racks, backbone cabling and interface control panels for information and communication systems. Systems may include master antenna television (MATV), internet protocol television (IPTV), nurse call, security, telecommunications, building management system (BMS) and Fire/EWIS systems. Additional Considerations: The area shown is indicative; the size of the Communications Room will vary according to engineering consultant advice based on systems to be accommodated. Head end units for security, nurse call, BMS, TMV, IPTV/MATV to be accommodated as required. Equipment located in this room will require uninterruptible power fed from the essential supply (generator). Dedicated air conditioning that is monitored by the Building Management System (BMS) is required Provide adequate lighting to ensure visibility to both front and rear of racks. The configuration of power and data (i.e., wall mounted or ceiling mounted services) to supply the racks is to be determine base on the room layout and equipment selected. The Communication Room must be located such that it is not susceptible to possible water damage or excessive electromagnetic interference. Water or gas pipes must not pass through a Communication Room. Where a Distributed Antenna System (DAS) for in-building mobile reception is provided, the telco carrier base station equipment is to be located in the Communications Room. Refer to telco for spatial requirements to determine sizing of the Communications Room. A DAS shall conform to the most recent edition of the Mobile Carriers Forum Design Specification for Distributed Antenna Systems.

## Items
Standard Components - Items in room
Date of issue: 31.01.2024
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
COMM | Communications Room | FA | FLVY-001 | FLOOR FINISH: vinyl, seamless, coved, anti-static | 1
COMM | Communications Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
COMM | Communications Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
COMM | Communications Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
COMM | Communications Room | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1
COMM | Communications Room | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1
COMM | Communications Room | FA | CLCN-009 | CORNICE: wall trim fixing | 1
COMM | Communications Room | FFE | ITNE-052 | TELEPHONE: handset, wall mount | 1
COMM | Communications Room | FFE | ITNE-005 | COMMS BOARD | 1 | to suit project requirements
COMM | Communications Room | FFE | ITIN-123 | RACK: communications | 1 | to suit project requirements
COMM | Communications Room | FFE | ITIN-128 | RACK: voice, intermediate distribution frame (IDF) | 1 | optional, to suit project requirements
COMM | Communications Room | FFE | ITIN-139 | COMPUTER: mainframe | 1 | to suit project requirements
COMM | Communications Room | FFE | ITNE-011 | COMPUTER: server | 1 | to suit project requirements
COMM | Communications Room | FFE | FQGE-095 | STEP: safety | 1
COMM | Communications Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | to suit project requirements
COMM | Communications Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | to suit project requirements
COMM | Communications Room | SE | ELBO-015 | SWITCH: light, single | 1
COMM | Communications Room | SE | ELGP-208 | GPO: double, wall mounted | 3 | to suit project requirements
COMM | Communications Room | SE | ITSE-046 | SENSOR: motion detection, for staff alert | 1
COMM | Communications Room | SE | ITSE-038 | READER: access control, general | 1
COMM | Communications Room | SE | ITSE-020 | CONTROL PANEL: duress | 1 | optional, to suit project requirements
COMM | Communications Room | SE | ITBU-015 | HEAD END: IPTV | 1 | optional, to suit project requirements
COMM | Communications Room | SE | ITBU-016 | HEAD END: MATV | 1 | optional, to suit project requirements
COMM | Communications Room | SE | ELGP-235 | GPO: UPS, double, wall mounted | 4 | to suit project requirements, power may be wall mounted or delivered via ceiling mounted umbilicals for access depending on server selection.