## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
COMM | Communications Room | Logistics / Support Services | Translation and QA Only | 15 | 2700 |  | 6 | 07.04.2026 |  | 24 hours | 1-2 persons intermittently;;; | A secure room for engineering services to accommodate racks, backbone cabling and interface control panels for information and communication systems. Systems may include master antenna television (MATV), internet protocol television (IPTV), nurse call, security, telecommunications, building management system (BMS) and Fire/EWIS systems. | ~ The area shown is indicative; the size of the Communications Room will vary according to engineering consultant advice based on systems to be accommodated. ~ Head end units for security, nurse call, BMS, TMV, IPTV/MATV to be accommodated as required. ~ Equipment located in this room will require uninterruptible power fed from the essential supply (generator). ~ Dedicated air conditioning that is monitored by the Building Management System (BMS) is required ~ Provide adequate lighting to ensure visibility to both front and rear of racks. ~ The configuration of power and data (i.e., wall mounted or ceiling mounted services) to supply the racks is to be determine base on the room layout and equipment selected. ~ The Communication Room must be located such that it is not susceptible to possible water damage or excessive electromagnetic interference. Water or gas pipes must not pass through a Communication Room. ~ Where a Distributed Antenna System (DAS) for in-building mobile reception is provided, the telco carrier base station equipment is to be located in the Communications Room. Refer to telco for spatial requirements to determine sizing of the Communications Room. A DAS shall conform to the most recent edition of the Mobile Carriers Forum Design Specification for Distributed Antenna Systems. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
COMM | Communications Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
COMM | Communications Room | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
COMM | Communications Room | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
COMM | Communications Room | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
COMM | Communications Room | Logistics / Support Services | D+W | DOHI-104.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-021]
COMM | Communications Room | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ELGP-261 | GPO: double, UPS, wall mounted | 4 | 1 |  | [ELGP-235] to suit project requirements, power may be wall mounted or delivered via ceiling mounted umbilicals for access depending on server selection.
COMM | Communications Room | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
COMM | Communications Room | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
COMM | Communications Room | Logistics / Support Services | FIN | FLVY-103 | FLOOR FINISH: vinyl, seamless, standard slip resistance, static dissipative | 1 | 1 | Floor Finish 1 | [FLVY-001]
COMM | Communications Room | Logistics / Support Services | FFE | FQGE-162 | STOOL: step, safety | 1 | 1 |  | [FQGE-095]
COMM | Communications Room | Logistics / Support Services | SER | ITBU-151 | HEAD END: IPTV system | 1 | 3 |  | [ITBU-015] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITBU-171 | HEAD END: MATV system | 1 | 3 |  | [ITBU-016] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-201 | ICT RACK: server equipment, floor standing | 1 | 1 |  | [ITNE-011] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-211 | ICT RACK: network communications equipment, floor standing | 1 | 1 |  | [ITNE-005] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-211 | ICT RACK: network communications equipment, floor standing | 1 | 1 |  | [ITIN-123] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-221 | ICT RACK: main distribution frame (MDF) | 1 | 1 |  | [ITIN-139] to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITIN-231 | ICT RACK: intermediate distribution frame (IDF) | 1 | 3 |  | [ITIN-128] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-052]
COMM | Communications Room | Logistics / Support Services | SER | ITSE-054 | CONTROL PANEL: security, duress | 1 | 3 |  | [ITSE-020] optional, to suit project requirements
COMM | Communications Room | Logistics / Support Services | SER | ITSE-221 | SENSOR: safety, motion detection, for staff alert, wall mounted | 1 | 1 |  | [ITSE-046]
COMM | Communications Room | Logistics / Support Services | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | [ITSE-038]
COMM | Communications Room | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]