## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | Full AHIA Review | 16 | 2700 |  | 9 | 31.03.2026 |  | Up to 24 hours | 1 patient; 1 visitor; 1-2 staff | The Consult Room ENT/ Ophthalmology provides the space, equipment and services for consultation, assessment, examination and minor treatment and observation of patients for acute ENT and Ophthalmology related injury and illness with specialised equipment. | ~ This Standard Component is intended to support minor treatments. Where patients require sedation (including with nitrous oxide) access to a larger procedure room is required. ~ Where this room may also be used for general consultation, specialised equipment for ENT and Ophthalmology must be able to be stored within a lockable cupboard or store room. ~ Eye testing with a visual acuity chart and mirror requires a 6m distance from the chart to the patient when chart is reflected. ~ Vision panels within the door(s) are to have a cover to enable blackout of the room for eye testing as determined by clinical services requirements. ~ An eye wash station has been indicated within the room. Disposable eye wash bottles may be considered in conjunction with or instead of a fixed eye wash station depending clinical services requirements and local IPC policies. ~ Acoustic treatments may be required to minimise reverberation for ENT testing and are to be determined suit clinical services requirements. All acoustic finishes must meet IPC requirements (Refer to Part D: Infection Prevention and Control for more information). ~ A second door may be required for staff egress and provision will be dependent on local Work Health and Safety (WHS) policies. The location of the second door will be dependent on the overall department plan and availability of an appropriate area to egress. ~ The weight capacity of the examination chair selected must be considered to suit a wide range of patient requirements. ~ The clear area required on each side of the examination chair for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Ready access to medications, including refrigerated medications, is required. A small medication fridge with temperature monitoring, connected to building management system (BMS), may be provided within the room depending on local operational models for medication management. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ The type, extent and configuration of storage within the room for consumables will be dependent on clinical services requirements, operational policies for stock centralisation/decanting and IPC policies. ~ Size, type and quantity of waste bins provided, including sharps bins, will be dependent on clinical services requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 91
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to room side
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to room side
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to corridor side
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | cover to vision panel required to control light for eye examinations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | D+W | DOHI-013.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel, with cover | 1 | 3 | Internal - Door 2 | optional, for secondary staff egress; provision dependent on local WHS policies; cover to vision panel required to control light for eye examinations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to eye chart display screen
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for examination chair
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | optional, to medication fridge if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | to articulated examination light
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | over desk, for charging portable devices
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to slit lamp and retinal camera
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 3 | Panel 1 | optional, to articulated examination light; controls may be integral to light fitting
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | optional
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | collocated with alcohol based hand rub
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | to basin
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 3 |  | optional, to patient monitor if provided; with cable and accessory management items as required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 8 | 1 | Floor Skirting
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin and eye wash station or an inset section of non-slip vinyl is required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on a clinical trolley that is shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | with removable shroud to pipework; location of thermostatic mixing valve to be determined based on ability to share with nearby basins
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to basin, 1 to eye washing station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYSH-106 | STATION: emergency, safety, eye wash, wall mounted | 1 | 1 |  | disposable eye wash bottles may be considered in conjunction with or instead of a fixed eye wash station depending clinical services requirements and local IPC policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to basin tapware, 1 to eye washing station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; located to ensure visibility along paths of travel
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | 1 to entry door, 1 to examination chair; located to support quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | 1 to entry door, 1 to examination chair; may be combined on a single face plate with patient to staff call button; located to support quick access by staff
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | optional, to medication fridge if provided; for temperature monitoring BMS connection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | optional, to patient monitor if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to slit lamp and retinal camera
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | optional, provision dependent on clinical services requirements and local ICT strategies and policies
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | to computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | for storage of consumables and specialist equipment
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 3 |  | optional, to shelving over computer workstation if provided
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | to tall cupboard
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 3 |  | optional, over computer workstation
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMBE-176 | CHAIR: patient, examination, electric | 1 | 1 |  | suitable for ENT examinations and minor treatments
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-391 | DISPLAY SCREEN: eye examination, testing chart | 1 | 1 |  | align with mirror; locate to achieve 6m distance to patient when chart is reflected
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-396 | MIRROR: eye examination, to testing chart display screen | 1 | 1 |  | align with eye chart; locate to achieve 6m distance to patient when chart is reflected
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-401 | DEVICE: eye examination, slit lamp | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMGE-406 | DEVICE: eye examination, retinal camera | 1 | 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMPH-021 | FRIDGE: medication/vaccine, 150L nom, single door, under bench | 1 | 3 |  | optional, with temperature monitoring; provision is dependent on operational models for medication management
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 3 |  | optional, provision and configuration of monitoring to be confirmed to suit clinical services requirements
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | to basin and eye wash station
CONS-ENT-OP | Consult Room - ENT / Ophthalmology | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection