## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CONS-UN | Consult Room - Universal Access | Ambulatory Care | Translation and QA Only | 17 | 2700 |  | 2 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient; 1-2 visitors; 1-2 staff | The Consult Room - Universal Access will provide for private consultation and physical examination of a range of patients with or without support persons present. | ~ The spatial allowance will accommodate patients who (a) are using a wheelchair, including a bariatric sized wheelchair; or (b) require a hoist to transfer. ~ The position of the basin, dispensers and other fittings also allows for use by staff in wheelchairs. ~ A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. ~ It is anticipated that one of these rooms may be provided within a 'pod' of consult rooms. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to room side
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | DWGL-033]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-005] optional, second door for egress
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-007]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-223 | DISPENSER: paper bed roll, exam couch mounted | 1 | 1 |  | [FIDI-003] may be provided as an attachment to exam couch
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 3 |  | [FIHR-019] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 1 |  | [FQBS-018]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQDW-134.03 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1500W | 1 | 1 |  | [FQDW-037]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-050]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] high resolution monitor for PACS viewing
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-027] may be wall mounted
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MGFP-061 | ADAPTER: suction | 1 | 3 |  | [MMGE-002] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-172 | COUCH: patient, examination, electric, bariatric | 1 | 1 |  | [MMBE-064] hi/low operation
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | [MMBE-056]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 1 |  | [MMBE-052] for patient lifter track
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMBE-261 | SLING: patient lifter | 1 | 3 |  | [MMBE-054] optional, for patient lifter motor
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 3 |  | [MMGE-100] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | MMGE-233 | DIAGNOSTIC SET: otoscope and ophthalmoscope, wall mounted | 1 | 1 |  | [MMGE-031] may be portable/mobile on stand
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 3 | 1 |  | [FQBS-058] consider weight capacity of chairs
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-031]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-025] to patient/visitor chairs
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 3 | [WLWA-020] to exam couch
CONS-UN | Consult Room - Universal Access | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 4 | [WLWA-007] to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | [MGAS-022] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 3 | Panel 1 | [MGAS-042] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 3 | Panel 1 | [MGAS-062] optional
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 3 | Panel 1 | [MGFP-002] optional, provide if medical air required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 3 | Panel 1 | [MGFP-004] optional, provide if oxygen required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 3 | Panel 1 | [MMGE-002] optional, provide if suction required
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | ELGP-216 | GPO: double, on services panel | 1 | 1 | Panel 1 | [ELGP-205]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | ELGP-246 | GPO: double, emergency power, on services panel | 1 | 1 | Panel 1 | [ELGP-222]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low level, for electric couch
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] 2x below desk, 1x above desk
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] for exam light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 to exam light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] + indicator button & light
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028]
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1 |  | [ITIN-036] to desk
CONS-UN | Consult Room - Universal Access | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] in discreet location easily accessible by staff