## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
CORR | Corridor - Patient Treatment Areas | 0 |  | N/A | 24 hours |  | Corridor widths must be sized to allow for the safe movement and passing of trolleys, beds, wheelchairs and other mobile equipment. Provision should also be made where oversized, additional equipment is used, ie, bed extensions or bariatric beds. Area (m2) included in HPU circulation. 1 x GPO-Cleaner should be provided as per mandatory requirements. Corridor lighting, where patients are transported on trolleys, positioned to prevent unnecessary glare to patient eyes. Light fittings shall be recessed, flush fitting and sealed to prevent dust ingress. Refer to AusHFG Part C, 710 Space Standards and Dimensions, for further information.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
CORR | Corridor - Patient Treatment Areas | Fabrics | 1000 | Floor finish | 1 | Default = vinyl or carpet tiles are also acceptable. | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 2000 | Skirting | 1 | Default = coved vinyl, featheredged vinyl skirting to carpet tiles. | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 2530 | Door protection | 1 |  | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 2670 | Wall protection | 1 | Align heights of corner guards with other corridor elements |  |  | Corner guards to 900 AFFL minimum | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 2729 | Handrail | 1 | One side minimum. Provision on both sides of corridor to be project specific. |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 3010 | Wall finish | 1 |  | Paint | Scrub resistant |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 5060 | Ceiling - Acoustic | 1 |  | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 7001 | Windows | 1 | Desirable. |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 8040 | Door protection | 1 | Optional. To be decided at project level. | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | Fabrics | 9004 | Door - 1100mm | 1 | 1200mm (single door) or 1500mm (1+1/2 doors) clear opening. Doors widths to ensure movement of trolleys/beds from corridors to adjacent rooms. Glazing optional. Hold open devices may be applied, magnetic hold open devices to fire doors must be connected to the fire alarm system. | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | FF | FF-5828 | External window dressing | 1 | Number to align with window configuration. Window dressing type to comply with Infection Control policy. |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | FF | FF-5830 | Dispenser - antiseptic hand rub | 2 | Number to suit corridor layout and Infection Control policies. |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | SE | S-10020 | Card access | 1 | To Unit entry doors where required |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | SE | S-8040 | Annunciator | 1 | Ceiling mounted, clinical areas only. Number to suit corridor layout. |  |  |  | No | No | No | No | No | No | No | No | No
CORR | Corridor - Patient Treatment Areas | SE | S-9015 | GPO: Cleaner | 1 | Beige face plate. Number and location to comply with mandatory requirements. |  |  |  | No | No | No | No | No | No | No | No | No