## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
CTPR | CT Planning Room | Radiation Oncology | Translation and QA Only | 45 | 3000 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 patient;; up to 4 staff assisting | The CT Planning Room provides space and facilities for Computed Tomography (CT) scanning procedures as part of the planning of radiation therapy treatment for patients. A collocated Control Room with observation window is required for the remote operation of equipment. | ~ An Equipment Room may be required and will need to be in close proximity due to acceptable cable lengths. ~ Cable ducts between the Scanning Room, Control Room and Equipment Room will be required. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ The CT Planning Room must be adequately shielded. Radiation shielding is to be as advised and confirmed by a Radiation Consultant to suit the equipment procured. 'X-ray in Use' lights are required outside each entry door to be illuminated when scanning begins. ~ Interlock system to doors recommended to prevent machine from running if door open and to stop the machine upon entry if in use. ~ Additional medical gases may be provided (including additional oxygen, additional suction, nitrous oxide and scavenge) depending on clinical requirements, such as the provision of anaesthetic services. ~ Dimmable lights are to be provided and lights are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort and distraction. ~ Where possible, it is preferred that ductwork in the ceiling is designed to the perimeter of room to allow for future flexibility to provide ceiling mounted equipment. ~ The need for and extent of emergency and UPS power must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ Unistrut ceiling able to carry moving loads may be required. ~ A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be provided depending on clinical/service requirements and will be coordinated to support the technologies provided in the Linear Accelerator Treatment Room. The provision of these technologies is to be confirmed by the project and may have additional design requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 3 | 1 | Internal - Door 1 | [DWPR-005] to imaging room side
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to imaging room side
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
CTPR | CT Planning Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to control room side
CTPR | CT Planning Room | Radiation Oncology | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | [DWSC-005] to control room
CTPR | CT Planning Room | Radiation Oncology | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-034] to corridor
CTPR | CT Planning Room | Radiation Oncology | D+W | WIFX-007.03 | WINDOW: fixed, internal, single glazed, sill at 900H, shielded, lead glass | 1 | 1 | Internal - Window 1 | [DWOB-009] safety glass, to control room
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | [FIHR-030] for patient slide
CTPR | CT Planning Room | Radiation Oncology | FFE | FIHR-091 | HOOK: anchor point, for attaching patient self-assist positioning aid, wall mounted | 1 | 1 |  | [FIHR-092]
CTPR | CT Planning Room | Radiation Oncology | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
CTPR | CT Planning Room | Radiation Oncology | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142]
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
CTPR | CT Planning Room | Radiation Oncology | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
CTPR | CT Planning Room | Radiation Oncology | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
CTPR | CT Planning Room | Radiation Oncology | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
CTPR | CT Planning Room | Radiation Oncology | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
CTPR | CT Planning Room | Radiation Oncology | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 1 | 1 |  | [ITCL-012 + FIHR-078] for patient observation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
CTPR | CT Planning Room | Radiation Oncology | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 3 |  | [ITCL-012 + FIHR-077] optional; for patient observation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
CTPR | CT Planning Room | Radiation Oncology | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-135]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
CTPR | CT Planning Room | Radiation Oncology | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOSP-032 | JOINERY UNIT: bespoke, radiotherapy, tall, horizontal patient device storage | 2 | 1 |  | [FIJO-166]
CTPR | CT Planning Room | Radiation Oncology | FFE | JOSP-033 | JOINERY UNIT: bespoke, radiotherapy, tall, vertical patient device storage | 1 | 1 |  | [FIJO-167]
CTPR | CT Planning Room | Radiation Oncology | FFE | MICT-002 | IMAGING DEVICE: computerised tomography (CT), gantry, wide bore | 1 | 1 |  | [MMMI-109]
CTPR | CT Planning Room | Radiation Oncology | FFE | MICT-006 | TABLE: patient, computerised tomography (CT) | 1 | 1 |  | [MMMI-105]
CTPR | CT Planning Room | Radiation Oncology | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1 |  | [MMMI-377] may be located in control room
CTPR | CT Planning Room | Radiation Oncology | FFE | MIGE-053 | INJECTOR: contrast, ceiling mounted | 1 | 1 |  | [MMMI-107] may be mobile
CTPR | CT Planning Room | Radiation Oncology | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | [MMBE-042] patient transfer devices to be based on operational requirements and WHS policies
CTPR | CT Planning Room | Radiation Oncology | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-056 | LASER: patient positioning, radiotherapy, table tracking | 1 | 1 |  | [MMRA-019]
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-061 | LASER: patient positioning, radiotherapy, bridge | 1 | 1 |  | [MMRA-014] wall and ceiling mounted lasers are also acceptable
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-071 | DEVICE: surface guided radiation therapy system, ceiling mounted | 1 | 1 |  | [MMRA-008 + FIHR-089] as required for respiratory gating / motion management / surface guidance systems, to suit service requirements
CTPR | CT Planning Room | Radiation Oncology | FFE | MMRA-151 | DEVICE: oven, thermoplastic warming, radiotherapy moulds | 1 | 1 |  | [MMRA-020]
CTPR | CT Planning Room | Radiation Oncology | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | [MMGE-139]
CTPR | CT Planning Room | Radiation Oncology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
CTPR | CT Planning Room | Radiation Oncology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
CTPR | CT Planning Room | Radiation Oncology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
CTPR | CT Planning Room | Radiation Oncology | FIN | FLVY-103 | FLOOR FINISH: vinyl, seamless, standard slip resistance, static dissipative | 1 | 1 | Floor Finish 1 | [FLVY-001] floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
CTPR | CT Planning Room | Radiation Oncology | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
CTPR | CT Planning Room | Radiation Oncology | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 7 | 1 | Wall Finish 2 | [WLWA-020]
CTPR | CT Planning Room | Radiation Oncology | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007]
CTPR | CT Planning Room | Radiation Oncology | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-122]
CTPR | CT Planning Room | Radiation Oncology | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
CTPR | CT Planning Room | Radiation Oncology | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
CTPR | CT Planning Room | Radiation Oncology | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
CTPR | CT Planning Room | Radiation Oncology | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
CTPR | CT Planning Room | Radiation Oncology | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
CTPR | CT Planning Room | Radiation Oncology | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
CTPR | CT Planning Room | Radiation Oncology | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to clock
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to patient observation camera
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 3 |  | [ELGP-101] optional, to additional patient observation camera if provided
CTPR | CT Planning Room | Radiation Oncology | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
CTPR | CT Planning Room | Radiation Oncology | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
CTPR | CT Planning Room | Radiation Oncology | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
CTPR | CT Planning Room | Radiation Oncology | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
CTPR | CT Planning Room | Radiation Oncology | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | [ELBO-001]
CTPR | CT Planning Room | Radiation Oncology | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
CTPR | CT Planning Room | Radiation Oncology | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
CTPR | CT Planning Room | Radiation Oncology | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
CTPR | CT Planning Room | Radiation Oncology | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry door
CTPR | CT Planning Room | Radiation Oncology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
CTPR | CT Planning Room | Radiation Oncology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 1 |  | [ITIN-011] to patient observation camera
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-011] optional, to additional patient observation camera if provided
CTPR | CT Planning Room | Radiation Oncology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
CTPR | CT Planning Room | Radiation Oncology | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | [ITSE-025]
CTPR | CT Planning Room | Radiation Oncology | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038] desirable
CTPR | CT Planning Room | Radiation Oncology | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | [LIFX-002] outside room doors, auto-on when modality in use