## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
DEN-MLB | Dental Laboratory, Minor | Oral Health | Translation and QA Only | 12 | 2700 |  | 4 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1-2 staff | The Minor Dental Laboratory provides facilities and equipment for dental clinicians/technicians to make adjustments to dentures or other dental prosthetics, and to store prosthetic supplies. | ~ Dust extraction is required at the source and may be integral to equipment in some instances. ~ If Bunsen burner to be used in this room, gas outlet or portable gas is required and overhead joinery may need to be reviewed to provide appropriate clearance. ~ A workstation with computer and barcode scanner may be provided for digital tracking and records. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DEN-MLB | Dental Laboratory, Minor | Oral Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQBS-207 | STOOL: office areas, mobile, high | 1 | 1 |  | [FQBS-052]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQDW-131.01 | WORKSTATION: straight, adjustable height, 720H nom, 600D x 1000W | 1 | 3 |  | [FQDW-052] optional
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 6 | 1 |  | [FQSN-006]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 4 | 1 |  | [FQSN-006]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYTP-061 | TAPWARE: basin, tap set, fixture mounted | 1 | 1 |  | [HYTP-038]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | HYTP-151 | TAPWARE: sink, mixer, fixture mounted | 1 | 1 |  | [HYTP-037]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-052]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | [ITNE-007] optional, to workstation if provided
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 3 |  | [ITNE-003] optional; to workstation if provided
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 2 | 1 |  | [FIJO-021]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 2 | 1 |  | [FIJO-100 + FIJO-197] some shelves may be removable or omitted to allow for storage of bulk items on mobile dolly
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 5 | 1 |  | [FIJO-152]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-161 | DEVICE: dental, micromotor, benchtop | 1 | 3 |  | [MMDN-004] optional
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-162 | DEVICE: dental, model trimmer, benchtop | 1 | 1 |  | [MMDN-005] plumbed to sink
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-163 | DEVICE: dental, lathe, benchtop | 1 | 1 |  | [MMDN-009] extraction is required if not integral to equipment
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-164 | DEVICE: dental, moulder, forming machine, benchtop | 1 | 1 |  | [MMDN-013]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-165 | DEVICE: dental, mixing vibrator | 1 | 1 |  | [MMDN-024] a vacuum mixer may also be considered
DEN-MLB | Dental Laboratory, Minor | Oral Health | FFE | MMDN-171 | DEVICE: dental, dust extraction unit | 1 | 1 |  | [MMDN-023]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
DEN-MLB | Dental Laboratory, Minor | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-010] to bench
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 3 |  | [ELGP-208] optional; to workstation if provided
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 2 x task light
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | HYDR-151 | TRAP: plaster | 1 | 1 |  | [HYDR-008]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | LIFX-108 | LIGHT: task, integral to joinery | 5 | 1 |  | [LIFX-008]
DEN-MLB | Dental Laboratory, Minor | Oral Health | SER | MGAS-153 | OUTLET: compressed air, wall mounted | 1 | 1 |  | [MGAS-008] to forming machine