## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
DENSR-1 | Dental Surgery, Type 1 | Oral Health | Translation and QA Only | 14.5 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (dependent on unit operating hours) | 1 patient; 1-2 carers / support persons; 1-2 staff | The Dental Surgery provides for dental consultation, examination and treatment for patients. This Standard Component provides a configuration for switching between a a right-handed and left-handed set-up and should not be mirrored. Dental surgery layouts will vary and will be dependent on existing/proposed workflows and the equipment procured. | ~ Services will be required for the dental chair unit; these will be dependent on the chair model and supplier and include dental air, dental suction, filtered water, power and drainage. ~ Facilities for viewing physical x-ray films brought in by patients may be provided in a central location as required. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Radiation shielding to be advised by Radiation Consultant. ~ An external outlook is desirable. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | D+W | WIFX-157.04 | WINDOW: fixed, external, double glazed, sill at 900H, with integral blind | 1 | 1 | External - Window 1 | [DWWH-005 + DWWD-007] desirable
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-101 | DISPENSER: PPE, disposable masks, wall mounted | 1 | 1 |  | [FIDI-021]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1 |  | [FIDI-014]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-121 | RACK: lead apron, single, wall mounted | 1 | 3 |  | [FIHR-091] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FIHR-211 | BRACKET: computer display screen, single, articulated, bench/desk mounted | 1 | 1 |  | [FIHR-088] articulated with smooth action, reach to be sufficient for left handed and right handed setup
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-028]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQBS-202 | STOOL: clinical areas, mobile | 2 | 1 |  | [FQBS-051]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYBA-421 | SINK: dental, single bowl | 1 | 3 |  | [HYBA-079] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYTP-066 | TAPWARE: basin, tap set, wall mounted | 1 | 1 |  | [HYTP-037]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | HYTP-151 | TAPWARE: sink, mixer, fixture mounted | 1 | 3 |  | [HYTP-038] optional, to sink if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | [ITNE-063]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | ITNE-203 | INPUT DEVICE: keyboard and mouse, medical grade, washable | 1 | 1 |  | [ITNE-067]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-059]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 1 | 3 |  | [FIJO-145] optional, extent of storage dependent on service requirements and approach to consumables storage
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135] below sink if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 3 |  | [FIJO-212] optional, over wall mounted joinery if provided; plasterboard bulkhead is also acceptable
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-031 | CHAIR: dental, electric | 1 | 1 |  | [MMDN-002]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-041 | DELIVERY SYSTEM: instrumentation, dentist, chair mounted | 1 | 1 |  | [MMDN-021]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-051 | DELIVERY SYSTEM: instrumentation, assistant, chair mounted | 1 | 1 |  | [MMDN-022]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-061 | DISPLAY SCREEN: dental, chair mounted | 1 | 3 |  | [MMDN-025] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-072 | LIGHT: dental, ceiling mounted | 1 | 1 |  | [MMDN-020]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-091 | IMAGING DEVICE: dental x-ray, wall mounted | 1 | 1 |  | [MMDN-018]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-096 | CONTROL PANEL: dental x-ray, remote activation | 1 | 1 |  | [MMDN-018]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMDN-121 | TROLLEY: dental, procedure | 1 | 1 |  | [MMDN-016]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1 | [WLWA-004]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 2 | [WLWA-007] to basin
DENSR-1 | Dental Surgery, Type 1 | Oral Health | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 3 | Wall Finish 3 | [WLWA-010] optional, to sink if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGE-002 | DIRECT CONNECTION: power, emergency | 1 | 1 |  | [ELGE-004] to dental chair
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-123] to x-ray unit
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-125]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELGP-201 | GPO: double, wall mounted | 6 | 1 |  | [ELGP-208]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | [ELPR-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] to general room lighting
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ELSW-001 | SWITCH: light | 2 | 3 |  | [ELBO-015] optional, to task lighting if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | HYDR-206 | DIRECT CONNECTION: wastewater, dental chair | 1 | 1 |  | [HYDR-001] to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | [HYTP-008] to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional, depending on service requirements
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITIN-012 | OUTLET: data, single RJ45, in floor box | 1 | 1 |  | [ITIN-010] connection only, to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 3 |  | [LIFX-008] optional, under wall mounted joinery if provided
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | MGAS-029 | DIRECT CONNECTION: medical air | 1 | 1 |  | [MGAS-020] to dental chair, dependent on service requirements and vendor specifications
DENSR-1 | Dental Surgery, Type 1 | Oral Health | SER | MGAS-099 | DIRECT CONNECTION: suction, dental | 1 | 1 |  | [MGAS-090] to dental chair, dependent on service requirements and vendor specifications