## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
DINR | Dining - Patient | Logistics / Support Services | Translation and QA Only | 40 | 2700 |  | 4 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 16 patients seated;; 3-4 staff intermittently | The Dining Room is an area provided for patients to eat their meals away from the bedroom environment in an inpatient setting. The Dining Room may be used for other patient recreational activities when not in use for meals. In this instance, additional transfer of noise to adjacent patient care areas to be considered. | ~ Food services model, e.g. meal trolley (tray or re-thermalisation), servery, beverage bay, etc. will impact room design. A kitchen, servery or beverage bay may be collocated or combined with the Dining Room. ~ Size of space will depend on number of beds and models of care; designed area based on 3m2 per person. ~ Access will be required for patients with limited mobility including wheelchairs, walking frames and other walking aids. Design must also consider the needs of patients with dementia and frail/elderly. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. ~ Duress provision will be dependent on service requirements. ~ Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Lighting to be consistent across the space. ~ Size, type and quantity of waste bins is dependent on environmental management policies and service requirements. Where a facility has additional waste streams, beyond the general waste and comingled recycling indicatively shown in this Standard Component, additional area may be required to accommodate the receptacles. Depending on frequency of waste removal, bin sizes may be larger in high use areas or as guided by local waste management policies. Joinery to conceal bins may be provided depending on infection prevention and control policies. ~ Where possible a achieving a domestic appearance with furniture, fittings and finishes is recommended. ~ The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. ~ Natural light and external outlook is essential. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
DINR | Dining - Patient | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DINR | Dining - Patient | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DINR | Dining - Patient | Logistics / Support Services | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 2 | 1 | External - Window 1 | [DWWD-004]
DINR | Dining - Patient | Logistics / Support Services | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 2
DINR | Dining - Patient | Logistics / Support Services | D+W | DOHI-144.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-031] with hold open device to support trolley movement as required
DINR | Dining - Patient | Logistics / Support Services | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] natural light and external outlook is essential
DINR | Dining - Patient | Logistics / Support Services | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 2 | [DWWH-005] natural light and external outlook is essential
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 3 |  | [FIHR-006] optional
DINR | Dining - Patient | Logistics / Support Services | FFE | FQBS-151 | CHAIR: dining areas | 16 | 1 |  | [FQBS-015] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
DINR | Dining - Patient | Logistics / Support Services | FFE | FQCA-082 | TROLLEY: food delivery, hot/cold | 1 | 1 |  | [FQCA-082] as required to suit food service model
DINR | Dining - Patient | Logistics / Support Services | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1 |  | [FQGE-002]
DINR | Dining - Patient | Logistics / Support Services | FFE | FQTA-226.01 | TABLE: square, 750H, 1000L | 4 | 1 |  | [FQTA-059] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
DINR | Dining - Patient | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] size, type and quantity of bins dependent on local waste management policies
DINR | Dining - Patient | Logistics / Support Services | FFE | FQWS-073 | BIN: recycling, commingled, 50L | 1 | 1 |  | [FQCW-062] size, type and quantity of bins dependent on local waste management policies
DINR | Dining - Patient | Logistics / Support Services | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DINR | Dining - Patient | Logistics / Support Services | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DINR | Dining - Patient | Logistics / Support Services | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 3 |  | [ITBU-011] optional
DINR | Dining - Patient | Logistics / Support Services | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
DINR | Dining - Patient | Logistics / Support Services | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
DINR | Dining - Patient | Logistics / Support Services | FFE | JODW-031 | DRAWER UNIT: under bench, 3 drawers, equal | 1 | 1 |  | [FIJO-104]
DINR | Dining - Patient | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DINR | Dining - Patient | Logistics / Support Services | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
DINR | Dining - Patient | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
DINR | Dining - Patient | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10/pendulum P3 or agreed equivalent to extend under basin; significant change in colour to be avoided
DINR | Dining - Patient | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
DINR | Dining - Patient | Logistics / Support Services | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 2 | 1 | Wall Finish 2 | [WLWA-025] to meal trolley parking area
DINR | Dining - Patient | Logistics / Support Services | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
DINR | Dining - Patient | Logistics / Support Services | SER | ELGP-101.01 | GPO: single, wall mounted, horizontal | 1 | 1 |  | [ELGP-109] to meal trolley parking area; power requirements dependent on type of meal trolley
DINR | Dining - Patient | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 3 | 1 |  | [ELGP-208]
DINR | Dining - Patient | Logistics / Support Services | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 3 |  | [ELGP-208] optional, to television
DINR | Dining - Patient | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 2 | 3 |  | [ITCL-006] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | [ITCL-008] with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 3 |  | [ITCL-028] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
DINR | Dining - Patient | Logistics / Support Services | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to wall mounted telephone
DINR | Dining - Patient | Logistics / Support Services | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, to television, MATV outlet may also be provided depending on local ICT policies