## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Disposal Room provides for the temporary holding of waste, separated into various waste streams (general waste, clinical waste, cardboard recycling, co-mingled recycling, cytotoxic waste, confidential waste, sharps, soiled linen, etc.) prior to removal to a designated waste zone in the loading dock. | ~ Waste will be collected at regular times each day, or when requested, to prevent build-up of waste in the unit. ~ Size requirements for a Disposal Room will be dependent on a department's estimated waste output, the frequency of waste collection and local operational policies for waste management that may dictate the number of waste streams and minimum bin sizes. ~ Adequate space must be provided to allow for segregation of waste streams. ~ The use of 660 L bins should be carefully considered due to the WHS risks associated with manual handling, however it is acknowledged in some areas with significant waste output they may be required. Where the weight of full waste receptacles is a concern, the use of tugs/ACVs is often required. ~ Waste transfer may be manual, by motorised movers/tugs or via automated guided vehicle (AGV) systems. Where tugs and AGVs are being considered, it is important to confirm clearances, door widths and turning circles within the room, in the adjacent corridor and along path of travel to designated waste zone. ~ Hold open door hardware may be required to allow for easy movement of bins and trolleys in and out of the room. ~ Shelf may be provided for storage of small sharps bins prior to collection. ~ If a handwashing basin is not provided within the Disposal Room, one should be located in close proximity. The location of hand hygiene facilities may be dependent on local infection control policies. ~ Staff only access may be required if this room is provided in a public or patient care area. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | [DWPR-005] to room side
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] lockable or secure staff access, hold open hardware may be required
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQCL-273 | TROLLEY: dirty linen collection, large | 1 | 1 |  | [MMGE-143]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-059 | BIN: general waste, 660L (skip) | 1 | 1 |  | [FQCW-022] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-098 | BIN: recycling, paper/cardboard, 240L | 1 | 1 |  | [FQCW-029] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | FQWS-238 | BIN: clinical waste, 240L | 1 | 1 |  | [FQCW-006] size, type and quantity of bins dependent on service requirements and local waste management policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010] may be provided outside of room depending on local infection control policies
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FFE | JOSH-401 | SHELF: wall mounted, laminate | 1 | 3 |  | [FIJO-194] optional, for storage of small sharps bins
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-023]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
DISP-10 | Disposal Room, 10m2 | Logistics / Support Services | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware