## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
DTUR-10 | Dirty Utility, 10m2 | 10 |  | 1 - 2 intermittently | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility provides for cleaning and holding of used equipment for collection and sterilisation elsewhere, disposal of clinical and other wastes and soiled linen, testing and disposing of patient specimens and decontamination and storage of patient utensils such as pans, urinals and bowls. Acoustics: Sound attenuation level - high; Acoustic privacy required

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
DTUR-10 | Dirty Utility, 10m2 | FE | FE-2800 | Basin - handwash, Type B | 1 | refer to BHWS-B (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FE | FE-38700 | Washer sanitiser - pan | 1 | not hardwired, combined utensil/pan sanitiser optional |  |  |  | Yes | No | Yes | Yes | Yes | No | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FE | FE-49111 | Sink - 450x350x250D | 1 | hot water |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FE | FE-49800 | Sink - flushing rim | 1 | & pressure control hose spray |  |  |  | No | No | Yes | Yes | No | No | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FE | FE-58200 | Washer sanitiser - utensil | 1 | combined utensil/pan sanitiser optional |  |  |  | Yes | No | Yes | Yes | Yes | No | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FE | FE-4045 | Tapware - elbow mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-1010 | Bench - stainless steel | 1 | with wet edge |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-12300 | Linen carrier - dirty, single | 3 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-1455 | Rack - bowl / basin | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-1470 | Bracket - sharps | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-16500 | Rack - pan & urinal | 2 | total of 12 pans/ 12 urinals |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-19700 | Sharps bin | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-19820 | Shelf - SS, under | 1 | @ 350mm AFFL |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-24125 | Waste bin - clinical | 1 | 240 litre sulo bin |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-4494 | Cupboard - urinalysis | 1 | over bench, optional |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-6156 | Dispenser - soap | 1 | to hand basin |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-7200 | Hook - equipment | 2 | for clean linen bags |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-9200 | Hook - for catheter bag | 2 | above flushing rim sink |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-5830 | Dispenser - antiseptic hand rub | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-1433 | Electrical Isolator: 1PH+N | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-9060 | GPO: Special: for equipment | 2 | Pan Sanitiser, Utensil Washer, or combined utensil/pan sanitiser optional |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-4000 | Hot water: outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-4010 | Cold water: outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-4033 | Floor waste | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-5015 | Ventilation | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-5019 | Exhaust | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | S-6200 | Light switches (2-way) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 1020 | Floor finish | 1 |  | Vinyl, non-slip | Safety | Seamless, coved | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 3052 | Wall finish | 1 |  | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 5023 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 9004 | Door - 1100mm | 1 | 910mm clear opening; pull handle/push plate, closer | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No